## Executive Summary
Executive Summary: DISIS-2018-001 Phase 2 of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2018. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.8 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2018-002 Phase 2 includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest ) NOTE: per SPP Tariff Attachment V; section 8.4.2 DISIS Phase Two will consist of a power flow analysis, a stability analysis, and a short-circuit analysis.
DISIS Manual Version 1.8
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
6,858.19 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $‭39,084,345.30 Steady State Network Upgrade $27,203,760.30 Stability Network Upgrade $11,880,585.00 Interconnection Costs: $223,120,342.00
Models Used in Steady State Study
2021 ITP Series
Winter: 2026
Summer: 2023, 2026
Light: 2026
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
Published: April 10, 2023
Costs for Solar/Battery Requests were allocated using the 26SP (summer peak) model.
Costs for Wind Requests were allocated using the 26L (light load) model.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.

## Revision History
Revision History
Date | Author | Change Description
4499100% | SPP | Phase 2 Draft Posting
4500500% | SPP | Phase 2 Final Posting
4502700% | SPP | Phase 2 Final Re-Posting - Cost Allocation and NRIS Constraint Identification Updates

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4500500% | Interconnection Costs | 1 | Executive Summary | Updated Interconnection Costs to reflect the removal of UID 155729 and 155730
4500500% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection Costs to reflect the removal of UID 155729 and 155730
4500500% | Interconnection Costs | 7 | Upgrade Summary | Updated Interconnection Costs to reflect the removal of UID 155729 and 155730
4502700% | Assigned Upgrade Costs | 6 | Assigned Upgrade Costs | Updated assigned upgrade costs for Summit to Watertown 115 kV Rebuild
4502700% | Assigned Upgrade Costs | 6 | Assigned Upgrade Costs | Updated assigned upgrade costs for Build a 50 MVAR SVC at GEN-2018-058 345 kV
4502700% | Transmission Owner | 7 | Upgrade Summary | Updated Transmission Owner to WERE for Build a 50 MVAR SVC at GEN-2018-058 345 kV
4502700% | Interconnection Costs | 1 | Executive Summary | Updated Interconnection Costs to reflect the removal and replacement of UID 155899 and 155900
4502700% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection Costs to reflect the removal and replacement of UID 155899 and 155900
4502700% | Interconnection Costs | 7 | Upgrade Summary | Updated Interconnection Costs to reflect the removal and replacement of UID 155899 and 155900
4502700% | LOIS Amount | 4 | Requests | Updated LOIS amounts for GEN-2018-059
4502700% | Network Upgrades | 1 | Executive Summary | Updated Network Upgrade Costs to reflect the removal of UID 156860, 156868, and 156867
4502700% | Network Upgrades | 5 | Constraint Summary | Removed thermal overloads responsible for UID 156850, 156860, 156868, and 156867
4502700% | Network Upgrades | 6 | Assigned Upgrade Costs | Removed UID 156850, 156860, 156868, and 156867
4502700% | Network Upgrades | 7 | Upgrade Summary | Removed UID 156850, 156860, 156868, and 156867
4502700% | Network Upgrades | 8 | All Thermal | Removed thermal overloads responsible for UID 156850, 156860, 156868, and 156867

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Reactive Compensation Requirements (MVAR) | Service | Area | POI | Status
ASGI-2017-013 | 01 - North | 20 | DIS-18-1 | Wind | 40 | 40 | None | -0.45 | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
GEN-2018-007 | 01 - North | 20 | DIS-18-1 | Solar | 150 | 150 | None | -1.92 | ER/NR | WAPA | Summit 115kV Substation | DISIS STAGE
GEN-2018-008 | 01 - North | 20 | DIS-18-1 | Wind | 252 | 252 | None | -4.99 | ER/NR | BEPC-SPP | Groton-Leland Olds 345kV Line | DISIS STAGE
GEN-2018-010 | 01 - North | 20 | DIS-18-1 | Storage | 74.1 | 74.1 | None | -0.06 | ER/NR | BEPC-SPP | Neset 230kV Substation | DISIS STAGE
GEN-2018-039 | 01 - North | 20 | DIS-18-1 | Solar | 72 | 72 | None | -1.35 | ER/NR | WAPA | Edgeley 115kV substation | DISIS STAGE
GEN-2018-012 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 74.1 | 74.1 | None | -11.04 | ER/NR | NPPD | Antelope - Hoskins 345kV line | DISIS STAGE
GEN-2018-025 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 | 200 | None | -0.31 | ER | OPPD | Fort Calhoun 345kV Substation | DISIS STAGE
GEN-2018-033 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 | 200 | None | -110.46 | ER | OPPD | Cass County 345kV Substation | DISIS STAGE
GEN-2018-037 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 100 | 100 | None | -0.05 | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | DISIS STAGE
GEN-2018-043 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 | 500 | None | -10.68 | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | DISIS STAGE
GEN-2018-044 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 | 500 | None | -10.68 | ER | OPPD | Fort Calhoun 345kV Substation | DISIS STAGE
GEN-2018-056 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 102.6 | 0 | Non-converged | -4.37 | ER/NR | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | DISIS STAGE
GEN-2018-060 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 50 | 0 | Non-converged | 0 | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
ASGI-2018-003 | 03 - Central | 20 | DIS-18-1 | Solar | 20 | 20 | None | -0.46 | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 - Central | 20 | DIS-18-1 | Solar | 20 | 20 | None | -8.27 | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 - Central | 20 | DIS-18-1 | Solar | 20 | 20 | None | -55.1 | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 - Central | 20 | DIS-18-1 | Solar | 35 | 35 | None | -51.55 | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 - Central | 20 | DIS-18-1 | Solar | 35 | 35 | None | -51.55 | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-009 | 03 - Central | 20 | DIS-18-1 | Wind | 150 | 150 | None | -12.27 | ER | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 | 74.1 | None | -2.13 | ER | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-014 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 | 74.1 | None | -6.37 | ER | KCPL | Holt County 345kV Substation | DISIS STAGE
GEN-2018-022 | 03 - Central | 20 | DIS-18-1 | Solar | 300 | 300 | None | -14.27 | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-030 | 03 - Central | 20 | DIS-18-1 | Storage | 200 | 200 | None | -3.37 | ER | SPS | Lamar-Finney 345kV Substation | DISIS STAGE
GEN-2018-031 | 03 - Central | 20 | DIS-18-1 | Storage | 50 | 50 | None | -23.63 | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 - Central | 20 | DIS-18-1 | Wind | 310 | 310 | None | -25.79 | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-049 | 03 - Central | 20 | DIS-18-1 | Solar | 120 | 120 | None | -31.23 | ER | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-053 | 03 - Central | 20 | DIS-18-1 | Wind | 100 | 100 | None | -4.8 | ER | WERE | Kelly 161kV Substation | DISIS STAGE
GEN-2018-054 | 03 - Central | 20 | DIS-18-1 | Solar | 120 | 120 | None | -1.9 | ER | KCPL | KC South - N. Raymore 161kV Line | DISIS STAGE
GEN-2018-057 | 03 - Central | 20 | DIS-18-1 | Solar | 203.4 | 203.4 | None | -2.85 | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-058 | 03 - Central | 20 | DIS-18-1 | Solar | 252 | 0 | Multiple contingencies causing unit tripping due to lack of plant reactive power support. | -66.2 | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2018-059 | 03 - Central | 20 | DIS-18-1 | Solar | 252 | 0 | Multiple contingencies causing unit tripping due to lack of plant reactive power support. | -66.4 | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2018-061 | 03 - Central | 20 | DIS-18-1 | Wind | 50 | 50 | None | -4.4 | ER | WERE | Kelly 161kV Substation | DISIS STAGE
GEN-2018-062 | 03 - Central | 20 | DIS-18-1 | Solar | 75.6 | 75.6 | None | -1.48 | ER/NR | KACY | Nearman 161kV substation | DISIS STAGE
GEN-2018-003 | 04 - Southeast | 20 | DIS-18-1 | Solar | 150 | 150 | None | -0.01 | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 - Southeast | 20 | DIS-18-1 | Storage | 74.1 | 74.1 | None | -0.62 | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 - Southeast | 20 | DIS-18-1 | Solar | 74.1 | 74.1 | None | -3.74 | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 | 100 | None | -0.19 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 | 100 | None | -0.24 | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 | 74.702 | 509776 52DELTP4 138 509800 36LEWIS4 138 1 (ftlo) P12:138:AEPW:R.S.S.-4:R:96YALE-4 | -0.07 | ER | AEPW | Tulsa Power Station 138kV Substation | DISIS STAGE
GEN-2018-028 | 04 - Southeast | 20 | DIS-18-1 | Storage | 200 | 200 | None | -28.7 | ER | OKGE | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 | 100 | None | -16.47 | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 - Southeast | 20 | DIS-18-1 | Solar | 300 | 300 | None | -2.5 | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 - Southeast | 20 | DIS-18-1 | Solar | 200 | 200 | None | -6.26 | ER | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-051 | 04 - Southeast | 20 | DIS-18-1 | Storage | 35 | 35 | None | -1.22 | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-055 | 04 - Southeast | 20 | DIS-18-1 | Solar | 252 | 252 | None | -23.99 | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 - Southwest | 20 | DIS-18-1 | Solar | 74.99 | 74.99 | None | -132.2 | ER | SPS | T14 Circuit 115kV line | DISIS STAGE
GEN-2018-015 | 05 - Southwest | 20 | DIS-18-1 | Solar | 252 | 252 | None | -4.48 | ER/NR | SPS | Tuco-Oklaunion 345kV Line | DISIS STAGE
GEN-2018-052 | 05 - Southwest | 20 | DIS-18-1 | Storage | 70 | 70 | None | -1.12 | ER | SPS | Roadrunner 115kV Substation | DISIS STAGE
J1040 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1045 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 20 |  |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1072 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J1092 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1164 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1169 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | XEL | Grant 115 kV Substation | IA PENDING
J1181 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1221 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1298 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Hayward - Murphy Creek 161kV Line | IA PENDING
J1312 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1314 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
J1325 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | ALTW | Magnolia 161 kV substation | IA PENDING
J1426 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1445 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1474 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  |  | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | IA PENDING
J1485 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J1494 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | XEL | Chisago 115kV | Not Started
J1495 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | XEL | North Rochester 161kV | Not Started
J1498 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | XEL | Chanarambie 115 kV Substation | Not Started
J1503 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Huntley 345 kV | Not Started
J1504 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Huntley 345 kV | Not Started
J1534 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Byron 345kV | Not Started
J1566 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Rutland Substation 161kV | Not Started
J1572 | 01 - North | 19.5 | DIS-18-1-PQ | Solar/Storage | 150 |  |  |  | ER/NR | XEL | Huntley to Blue Earth 161kV | Not Started
J1575 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 70 |  |  |  | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Not Started
J1581 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Nobles County 345 kV Substation | Not Started
J1582 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 160 |  |  |  | ER/NR | XEL | Pine Lake to Three Lakes 115 kV | Not Started
J1588 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Bison 345kV | Not Started
J1605 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Sherburne 345kV | Not Started
J1611 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 120 |  |  |  | ER/NR | XEL | Langola 115kV Tap | Not Started
J1620 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER | XEL | Pipestone to Split Rock 115kV | Not Started
J1622 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | OTP | Harvey-Underwood 230kV | Not Started
J1657 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER | XEL | Pine Lake to Apple River 161 kV | Not Started
J1730 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | XEL | Eau Claire to AS King 345 kV | Not Started
J1754 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER/NR | GRE | McHenry ND | Not Started
J1769 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 80 |  |  |  | ER | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Not Started
J1808 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 148 |  |  |  | ER | DPC | Barron 161 kV | Not Started
J1826 | 01 - North | 19.5 | DIS-18-1-PQ | Hydro | 4 |  |  |  | ER | XEL | Cannon Falls Transmission 69 kV | Not Started
J967 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  |  | ER | XEL | Adams 345kV Substation | IA PENDING
MPC03600 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03700 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03800 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC03900 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 151.2 |  |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC04000 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  |  | ER/NR | OTP | Square Butte 230 kV Substation
J1050 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J1132 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1174 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1270 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1313 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1359 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Combustion Turbine | 95 |  |  |  | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1365 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 169.4 |  |  |  | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1444 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J1520 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV | Not Started
J1529 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Not Started
J1530 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Not Started
J1532 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Clarinda-Coburg 69 kV | Not Started
J1590 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER/NR | MEC | O'Brien - Raun 345 kV | Not Started
J982 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
GIA-96 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 101.32 |  |  |  | ER | AECI | Stroud 138kV | IA PENDING
J1025 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1026 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | IA PENDING
J1145 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1182 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J1191 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 64 |  |  |  | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1202 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar/Storage | 68 |  |  |  | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1208 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1209 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1213 | 03 - Central | 19.5 | DIS-18-1-PQ | Hydro | 60 |  |  |  | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1216 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 185 |  |  |  | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1241 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1303 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  |  | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1311 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1352 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | IA PENDING
J1488 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 500 |  |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 1000 |  |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J956 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J976 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J994 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
J1007 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | IA PENDING
J1030 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | EES | Poco - Menard 138 kV | IA PENDING
J1034 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1060 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | IA PENDING
J1087 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1107 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1125 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | IA PENDING
J1155 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | EES-EAI | Driver 230 kV | IA PENDING
J1205 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER | CLEC | Centennial - West Bay 138 kV | IA PENDING
J1215 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 155 |  |  |  | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1231 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1239 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER | EES | Rilla 115 kV | IA PENDING
J1258 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1281 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 75 |  |  |  | ER/NR | EES-EAI | Crossett - Monticello East 115 kV | IA PENDING
J1299 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 149 |  |  |  | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J1373 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  |  | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1402 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 0 |  |  |  | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1415 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1424 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER | CLEC | Cooper - Penton Road 230 kV | IA PENDING
J1434 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1436 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | EES | Oak Ridge 115 kV | IA PENDING
J1437 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 180 |  |  |  | ER/NR | EES-EAI | AECC Dry Creek 161 kV | IA PENDING
J1442 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 105 |  |  |  | ER | EES | Rich (SHECO) - Livingston 138 kV | IA PENDING
J1509 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EMI | Greenwood - Pickens 115 kV | Not Started
J1514 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Driver 230kV | Not Started
J1558 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Not Started
J1559 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Not Started
J1562 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Not Started
J1577 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Hardin West SS to Sheridan 115 kV | Not Started
J1598 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 325.02 |  |  |  | ER | EES | Solac - Chalkley 230kV | Not Started
J1602 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 25 |  |  |  | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Not Started
J1612 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Not Started
J1669 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Not Started
J1670 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Not Started
J1671 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | EES | Rocky Creek to Lewis Creek 230kV | Not Started
J1672 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | EES-EMI | Tinnin Road 230kV | Not Started
J1673 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Not Started
J1709 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 100 |  |  |  | ER | EES | 138 kV Grimes | Not Started
J1710 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Not Started
J1723 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 10 |  |  |  | ER/NR | EES-EAI | Wynne East to Wynne South 161kV line (J1125 sub) | Not Started
J1747 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | EES-EMI | J830 POI | Not Started
J1748 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EMI | Twinkletown 230 kV | Not Started
J1760 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 205 |  |  |  | ER/NR | EES | Timberland 230kV | Not Started
J1816 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Not Started
J1820 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Not Started
J1827 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 90 |  |  |  | ER/NR | EES | Bastrop tap point | Not Started
J1834 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Combustion Turbine | 126 |  |  |  | ER/NR | EES | Sabine 138/230 kV Substation | Not Started
J1842 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 135 |  |  |  | ER | EES-EAI | Forrest City to Wynne S 161 KV | Not Started
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-199 | 01 - North | 19 | DIS-17-2 | Storage | 202 |  |  |  | ER/NR | BEPC-SPP | Groton 345kV Substation | DISIS STAGE
GEN-2017-200 | 01 - North | 19 | DIS-17-2 | Wind | 302 |  |  |  | ER/NR | BEPC-SPP | Groton 345kV Substation | DISIS STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  |  | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-235 | 01 - North | 19 | DIS-17-2 | Wind | 50 |  |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-236 | 01 - North | 19 | DIS-17-2 | Wind | 50 |  |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  |  | ER/NR | OPPD | Tekamah - Raun 161 kV Line | DISIS STAGE
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER | WAPA | Holt County 345kV | DISIS STAGE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 11.64 |  |  |  | ER | OPPD | Jones St. No 1201 69kV substation | DISIS STAGE
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  |  | ER/NR | NPPD | Hoskins 345kV Substation | DISIS STAGE
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Solar/Storage | 310 |  |  |  | ER | NPPD | McCool 345kV Substation | DISIS STAGE
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  |  | ER | NPPD | Spalding to North Loup 115kV | DISIS STAGE
ASGI-2017-014 | 03 - Central | 19 | DIS-17-2 | Solar | 40 |  |  |  | ER/NR | KCPL | Post Oak 69 kV
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 |  |  |  | ER | KCPL | Clinton â€“ Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  |  | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  |  | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-128 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Storage | 29.6 |  |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  |  | ER/NR | EMDE | Joplin 161kV sub | DISIS STAGE
GEN-2017-179 | 03 - Central | 19 | DIS-17-2 | Wind | 222 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  |  | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-191 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-192 | 03 - Central | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-194 | 03 - Central | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | WERE | Tecumseh 230kV Substation | DISIS STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Storage | 128 |  |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar/Storage | 300 |  |  |  | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Storage | 152 |  |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-225 | 03 - Central | 19 | DIS-17-2 | Storage | 76 |  |  |  | ER/NR | KCPL | Craig 345kV Substation | DISIS STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Storage | 201.6 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-229 | 03 - Central | 19 | DIS-17-2 | Storage | 76 |  |  |  | ER/NR | KCPL | Stilwell 345kV Substation | DISIS STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Storage | 19.8 |  |  |  | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER/NR | OKGE | Muskogee 345kV Substation | DISIS STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar/Storage | 210 |  |  |  | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-213 | 04 - Southeast | 19 | DIS-17-2 | Solar/Storage | 300 |  |  |  | ER | AEPW | Clarksville 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  |  | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  |  | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  |  | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-240 | 04 - Southeast | 19 | DIS-17-2 | Solar | 202 |  |  |  | ER/NR | OKGE | Bristow 138kV Substation | DISIS STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  |  | ER | SPS | Deaf Smith-Plant X 230kV | DISIS STAGE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER | SPS | Tuco-Oklaunion 345kV Line | DISIS STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-176 | 05 - Southwest | 19 | DIS-17-2 | Solar/Wind | 300 |  |  |  | ER/NR | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  |  | ER | SPS | Sulphur Springs 115kV Substation | DISIS STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  |  | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  |  | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  |  | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  |  | ER | XEL | Tracy 69 kV line | DISIS STAGE
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  |  | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  |  | ER | ALTW | Ledyard 345kV Substation
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  |  | ER/NR | AECI | McCredie 345 kV
GIA-84 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 200.62 |  |  |  | ER | AECI | New Madrid 345 kV
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar/Storage | 447.3 |  |  |  | ER/NR | AECI | Morgan 345 kV | DISIS STAGE
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  |  | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-92 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 170 |  |  |  | ER/NR | AECI | Harrisburg - Higbee 161 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-94 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 225 |  |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  |  | ER | WAPA | Rhame 230 kV Sub | FACILITY STUDY STAGE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | WAPA | Philip Tap 230 kV | FACILITY STUDY STAGE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | BEPC-SPP | Neset 230 kV Substation | FACILITY STUDY STAGE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | FACILITY STUDY STAGE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  |  | ER | WAPA | Underwood 115 kV Sub | FACILITY STUDY STAGE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  |  | ER | SUNC | Elm Creek - Summit 345 kV | FACILITY STUDY STAGE
GEN-2017-005 | 03 - Central | 18 | DIS-17-1 | Wind | 190 |  |  |  | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  |  | ER/NR | SUNC | Thistle 345 kV sub | FACILITY STUDY STAGE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | AEPW | Chisholm-Gracemont 345kV Line | FACILITY STUDY STAGE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | FACILITY STUDY STAGE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  |  | ER | WFEC | Snyder - Cache 138 kV | FACILITY STUDY STAGE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | FACILITY STUDY STAGE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  |  | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  |  | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  |  | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  |  | ER | BEPC-SPP | NELSON 7
GEN-2016-036 | 01 - North | 17 | DIS-16-2 | Wind | 44.6 |  |  |  | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  |  | ER | NPPD | Sidney 115 kV Sub | IA PENDING
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-115 | 03 - Central | 17 | DIS-16-2 | Wind | 300 |  |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Storage | 20 |  |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  |  | ER | SPS | TEXAS_CNTY 3
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Combustion Turbine | 17 |  |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | Dis-16-2-PQ | Wind | 238 |  |  |  | ER/NR | AECI | 5MARYVL
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 300 |  |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  |  | ER | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Combustion Turbine | 29 |  |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | Wind | 220 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 |  |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 04 - Southeast | 16 | DIS-16-1 | Wind | 150 |  |  |  | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 - Southeast | 16 | DIS-16-1 | Wind | 250.7 |  |  |  | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
PQOKGEMustang | 04 - Southeast | 16 | DIS-16-1 | Combustion Turbine | 287 |  |  |  | ER | OKGE | MUSTANG4
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 - Southwest | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Storage | 20 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-055 | 04 - Southeast | 15 | DIS-15-2 | Solar | 40 |  |  |  | ER | WFEC | Erick 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.5 |  |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  |  |  | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV]
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  |  | ER/NR | XEL | Marshall 115kV
GEN-2007-020IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2010-003IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
MPC02100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.75 |  |  |  | ER | OTP | Center - Mandan 230 kV
GEN-2007-017IS | 02 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 202 |  |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 02 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 198 |  |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Combustion Turbine | 6.13 |  |  |  | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 200.11 |  |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 - Southeast | 13 | DIS-14-2 | Wind | 249.9 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 - Southwest | 13 | DIS-14-2 | Solar | 30 |  |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 |  |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  |  | ER | SPS | FE Clovis 115kV
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  |  | ER | SPS | FE-Clovis Interchange 115kV
NPPDBuffaloCountySolar | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  |  | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Waste Heat | 22.5 |  |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
ASGI-2010-006GIA-27 | 04 - Southeast | 8 | PQ | Wind | 150 |  |  |  | ER | AECI | Remington 138kV
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 |  |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Central | 2 | ICS1 | Wind | 250 |  |  |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
01ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
01ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
01ALL | ERIS | Thermal | 652433 EDGELEY8 69.0 996769 ED KY6A _1 69.0 1 | 26WP | 652432 EDGELEY7 115 652445 JAMESTN7 115 1 |  | 37.5 | 49.78 | 101.13 |  |  |  | Edgeley 115-69 kV Transformer Replacement
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 | 23SP, 26SP | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1 |  | 186 | 55.43 | 105.39 |  |  |  | Summit to Watertown 115 kV Rebuild
01ALL | ERIS | Thermal | None | 26L | None | [7 empty] | None
01ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | None | 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
02ALL | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | ERIS | Stability | Low Voltages; Protection Tripping | 25S, 25W | Multiple Contingencies (See Stability Analysis Results Tab) | [7 empty] | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03ALL | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
04ALL | ERIS | Thermal | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 | 23SP, 26SP, 26WP | P23:345:AEPW:WELSH CB 11990 NBTB |  | 153 |  | 130.05 |  |  |  | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001)
04ALL | ERIS | Thermal | 509776 52DELTP4 138 509800 36LEWIS4 138 1 | 23SP, 26SP | P12:138:AEPW:R.S.S.-4:R:96YALE-4 |  | 278 |  | 109.1 |  |  |  | Delaware Tap to 36th&Lewis 138 kV Rebuild (DISIS-2018-001)
04ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
05ALL | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
01NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
01NR | NRIS | Voltage | None | 26L | None | [7 empty] | None
02NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
02NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
02NR | NRIS | Voltage | None | 26L | None | [7 empty] | None
03NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
03NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
03NR | NRIS | Voltage | None | 26L | None | [7 empty] | None
04NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
04NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
04NR | NRIS | Voltage | None | 26L | None | [7 empty] | None
05NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
05NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
05NR | NRIS | Voltage | None | 26L | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
GEN-2018-039 | 01 - North | TBD | ERIS | Edgeley 115-69 kV Transformer Replacement | Current Study | Replace the existing 115/69 kV transformer at Edgeley to a minimum rating of 42 MVA | 2777743 | 100% | 2777743 | 0.09988
GEN-2018-039 | 01 - North | 155905 | ERIS | Edgeley 115kV Substation GEN-2018-039 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-039 | 1709000 | 100% | 1709000 | 1
GEN-2018-039 | 01 - North | 155906 | ERIS | Edgeley 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-039 | 1709000 | 100% | 1709000 | 1
GEN-2018-008 | 01 - North | 156037 | ERIS | Groton-Leland Olds 345kV GEN-2018-008 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2018-008 | 2334054 | 100% | 2334054 | 1
GEN-2018-008 | 01 - North | 156038 | ERIS | Groton-Leland Olds 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-008 | 20903079 | 100% | 20903079 | 1
GEN-2018-010 | 01 - North | 156176 | ERIS | Neset 230kV Substation GEN-2018-010 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2018-010 | 120000 | 100% | 120000 | 1
GEN-2018-010 | 01 - North | 156177 | ERIS | Neset 230kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-010 | 0 | 100% | 0 | 1
GEN-2018-007 | 01 - North | 156238 | ERIS | Summit 115kV Substation GEN-2018-007 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-007 | 1565000 | 100% | 1565000 | 1
GEN-2018-007 | 01 - North | 156239 | ERIS | Summit 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-007 | 1565000 | 100% | 1565000 | 1
GEN-2018-007 | 01 - North | TBD | ERIS | Summit to Watertown 115 kV Rebuild | Current Study | Rebuild the Summit to Watertown 115 kV 30.7 mile line to a minimum rating of 212 MVA | 19972030.642 | 93.32% | 21822788 | 0.47877
GEN-2018-008 | 01 - North | TBD | ERIS | Summit to Watertown 115 kV Rebuild | Current Study | Rebuild the Summit to Watertown 115 kV 30.7 mile line to a minimum rating of 212 MVA | 1011979.6264 | 4.637% | 21822788 | 0.01444
GEN-2018-039 | 01 - North | TBD | ERIS | Summit to Watertown 115 kV Rebuild | Current Study | Rebuild the Summit to Watertown 115 kV 30.7 mile line to a minimum rating of 212 MVA | 838777.7315 | 3.844% | 21822788 | 0.04189
GEN-2018-012 | 02 - Nebraska | 155889 | ERIS | Antelope - Hoskins 345kV GEN-2018-012 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-012 | 1500000 | 100% | 1500000 | 1
GEN-2018-012 | 02 - Nebraska | 155890 | ERIS | Antelope - Hoskins 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-012 | 5500000 | 100% | 5500000 | 1
GEN-2018-060 | 02 - Nebraska | 155891 | ERIS | Axtell-Post Rock 345 kV GEN-2018-060 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-060 | 1500000 | 100% | 1500000 | 1
GEN-2018-060 | 02 - Nebraska | 155892 | ERIS | Axtell-Post Rock 345 kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-060 | 50000 | 100% | 50000 | 1
GEN-2018-033 | 02 - Nebraska | 155897 | ERIS | Cass County 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-033 | 2292537 | 100% | 2292537 | 1
GEN-2018-033 | 02 - Nebraska | 155898 | ERIS | Cass County 345kV Substation Interconnection Expansion GEN-2018-033 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-033 | 1662072 | 100% | 1662072 | 1
GEN-2018-025 | 02 - Nebraska | 155907 | ERIS | Fort Calhoun 345kV Substation GEN-2018-025 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-025 | 0 | 100% | 0 | 1
GEN-2018-044 | 02 - Nebraska | 155908 | ERIS | Fort Calhoun 345kV Substation GEN-2018-044 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-044 | 0 | 100% | 0 | 1
GEN-2018-025 | 02 - Nebraska | 156027 | ERIS | Fort Calhoun 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-025 and GEN-2018-044 | 863310.5714 | 28.57% | 3021587 | 1
GEN-2018-044 | 02 - Nebraska | 156027 | ERIS | Fort Calhoun 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-025 and GEN-2018-044 | 2158276.4286 | 71.43% | 3021587 | 1
GEN-2018-056 | 02 - Nebraska | 156028 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV GEN-2018-056 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-056 | 2898000 | 100% | 2898000 | 1
GEN-2018-056 | 02 - Nebraska | 156029 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-056 | 2898000 | 100% | 2898000 | 1
GEN-2018-043 | 02 - Nebraska | 156030 | ERIS | Ft. Calhoun - Raun 345 kV GEN-2018-043 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-043 | 8894071 | 100% | 8894071 | 1
GEN-2018-043 | 02 - Nebraska | 156031 | ERIS | Ft. Calhoun - Raun 345 kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-043 | 0 | 100% | 0 | 1
GEN-2018-056 | 02 - Nebraska | NTC 200220 | ERIS | Gentleman to Cherry County and Cherry County to Holt new 345 kV line | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | 0 | 98.07% | 450832958 | 0.18821
GEN-2018-060 | 02 - Nebraska | NTC 200220 | ERIS | Gentleman to Cherry County and Cherry County to Holt new 345 kV line | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | 0 | 1.927% | 450832958 | 0.00759
GEN-2018-037 | 02 - Nebraska | 156166 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-037 | 1722352 | 100% | 1722352 | 1
GEN-2018-037 | 02 - Nebraska | 156167 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV GEN-2018-037 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-037 | 10260510 | 100% | 10260510 | 1
GEN-2018-013 | 03 - Central | 155729 | ERIS | Abilene Energy Center-Northview 115kV GEN-2018-013 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-013 | 0 | 0% | 0 | 1
GEN-2018-013 | 03 - Central | 155730 | ERIS | Abilene Energy Center-Northview 115kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-013 | 0 | 0% | 0 | 1
GEN-2018-031 | 03 - Central | 155893 | ERIS | Blue Valley 161kV Substation GEN-2018-031 Interconnection (TOIF) (INDN) | Interconnection | Facilitate the interconnection of GEN-2018-031 | 1500000 | 100% | 1500000 | 1
GEN-2018-031 | 03 - Central | 155894 | ERIS | Blue Valley 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-031 | 4500000 | 100% | 4500000 | 1
GEN-2018-009 | 03 - Central | 155901 | ERIS | Cimarron 115kV Substation GEN-2018-009 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2018-009 | 500000 | 100% | 500000 | 1
GEN-2018-009 | 03 - Central | 155902 | ERIS | Cimarron 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-009 | 4000000 | 100% | 4000000 | 1
GEN-2018-057 | 03 - Central | 156035 | ERIS | Gordon Evans 138kV Substation GEN-2018-057 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-057 | 744762 | 100% | 744762 | 1
GEN-2018-057 | 03 - Central | 156036 | ERIS | Gordon Evans 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-057 | 1234682 | 100% | 1234682 | 1
GEN-2018-014 | 03 - Central | 156039 | ERIS | Holt County 345kV Substation GEN-2018-014 Interconnection (TOIF) (TMO) | Interconnection | Facilitate the interconnection of GEN-2018-014 | 0 | 100% | 0 | 1
GEN-2018-014 | 03 - Central | 156040 | ERIS | Holt County 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-014 | 0 | 100% | 0 | 1
GEN-2018-054 | 03 - Central | 156043 | ERIS | KC South - N. Raymore 161kV GEN-2018-054 Interconnection (TOIF) (EMW) | Interconnection | Facilitate the interconnection of GEN-2018-054 | 631242 | 100% | 631242 | 1
GEN-2018-054 | 03 - Central | 156044 | ERIS | KC South - N. Raymore 161kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-054 | 6577588 | 100% | 6577588 | 1
GEN-2018-053 | 03 - Central | 156045 | ERIS | Kelly 161kV Substation GEN-2018-053 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-053 | 842712 | 100% | 842712 | 1
GEN-2018-061 | 03 - Central | 156046 | ERIS | Kelly 161kV Substation GEN-2018-061 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-061 | 842712 | 100% | 842712 | 1
GEN-2018-053 | 03 - Central | 156047 | ERIS | Kelly 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-053 and GEN-2018-061 | 5836541.3333 | 66.67% | 8754812 | 1
GEN-2018-061 | 03 - Central | 156047 | ERIS | Kelly 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-053 and GEN-2018-061 | 2918270.6667 | 33.33% | 8754812 | 1
GEN-2018-030 | 03 - Central | 156162 | ERIS | Lamar-Finney 345kV Substation GEN-2018-030 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-030 | 1975117 | 100% | 1975117 | 1
GEN-2018-030 | 03 - Central | 156163 | ERIS | Lamar-Finney 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-030 | 1152973 | 100% | 1152973 | 1
GEN-2018-022 | 03 - Central | 156168 | ERIS | Mullen Creek 345kV Substation GEN-2018-022 Interconnection (TOIF) (EMW) | Interconnection | Facilitate the interconnection of GEN-2018-022 | 1900000 | 100% | 1900000 | 1
GEN-2018-022 | 03 - Central | 156169 | ERIS | Mullen Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-022 | 5800000 | 100% | 5800000 | 1
GEN-2018-062 | 03 - Central | 156172 | ERIS | Nearman 161kV Substation GEN-2018-062 Interconnection (TOIF) (KACY) | Interconnection | Facilitate the interconnection of GEN-2018-062 | 510232 | 100% | 510232 | 1
GEN-2018-062 | 03 - Central | 156173 | ERIS | Nearman 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-062 | 2005192 | 100% | 2005192 | 1
GEN-2018-032 | 03 - Central | 156174 | ERIS | Neosho 345kV Substation GEN-2018-032 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-032 | 1158673 | 100% | 1158673 | 1
GEN-2018-032 | 03 - Central | 156175 | ERIS | Neosho 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-032 | 2287131 | 100% | 2287131 | 1
GEN-2018-058 | 03 - Central | TBD | ERIS | Build a 50 MVAR SVC at GEN-2018-058 345 kV | Current Study | Install a 50 MVAR SVC at the GEN-2018-058 345 kV substation | 5940292.5 | 50% | 11880585 | 1
GEN-2018-059 | 03 - Central | TBD | ERIS | Build a 50 MVAR SVC at GEN-2018-058 345 kV | Current Study | Install a 50 MVAR SVC at the GEN-2018-058 345 kV substation | 5940292.5 | 50% | 11880585 | 1
GEN-2018-058 | 03 - Central | 156235 | ERIS | Stranger Creek 345kV GEN-2018-058 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-058 | 979960 | 100% | 979960 | 1
GEN-2018-059 | 03 - Central | 156236 | ERIS | Stranger Creek 345kV GEN-2018-059 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-059 | 979960 | 100% | 979960 | 1
GEN-2018-058 | 03 - Central | 156237 | ERIS | Stranger Creek 345kV Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-058 and GEN-2018-059 | 385675 | 50% | 771350 | 1
GEN-2018-059 | 03 - Central | 156237 | ERIS | Stranger Creek 345kV Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-058 and GEN-2018-059 | 385675 | 50% | 771350 | 1
GEN-2018-049 | 03 - Central | 156246 | ERIS | Thistle 345kV Substation GEN-2018-049 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2018-049 | 857280 | 100% | 857280 | 1
GEN-2018-049 | 03 - Central | 156247 | ERIS | Thistle 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-049 | 3000000 | 100% | 3000000 | 1
GEN-2018-024 | 04 - Southeast | 155895 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV GEN-2018-024 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-024 | 1500000 | 100% | 1500000 | 1
GEN-2018-024 | 04 - Southeast | 155896 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-024 | 2500000 | 100% | 2500000 | 1
GEN-2018-021 | 04 - Southeast | TBD | ERIS | GEN-2016-037 Interconnection Costs | Contingent | Facilitate the interconnection of GEN-2018-021 | 0 | 100% | 18000000 | 1
GEN-2018-027 | 04 - Southeast | TBD | ERIS | Delaware Tap to 36th&Lewis 138 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Delaware Tap to 36th&Lewis 138 kV 0.97 mile line with a minimum summer emergency rating of 305 MVA | 935234.23 | 100% | 935234.23 | 0.28572
GEN-2018-011 | 04 - Southeast | 155903 | ERIS | Dover 138 kV Switching Station GEN-2018-011 Interconnection (TOIF) (WFEC) | Interconnection | Facilitate the interconnection of GEN-2018-011 | 1479500 | 100% | 1479500 | 1
GEN-2018-011 | 04 - Southeast | 155904 | ERIS | Dover 138 kV Switching Station Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-011 | 0 | 100% | 0 | 1
GEN-2018-029 | 04 - Southeast | 156041 | ERIS | Horseshoe Lake 138kV Substation GEN-2018-029 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2018-029 | 3500000 | 100% | 3500000 | 1
GEN-2018-029 | 04 - Southeast | 156042 | ERIS | Horseshoe Lake 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-029 | 750000 | 100% | 750000 | 1
GEN-2018-050 | 04 - Southeast | 156164 | ERIS | Longwood 345kV Substation GEN-2018-050 Interconnection (TOIF) (AEPW) | Interconnection | Facilitate the interconnection of GEN-2018-050 | 1541013 | 100% | 1541013 | 1
GEN-2018-050 | 04 - Southeast | 156165 | ERIS | Longwood 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-050 | 8130655 | 100% | 8130655 | 1
GEN-2018-026 | 04 - Southeast | 156170 | ERIS | Mustang 138kV Substation GEN-2018-026 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2018-026 | 750000 | 100% | 750000 | 1
GEN-2018-026 | 04 - Southeast | 156171 | ERIS | Mustang 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-026 | 2000000 | 100% | 2000000 | 1
GEN-2018-003 | 04 - Southeast | TBD | ERIS | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating and winter emergency rating of 173/199 MVA | 1667995.07 | 100% | 1667995.07 | 0.26034
GEN-2018-003 | 04 - Southeast | 156178 | ERIS | North Boston-Bann 138kV GEN-2018-003 Interconnection (TOIF) (AEPW) | Interconnection | Facilitate the interconnection of GEN-2018-003 | 1337068 | 100% | 1337068 | 1
GEN-2018-003 | 04 - Southeast | 156179 | ERIS | North Boston-Bann 138kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-003 | 8857127 | 100% | 8857127 | 1
GEN-2018-048 | 04 - Southeast | 156180 | ERIS | Pecan Creek 345kV Substation GEN-2018-048 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-048 | 1500000 | 100% | 1500000 | 1
GEN-2018-048 | 04 - Southeast | 156182 | ERIS | Pecan Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-048 and GEN-2018-051 (Group 05) | 8955223.8806 | 89.55% | 10000000 | 1
GEN-2018-055 | 04 - Southeast | 156244 | ERIS | Terry Road 345kV Substation (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-055 | 733380 | 100% | 733380 | 1
GEN-2018-055 | 04 - Southeast | 156245 | ERIS | Terry Road 345kV Substation Interconnection Expansion | Interconnection | Facilitate the interconnection of GEN-2018-055 | 50000 | 100% | 50000 | 1
GEN-2018-028 | 04 - Southeast | 156221 | ERIS | Tulsa North 138kV Substation GEN-2018-028 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-028 | 1337068 | 100% | 1337068 | 1
GEN-2018-028 | 04 - Southeast | 156222 | ERIS | Tulsa North 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-028 | 5324780 | 100% | 5324780 | 1
GEN-2018-027 | 04 - Southeast | 156223 | ERIS | Tulsa Power Station 38kV Substation GEN-2018-027 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-027 | 1337068 | 100% | 1337068 | 1
GEN-2018-027 | 04 - Southeast | 156224 | ERIS | Tulsa Power Station 38kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-027 | 9174000 | 100% | 9174000 | 1
GEN-2018-051 | 04 - Southeast | 156181 | ERIS | Pecan Creek 345kV Substation GEN-2018-051 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-051 | 1500000 | 100% | 1500000 | 1
GEN-2018-051 | 04 - Southeast | 156182 | ERIS | Pecan Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-048 and GEN-2018-051 (Group 05) | 1044776.1194 | 10.45% | 10000000 | 1
GEN-2018-052 | 05 - Southwest | 156183 | ERIS | Roadrunner 115kV Substation GEN-2018-052 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-052 | 1128837 | 100% | 1128837 | 1
GEN-2018-052 | 05 - Southwest | 156184 | ERIS | Roadrunner 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-052 | 1039552 | 100% | 1039552 | 1
GEN-2018-004 | 05 - Southwest | 156242 | ERIS | T14 Circuit 115kV GEN-2018-004 Interconnection (TOIF) | Interconnection | Facilitate the interconnection of GEN-2018-004 | 1107176 | 100% | 1107176 | 1
GEN-2018-004 | 05 - Southwest | 156243 | ERIS | T14 Circuit 115kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-004 | 10430297 | 100% | 10430297 | 1
GEN-2018-015 | 05 - Southwest | 156219 | ERIS | Tuco-Oklaunion 345kV GEN-2018-015 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-015 | 1860250 | 100% | 1860250 | 1
GEN-2018-015 | 05 - Southwest | 156220 | ERIS | Tuco-Oklaunion 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-015 | 18641931 | 100% | 18641931 | 1
Total | [8 empty] | 262204687.3

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | Steady State | 01 - North | DISIS-2018-001 | ERIS | Edgeley 115-69 kV Transformer Replacement | TBD | Replace the existing 115/69 kV transformer at Edgeley to a minimum rating of 42 MVA | WAPA | 36 | 2777743
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Edgeley 115kV Substation GEN-2018-039 Interconnection (TOIF) (WAPA) | 155905 | Facilitate the interconnection of GEN-2018-039 | WAPA | TBD | 1709000
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Edgeley 115kV Substation Interconnection Expansion (DISIS-2018-001) | 155906 | Facilitate the interconnection of GEN-2018-039 | WAPA | TBD | 1709000
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Groton-Leland Olds 345kV GEN-2018-008 Interconnection (TOIF) (BEPC) | 156037 | Facilitate the interconnection of GEN-2018-008 | BEPC | 24 | 2334054
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Groton-Leland Olds 345kV Line Tap (DISIS-2018-001) | 156038 | Facilitate the interconnection of GEN-2018-008 | BEPC | 24 | 20903079
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Neset 230kV Substation GEN-2018-010 Interconnection (TOIF) (BEPC) | 156176 | Facilitate the interconnection of GEN-2018-010 | BEPC | 3 | 120000
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Neset 230kV Substation Interconnection Expansion (DISIS-2018-001) | 156177 | Facilitate the interconnection of GEN-2018-010 | BEPC | 0 | 0
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Summit 115kV Substation GEN-2018-007 Interconnection (TOIF) (WAPA) | 156238 | Facilitate the interconnection of GEN-2018-007 | WAPA | TBD | 1565000
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Summit 115kV Substation Interconnection Expansion (DISIS-2018-001) | 156239 | Facilitate the interconnection of GEN-2018-007 | WAPA | TBD | 1565000
Current Study | Steady State | 01 - North | DISIS-2018-001 | ERIS | Summit to Watertown 115 kV Rebuild | TBD | Rebuild the Summit to Watertown 115 kV 30.7 mile line to a minimum rating of 212 MVA | WAPA | 36 | 21822788
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Antelope - Hoskins 345kV GEN-2018-012 Interconnection (TOIF) (NPPD) | 155889 | Facilitate the interconnection of GEN-2018-012 | NPPD | TBD | 1500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Antelope - Hoskins 345kV Line Tap (DISIS-2018-001) | 155890 | Facilitate the interconnection of GEN-2018-012 | NPPD | TBD | 5500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Axtell-Post Rock 345 kV GEN-2018-060 Interconnection (TOIF) (NPPD) | 155891 | Facilitate the interconnection of GEN-2018-060 | NPPD | TBD | 1500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Axtell-Post Rock 345 kV Line Tap (DISIS-2018-001) | 155892 | Facilitate the interconnection of GEN-2018-060 | NPPD | TBD | 50000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Cass County 345kV Substation Interconnection Expansion (DISIS-2018-001) | 155897 | Facilitate the interconnection of GEN-2018-033 | OPPD | 24 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Cass County 345kV Substation Interconnection Expansion GEN-2018-033 Interconnection (TOIF) (OPPD) | 155898 | Facilitate the interconnection of GEN-2018-033 | OPPD | 24 | 1662072
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Calhoun 345kV Substation GEN-2018-025 Interconnection (TOIF) (OPPD) | 155907 | Facilitate the interconnection of GEN-2018-025 | OPPD | 0 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Calhoun 345kV Substation GEN-2018-044 Interconnection (TOIF) (OPPD) | 155908 | Facilitate the interconnection of GEN-2018-044 | OPPD | 0 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Calhoun 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156027 | Facilitate the interconnection of GEN-2018-025 and GEN-2018-044 | OPPD | 24 | 3021587
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV GEN-2018-056 Interconnection (TOIF) (WAPA) | 156028 | Facilitate the interconnection of GEN-2018-056 | WAPA | TBD | 2898000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV Line Tap (DISIS-2018-001) | 156029 | Facilitate the interconnection of GEN-2018-056 | WAPA | TBD | 2898000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Ft. Calhoun - Raun 345 kV GEN-2018-043 Interconnection (TOIF) (OPPD) | 156030 | Facilitate the interconnection of GEN-2018-043 | OPPD | 30 | 8894071
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Ft. Calhoun - Raun 345 kV Line Tap (DISIS-2018-001) | 156031 | Facilitate the interconnection of GEN-2018-043 | OPPD | 0 | 0
Contingent | Steady State | 02 - Nebraska | DISIS-2017-002 | ERIS | Gentleman to Cherry County and Cherry County to Holt new 345 kV line | NTC 200220 | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | NPPD | 36 | 450832958
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV (DISIS-2018-001) | 156166 | Facilitate the interconnection of GEN-2018-037 | OPPD | 24 | 1722352
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV GEN-2018-037 Interconnection (TOIF) (OPPD) | 156167 | Facilitate the interconnection of GEN-2018-037 | OPPD | 24 | 10260510
Current Study | Stability | 03 - Central | DISIS-2018-001 | ERIS | Build a 50 MVAR SVC at GEN-2018-058 345 kV | TBD | Install a 50 MVAR SVC at the GEN-2018-058 345 kV substation | WERE | 36 | 11880585
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Abilene Energy Center-Northview 115kV GEN-2018-013 Interconnection (TOIF) (EKC) | 155729 | Facilitate the interconnection of GEN-2018-013 | WERE | 24 | 0
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Abilene Energy Center-Northview 115kV Line Tap (DISIS-2018-001) | 155730 | Facilitate the interconnection of GEN-2018-013 | WERE | 24 | 0
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Blue Valley 161kV Substation GEN-2018-031 Interconnection (TOIF) (INDN) | 155893 | Facilitate the interconnection of GEN-2018-031 | INDN | 24 | 1500000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Blue Valley 161kV Substation Interconnection Expansion (DISIS-2018-001) | 155894 | Facilitate the interconnection of GEN-2018-031 | INDN | 36 | 4500000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Cimarron 115kV Substation GEN-2018-009 Interconnection (TOIF) (SUNC) | 155901 | Facilitate the interconnection of GEN-2018-009 | SEPC | 33 | 500000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Cimarron 115kV Substation Interconnection Expansion (DISIS-2018-001) | 155902 | Facilitate the interconnection of GEN-2018-009 | SEPC | 33 | 4000000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Gordon Evans 138kV Substation GEN-2018-057 Interconnection (TOIF) (EKC) | 156035 | Facilitate the interconnection of GEN-2018-057 | WERE | 24 | 744762
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Gordon Evans 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156036 | Facilitate the interconnection of GEN-2018-057 | WERE | 24 | 1234682
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Holt County 345kV Substation GEN-2018-014 Interconnection (TOIF) (TMO) | 156039 | Facilitate the interconnection of GEN-2018-014 | WERE | 0 | 0
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Holt County 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156040 | Facilitate the interconnection of GEN-2018-014 | WERE | 48 | 0
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | KC South - N. Raymore 161kV GEN-2018-054 Interconnection (TOIF) (EMW) | 156043 | Facilitate the interconnection of GEN-2018-054 | WERE | 42 | 631242
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | KC South - N. Raymore 161kV Line Tap (DISIS-2018-001) | 156044 | Facilitate the interconnection of GEN-2018-054 | WERE | 42 | 6577588
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Kelly 161kV Substation GEN-2018-053 Interconnection (TOIF) (EKC) | 156045 | Facilitate the interconnection of GEN-2018-053 | WERE | 24 | 842712
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Kelly 161kV Substation GEN-2018-061 Interconnection (TOIF) (EKC) | 156046 | Facilitate the interconnection of GEN-2018-061 | WERE | 24 | 842712
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Kelly 161kV Substation Interconnection Expansion (DISIS-2018-001) | 156047 | Facilitate the interconnection of GEN-2018-053 and GEN-2018-061 | WERE | 24 | 8754812
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Lamar-Finney 345kV Substation GEN-2018-030 Interconnection (TOIF) (SWPS) | 156162 | Facilitate the interconnection of GEN-2018-030 | SPS | 32 | 1975117
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Lamar-Finney 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156163 | Facilitate the interconnection of GEN-2018-030 | SPS | 32 | 1152973
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Mullen Creek 345kV Substation GEN-2018-022 Interconnection (TOIF) (EMW) | 156168 | Facilitate the interconnection of GEN-2018-022 | WERE | 36 | 1900000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Mullen Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156169 | Facilitate the interconnection of GEN-2018-022 | WERE | 36 | 5800000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Nearman 161kV Substation GEN-2018-062 Interconnection (TOIF) (KACY) | 156172 | Facilitate the interconnection of GEN-2018-062 | KACY | 36 | 510232
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Nearman 161kV Substation Interconnection Expansion (DISIS-2018-001) | 156173 | Facilitate the interconnection of GEN-2018-062 | KACY | 36 | 2005192
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Neosho 345kV Substation GEN-2018-032 Interconnection (TOIF) (EKC) | 156174 | Facilitate the interconnection of GEN-2018-032 | WERE | 36 | 1158673
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Neosho 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156175 | Facilitate the interconnection of GEN-2018-032 | WERE | 36 | 2287131
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Stranger Creek 345kV GEN-2018-058 Interconnection (TOIF) (EKC) | 156235 | Facilitate the interconnection of GEN-2018-058 | WERE | 36 | 979960
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Stranger Creek 345kV GEN-2018-059 Interconnection (TOIF) (EKC) | 156236 | Facilitate the interconnection of GEN-2018-059 | WERE | 36 | 979960
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Stranger Creek 345kV Interconnection Expansion (DISIS-2018-001) | 156237 | Facilitate the interconnection of GEN-2018-058 and GEN-2018-059 | WERE | 36 | 771350
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Thistle 345kV Substation GEN-2018-049 Interconnection (TOIF) (ITCGP) | 156246 | Facilitate the interconnection of GEN-2018-049 | ITCGP | TBD | 857280
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Thistle 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156247 | Facilitate the interconnection of GEN-2018-049 | ITCGP | TBD | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV GEN-2018-024 Interconnection (TOIF) (OGE) | 155895 | Facilitate the interconnection of GEN-2018-024 | OGE | 24 | 1500000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV Line Tap (DISIS-2018-001) | 155896 | Facilitate the interconnection of GEN-2018-024 | OGE | 24 | 2500000
Contingent | Steady State | 04 - Southeast | DISIS-2016-001 | ERIS | GEN-2016-037 Interconnection Costs | TBD | Facilitate the interconnection of GEN-2018-021 | AEP | TBD | 18000000
Current Study | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Delaware Tap to 36th&Lewis 138 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing Delaware Tap to 36th&Lewis 138 kV 0.97 mile line with a minimum summer emergency rating of 305 MVA | AEPW | 36 | 935234.23
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Dover 138 kV Switching Station GEN-2018-011 Interconnection (TOIF) (WFEC) | 155903 | Facilitate the interconnection of GEN-2018-011 | WFEC | 36 | 1479500
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Dover 138 kV Switching Station Interconnection Expansion (DISIS-2018-001) | 155904 | Facilitate the interconnection of GEN-2018-011 | WFEC | 0 | 0
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Horseshoe Lake 138kV Substation GEN-2018-029 Interconnection (TOIF) (OKGE) | 156041 | Facilitate the interconnection of GEN-2018-029 | OGE | 24 | 3500000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Horseshoe Lake 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156042 | Facilitate the interconnection of GEN-2018-029 | OGE | 24 | 750000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Longwood 345kV Substation GEN-2018-050 Interconnection (TOIF) (AEPW) | 156164 | Facilitate the interconnection of GEN-2018-050 | AEP | 36 | 1541013
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Longwood 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156165 | Facilitate the interconnection of GEN-2018-050 | AEP | 36 | 8130655
Contingent | Steady State | 04 - Southeast | DISIS-2017-002 | ERIS | Multi - Border - Woodward 345 kV Tap | NTC 210627 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm. | AEPW | 36 | 5264319
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Mustang 138kV Substation GEN-2018-026 Interconnection (TOIF) (OKGE) | 156170 | Facilitate the interconnection of GEN-2018-026 | OGE | 24 | 750000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Mustang 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156171 | Facilitate the interconnection of GEN-2018-026 | OGE | 24 | 2000000
Current Study | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001) | TBD | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating and winter emergency rating of 173/199 MVA | AEPW | 36 | 1667995.07
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | North Boston-Bann 138kV GEN-2018-003 Interconnection (TOIF) (AEPW) | 156178 | Facilitate the interconnection of GEN-2018-003 | AEP | 36 | 1337068
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | North Boston-Bann 138kV Line Tap (DISIS-2018-001) | 156179 | Facilitate the interconnection of GEN-2018-003 | AEP | 36 | 8857127
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Pecan Creek 345kV Substation GEN-2018-048 Interconnection (TOIF) (OGE) | 156180 | Facilitate the interconnection of GEN-2018-048 | OGE | 24 | 1500000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Pecan Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156182 | Facilitate the interconnection of GEN-2018-048 and GEN-2018-051 (Group 05) | OGE | 24 | 10000000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Terry Road 345kV Substation (TOIF) (AEP) | 156244 | Facilitate the interconnection of GEN-2018-055 | AEP | 36 | 733380
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Terry Road 345kV Substation Interconnection Expansion | 156245 | Facilitate the interconnection of GEN-2018-055 | AEP | 36 | 50000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Tulsa North 138kV Substation GEN-2018-028 Interconnection (TOIF) (AEP) | 156221 | Facilitate the interconnection of GEN-2018-028 | AEP | 36 | 1337068
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Tulsa North 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156222 | Facilitate the interconnection of GEN-2018-028 | AEP | 36 | 5324780
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Tulsa Power Station 38kV Substation GEN-2018-027 Interconnection (TOIF) (AEP) | 156223 | Facilitate the interconnection of GEN-2018-027 | AEP | 36 | 1337068
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Tulsa Power Station 38kV Substation Interconnection Expansion (DISIS-2018-001) | 156224 | Facilitate the interconnection of GEN-2018-027 | AEP | 36 | 9174000
Contingent | Steady State | 05 - Southwest | 2021 ITP | ERIS | Crossroads to Hobbs 345 kV New Line (2021 ITP) | TBD | Build approximately 97.38 miles of new 345 kV line from Crossroads to Hobbs | SPS | 36 | 0
Contingent | Steady State | 05 - Southwest | 2021 ITP | ERIS | Hobbs to Roadrunner 345 kV New Line (2021 ITP) | TBD | Build approximately 45.82 miles of new 345 kV line from Hobbs to Roadrunner | SPS | 36 | 0
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Pecan Creek 345kV Substation GEN-2018-051 Interconnection (TOIF) (OGE) | 156181 | Facilitate the interconnection of GEN-2018-051 | OGE | 24 | 1500000
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Roadrunner 115kV Substation GEN-2018-052 Interconnection (TOIF) (SWPS) | 156183 | Facilitate the interconnection of GEN-2018-052 | SPS | 24 | 1128837
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Roadrunner 115kV Substation Interconnection Expansion (DISIS-2018-001) | 156184 | Facilitate the interconnection of GEN-2018-052 | SPS | 24 | 1039552
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | T14 Circuit 115kV GEN-2018-004 Interconnection (TOIF) | 156242 | Facilitate the interconnection of GEN-2018-004 | SPS | 32 | 1107176
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | T14 Circuit 115kV Line Tap (DISIS-2018-001) | 156243 | Facilitate the interconnection of GEN-2018-004 | SPS | 32 | 10430297
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Tuco-Oklaunion 345kV GEN-2018-015 Interconnection (TOIF) (SWPS) | 156219 | Facilitate the interconnection of GEN-2018-015 | SPS | 32 | 1860250
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Tuco-Oklaunion 345kV Line Tap (DISIS-2018-001) | 156220 | Facilitate the interconnection of GEN-2018-015 | SPS | 32 | 18641931
736301964.3

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00NR | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 00NR | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 00NR | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43938 |  | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.56062 |  | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43938 |  | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43938 |  | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43938 |  | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.56062 |  | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.56062 |  | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43938 |  | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43938 |  | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05388 |  | P21:345:UMZW:# 324 #: FT2 IN SD. OPENING OF A LINE SECTION WO A FAULT
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05388 |  | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05388 |  | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05388 |  | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05388 |  | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05388 |  | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Non-Converge | 02ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | N/A | N/A | " | None |  |  |  |  | None
Non-Converge | 04NR | 0 | N/A | N/A | " | None |  |  |  |  | None
Non-Converge | 05ALL | 0 | N/A | N/A | " | None |  |  |  |  | None
Non-Converge | 05NR | 0 | N/A | N/A | " | None |  |  |  |  | None
Thermal | 00NR | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652432 EDGELEY7 115 996773 ED KY6A _1 69.0 1 |  | 38 | 0.23722 | 102.65 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 00NR | 1 | 23SP | GEN-2018-039 | TO -> FROM | 652433 EDGELEY8 69.0 996773 ED KY6A _1 69.0 1 |  | 38 | 0.23722 | 103.58 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 00NR | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652432 EDGELEY7 115 996771 ED KY6A _1 69.0 1 |  | 38 | 0.23502 | 100.95 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 00NR | 1 | 26SP | GEN-2018-039 | TO -> FROM | 652433 EDGELEY8 69.0 996771 ED KY6A _1 69.0 1 |  | 38 | 0.23502 | 101.59 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 00NR | 1 | 26WP | GEN-2018-039 | FROM -> TO | 652432 EDGELEY7 115 996769 ED KY6A _1 69.0 1 |  | 38 | 0.23502 | 107.62 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 00NR | 1 | 26WP | GEN-2018-039 | TO -> FROM | 652433 EDGELEY8 69.0 996769 ED KY6A _1 69.0 1 |  | 38 | 0.23502 | 108.58 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-007 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.46731 | 105.39 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-007 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.46731 | 105.13 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.07591 | 105.39 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.07591 | 105.13 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.06805 | 105.39 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.06805 | 105.13 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 1 | 26SP | GEN-2018-007 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.4669 | 102.13 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 26SP | GEN-2018-007 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.4669 | 101.9 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.07522 | 102.13 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.07522 | 101.9 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.06687 | 102.13 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 652531 WATERTN7 115 1 |  | 186 | 0.06687 | 101.9 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 26WP | GEN-2018-039 | TO -> FROM | 652432 EDGELEY7 115 996769 ED KY6A _1 69.0 1 |  | 37.5 | 0.23738 | 100.37 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 01ALL | 1 | 26WP | GEN-2018-039 | FROM -> TO | 652433 EDGELEY8 69.0 996769 ED KY6A _1 69.0 1 |  | 37.5 | 0.23738 | 101.13 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 01NR | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 02NR | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 03NR | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28061 | 112.81 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28061 | 112.81 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2666 | 110.24 | P42:345:AEPW:WILKES CB 1R30 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2666 | 110.24 | P23:345:AEPW:WILKES CB 1R30 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28258 | 107.03 | P12:138:AEPW:IPC-DOM4:BANN4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26434 | 106.54 | P13:138-345:AEPW:WILKES 4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27739 | 106.38 | P41:345:AEPW:WILKES CB 1U70 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27739 | 106.38 | P23:345:AEPW:WILKES CB 1U70 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26434 | 106.17 | P43:345:AEPW:WILKES CB 1W20 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26434 | 106.17 | P23:345:AEPW:WILKES CB 1W20 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26962 | 104.5 | P12:138:AEPW:OKAY4:TURK4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26962 | 104.5 | P12:HV:EES::OKAY 4:TURK 4%:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27598 | 103.38 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28841 | 103.38 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28841 | 103.38 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26897 | 101.33 | P12:138:AEPW:PATTERS4:OKAY4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26897 | 101.23 | P12:HV:EES::ASHDWNR4:PATTERS4!:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27739 | 100.52 | P12:345:AEPW:WELSH7:WILKES7
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28262 | 100.25 | P12:HV:EES::PATTERS4!:NWTXARK4:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28262 | 100.25 | P12:138:AEPW:PATTERS4:NWTXARK4
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.28404 | 109.1 | P12:138:AEPW:R.S.S.-4:R:96YALE-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.28267 | 103.48 | P12:138:AEPW:R.S.S.-4:S.HUD.-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.28487 | 102.32 | P23:345:AEPW:ONETA CB 3405A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.28487 | 102.32 | P42:345:AEPW:ONETA CB 3405A NBTB+FAULT
Thermal | 04ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 04ALL | 1 | 26SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28129 | 106.27 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 04ALL | 1 | 26SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28129 | 106.27 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.28094 | 108.66 | P12:138:AEPW:R.S.S.-4:R:96YALE-4
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.27955 | 103.15 | P12:138:AEPW:R.S.S.-4:S.HUD.-4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28121 | 130.05 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28121 | 130.05 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27826 | 118.85 | P23:345:AEPW:WILKES CB 1U70 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27826 | 118.85 | P41:345:AEPW:WILKES CB 1U70 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28338 | 116.59 | P12:138:AEPW:IPC-DOM4:BANN4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26758 | 116.53 | P23:345:AEPW:WILKES CB 1R30 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26758 | 116.53 | P42:345:AEPW:WILKES CB 1R30 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28938 | 115.96 | P23:345:AEPW:WELSH CB 10610 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28938 | 115.96 | P42:345:AEPW:WELSH CB 10610 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27019 | 113.5 | P12:138:AEPW:OKAY4:TURK4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27019 | 113.5 | P12:HV:EES::OKAY 4:TURK 4%:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27689 | 113 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27826 | 112.95 | P12:345:AEPW:WELSH7:WILKES7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28316 | 111.08 | P12:HV:EES::PATTERS4!:NWTXARK4:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28316 | 111.08 | P12:138:AEPW:PATTERS4:NWTXARK4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26534 | 110.56 | P13:138-345:AEPW:WILKES 4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 110.15 | P11:22:AEPW:WILKE2-1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26534 | 110.09 | P43:345:AEPW:WILKES CB 1W20 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26534 | 110.09 | P23:345:AEPW:WILKES CB 1W20 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26957 | 109.57 | P12:138:AEPW:PATTERS4:OKAY4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26957 | 109.44 | P12:HV:EES::ASHDWNR4:PATTERS4!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27561 | 108.99 | P43:345:AEPW:DIANA CB 11890 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27561 | 108.99 | P23:345:AEPW:DIANA CB 11890 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27558 | 108.9 | P43:345:AEPW:DIANA CB 10590 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27558 | 108.9 | P23:345:AEPW:DIANA CB 10590 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28771 | 108.46 | P12:345:AEPW:NWTXARK7:WELSH7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27567 | 108.41 | P23:345:AEPW:DIANA CB 12060 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27567 | 108.41 | P42:345:AEPW:DIANA CB 12060 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27614 | 108.38 | P23:345:AEPW:DIANA CB 12000 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27614 | 108.38 | P42:345:AEPW:DIANA CB 12000 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27826 | 108.03 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27826 | 108.03 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27894 | 107.89 | P12:138:AEPW:BANN4:NNBOSTN4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27573 | 107.81 | P12:345:AEPW:WELSH7:DIANA7_CKT1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2757 | 107.71 | P12:345:AEPW:WELSH7:DIANA7_CKT2
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27718 | 107.56 | P23:345:AEPW:DIANA CB 11910 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27718 | 107.56 | P42:345:AEPW:DIANA CB 11910 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28624 | 107.36 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28624 | 107.36 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26439 | 107.36 | P12:69:AEPW:NEWBOST2:BANN2
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28624 | 106.97 | P41:345:AEPW:WELSH CB 11590 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28624 | 106.97 | P23:345:AEPW:WELSH CB 11590 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.56 | P11:20:AEPW:WILKE1-1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2745 | 106.45 | P13:69-138:AEPW:SUGARHL2
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2772 | 106.35 | P12:HV:EES::3PATMOS.W#:FULTON!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.31 | P11:24:CLEC::G1DOLHIL:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.29 | P11:HV:EES::PIRKEY 1:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.29 | P11:24:AEPW:PIRKEY 1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2772 | 106.29 | P12:HV:EES::3COUCH%:FULTON!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2772 | 106.29 | P12:115:EES-EAI:COUCH:LEWISV:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2772 | 106.29 | P12:115:EES-EAI-AEPW:3COUCH:FULTON3
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27576 | 106.25 | P23:345:AEPW:DIANA CB 11900 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27576 | 106.25 | P43:345:AEPW:DIANA CB 11900 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.23 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.23 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27453 | 106.2 | P12:138:AEPW:PERDUE4:EXXONM4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2746 | 106.12 | P43:345:AEPW:DIANA CB 13100 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2746 | 106.12 | P23:345:AEPW:DIANA CB 13100 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.09 | P12:HV:EES::PIRKEY 4:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.09 | P13:138-24:AEPW:PIRKEY 4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 106.06 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27488 | 106 | P13:69-138:AEPW:BANN 2_#2
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27488 | 105.98 | P13:69-138:AEPW:BANN 2_#1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.93 | P11:22:AEPW:WILKE3-1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2662 | 105.93 | P12:138:AEPW:CRAIGJT4:PATTERS4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.92 | P11:HV:EES::1LEWIS_U3 ST:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2662 | 105.91 | P12:HV:EES::ASHDWN_W 4:PATTERS4!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27431 | 105.78 | P12:EHV:EES::MUSKOGE7!:FTSMITH7%:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27431 | 105.78 | P12:345:OKGE:BKRBKR295::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27431 | 105.77 | P42:345:OKGE:SB_DRER7383::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27271 | 105.77 | P12:138:AEPW:IDABEL-4:VALIANT4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27431 | 105.77 | P42:345:OKGE:SB_DRER7382::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27481 | 105.74 | P13:69-138:AEPW:SETEXAR2
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27481 | 105.73 | P12:69:AEPW:SETEXAR2:TEXARK 2
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2772 | 105.71 | P21:115:EES-EAI:COUCH:LEWISV:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2772 | 105.71 | P12:HV:EES::3COUCH%:3LEWISVILLE#:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27573 | 105.59 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27573 | 105.59 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.58 | P11:HV:EES::1NELSN_U7 G1:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.56 | P11:HV:EES::1WAT U3!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.56 | P11:25:EES:WATERF:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.56 | P13:230:EES:WATERF:T6:T7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27281 | 105.53 | P12:138:AEPW:LSSOUTH4:DIANA4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2742 | 105.51 | P22:345:AEP-CLEC::DOLHILL7:BUS
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2742 | 105.51 | P41:345:AEP,CLEC::DOLHILL7::BUS::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27445 | 105.47 | P12:138:AEPW:MARSHL-4:PIRKEY4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.4 | P11:21:EES:RVB:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.4 | P11:HV:EES::1RVR_BND_G1!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.4 | P12:230-21:EES:FCY:RVB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.4 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 105.4 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27561 | 105.38 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27561 | 105.38 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 105.29 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 105.29 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 105.29 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27319 | 105.13 | P12:138:WFEC:GOLDNHL_HUGO::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27319 | 105.13 | P12:138:WFEC:HUGO_GOLDNHL
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 104.06 | Base Case
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27476 | 103.09 | P12:138:AEPW:PETTY 4:WILKES 4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.88 | P11:138:OKGE:BKRBKR_GSU03::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.84 | P12:LV-EHV:EES::MUSKOGE7!:MUSKOG6G:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.84 | P11:345:OKGE:BKRBKR_GSU22::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 102.84 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 102.84 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 102.84 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 102.84 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27477 | 102.79 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27477 | 102.79 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27438 | 102.79 | P23:500:EES-EAI:KEO:B4921
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.79 | P11:EHV:EES::MUSKOG4G:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27471 | 102.79 | P24:345:AMMO::LABADIE:15H
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2742 | 102.76 | P13:345-230:CLEC:DOLET:5092
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2742 | 102.76 | P13:345,230:CLEC::DOLHILL::1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2742 | 102.76 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.74 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.74 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27474 | 102.74 | P23:345:MEC:CBEC 905
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.74 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27925 | 102.73 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27925 | 102.73 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.71 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2739 | 102.7 | P12:HV:EES::LOCKSBRG 4:PATTERS4!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.69 | P11:HV:EES::FULTONU1 1:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.69 | P11:16:AEPW:FULTONU1 1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.69 | P12:HV:EES::FULTON!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.69 | P13:16-115:AEPW:FULTONU1 1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27 | 102.66 | P12:138:AEPW-EES-EAI:SNASHVL4:4MURFRE
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27 | 102.66 | P12:HV:EES::4MURFBORO:SNASHVL4!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27439 | 102.65 | P23:500:EES-EAI:KEO:B4941
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27 | 102.62 | P21:115:EES-EAI:MURFSO:MURFET:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27 | 102.62 | P12:HV:EES::3MURFBORO.S!:3MURFBORO.E#:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27 | 102.61 | P12:115:EES-EAI:MURFSO:MURFET
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27 | 102.61 | P12:HV:EES::3MURFBORO.S!:3HS EHV-W!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.58 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.58 | P12:EHV:EES::7CALAWY 1:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.51 | P11:345:AMMO::CALLAWAY:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27414 | 102.48 | P12:138:ETEC:DOUGLASSVILLE-BLALOCK-ALAMANCE:::HV:
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.47 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.42 | P11:345:MEC-NPPD:COOPER 1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.2739 | 102.4 | P12:138:AEPW:SDIERKS4:PATTERS4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27675 | 102.39 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27675 | 102.38 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.29 | P12:69:AEPW:PATTERS2:NEKOOSA2
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27294 | 102.26 | P12:HV:EES::TURK 4%:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27294 | 102.26 | P13:138-345:AEPW:TURK 4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.13 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27618 | 102.1 | P12:HV:EES::TURK 4%:MANDEVILTP4:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.1 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.1 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.07 | P23:345:AEPW:RIVERSIDE CB 3433A NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.07 | P42:345:AEPW:RIVERSIDE CB 3433A NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27675 | 102.07 | P12:138:AEPW:TURK4:SUGARHL4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27675 | 102.07 | P12:HV:EES::TURK 4%:SUGARHL4:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 102.07 | P12:345:AEPW:R.S.S.-7:COGENT7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.28976 | 101.96 | P12:345:AEPW:NWTXARK7:LYDIA7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27178 | 101.88 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27178 | 101.88 | P23:345:AEPW:LONGWOOD CB 10280 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27 | 101.84 | P12:138:AEPW:PATTERS4:SNASHVL4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27 | 101.84 | P12:HV:EES::PATTERS4!:SNASHVL4!:1
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27684 | 101.79 | P12:345:AEPW:LYDIA7:VALIANT7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27294 | 101.79 | P12:345:AEPW:TURK7:NWTXARK7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27294 | 101.79 | P42:345:AEPW:TURK CB 20150 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27294 | 101.79 | P23:345:AEPW:TURK CB 20150 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27241 | 101.45 | P23:345:AEPW:LONGWOOD CB 1N70 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27241 | 101.45 | P43:345:AEPW:LONGWOOD CB 1N70 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27848 | 101.14 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27274 | 101.08 | P12:345:AEPW:LONGWD7:WILKES7
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27274 | 101.08 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27274 | 101.08 | P42:345:AEPW:LONGWOOD CB 1N60 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 101.02 | P23:345:WERE:WOLF_345-50::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 101.02 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 100.91 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 100.9 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 100.9 | P23:345:WERE:WOLF_345-60::
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27281 | 100.88 | P12:138:AEPW:WILKES4:JEFFRSN4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 100.79 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 100.79 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26907 | 100.72 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.26907 | 100.72 | P23:345:AEPW:WILKES CB 1W10 NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 100.33 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27475 | 100.33 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.274 | 100.08 | P12:138:AEPW:LSSOUTH4:WILKES4
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 100.06 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 100.06 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 100.05 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 100.05 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 100.05 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 04ALL | 1 | 26WP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.27559 | 100.05 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 04NR | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 05NR | 1 | 26L | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 01NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 02NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 03NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 04NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 05NR | 2 | N/A | N/A | None | [7 empty] | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_1 | 3 Phase fault on AURORA 7 (652474) 115 kV Bus a. Apply fault at the AURORA 7 (652474) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA 7 (652474) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_1 | 3 Phase fault on AURORA 7 (652474) 115 kV Bus a. Apply fault at the AURORA 7 (652474) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA 7 (652474) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | 1) Low voltage and protection tripping at GEN-2018-058 and GEN-2018-059 2) High End of Sim Voltage (Near Faulted Bus) - VOLT 652474 [AURORA 7 115.00] - VOLT 655379 [AURORAIP-ER7115.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_10 | 3 Phase fault on WILLISTON27 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_10 | 3 Phase fault on WILLISTON27 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_100 | 3 Phase fault on GR.LS-LO-BE3 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_100 | 3 Phase fault on GR.LS-LO-BE3 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_101 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_101 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_102 | 3 Phase fault on LOGAN___-BE7 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_102 | 3 Phase fault on LOGAN___-BE7 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_103 | 3 Phase fault on LO.LS-GR-BE3 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_103 | 3 Phase fault on LO.LS-GR-BE3 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_104 | 3 Phase fault on LO.LS-FT-BE3 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_104 | 3 Phase fault on LO.LS-FT-BE3 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_105 | 3 Phase fault on LUDDEN -CP7 (659172) 115 kV Bus a. Apply fault at the LUDDEN -CP7 (659172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUDDEN -CP7 (659172) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_105 | 3 Phase fault on LUDDEN -CP7 (659172) 115 kV Bus a. Apply fault at the LUDDEN -CP7 (659172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUDDEN -CP7 (659172) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_106 | 3 Phase fault on WATERTN3 (652529) 345 kV Bus a. Apply fault at the WATERTN3 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_106 | 3 Phase fault on WATERTN3 (652529) 345 kV Bus a. Apply fault at the WATERTN3 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_107 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_107 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_108 | 3 Phase fault on VALLEYC7 (652454) 115 kV Bus a. Apply fault at the VALLEYC7 (652454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC7 (652454) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_108 | 3 Phase fault on VALLEYC7 (652454) 115 kV Bus a. Apply fault at the VALLEYC7 (652454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC7 (652454) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_109 | 3 Phase fault on JAMESTN7 (652445) 115 kV Bus a. Apply fault at the JAMESTN7 (652445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN7 (652445) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_109 | 3 Phase fault on JAMESTN7 (652445) 115 kV Bus a. Apply fault at the JAMESTN7 (652445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN7 (652445) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_11 | 3 Phase fault on ELLENDL4 (661026) 230 kV Bus a. Apply fault at the ELLENDL4 (661026) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 661000 [LEOLA 7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_11 | 3 Phase fault on ELLENDL4 (661026) 230 kV Bus a. Apply fault at the ELLENDL4 (661026) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 661000 [LEOLA 7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_110 | 3 Phase fault on STATELIN-MW7 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_110 | 3 Phase fault on STATELIN-MW7 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_111 | 3 Phase fault on WILISTN7 (652421) 115 kV Bus a. Apply fault at the WILISTN7 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_111 | 3 Phase fault on WILISTN7 (652421) 115 kV Bus a. Apply fault at the WILISTN7 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_112 | 3 Phase fault on SE.WLSTN-MW7 (655938) 115 kV Bus a. Apply fault at the SE.WLSTN-MW7 (655938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_112 | 3 Phase fault on SE.WLSTN-MW7 (655938) 115 kV Bus a. Apply fault at the SE.WLSTN-MW7 (655938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_113 | 3 Phase fault on WHEELS_T-MW7 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_113 | 3 Phase fault on WHEELS_T-MW7 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_114 | 3 Phase fault on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_114 | 3 Phase fault on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_115 | 3 Phase fault on HESS GAS-MW7 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_115 | 3 Phase fault on HESS GAS-MW7 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_116 | 3 Phase fault on NORMANLK-BD7 (655780) 115 kV Bus a. Apply fault at the NORMANLK-BD7 (655780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORMANLK-BD7 (655780) 115.0 kV to LINDAHLS-MW7 (655910) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_116 | 3 Phase fault on NORMANLK-BD7 (655780) 115 kV Bus a. Apply fault at the NORMANLK-BD7 (655780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORMANLK-BD7 (655780) 115.0 kV to LINDAHLS-MW7 (655910) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_117 | 3 Phase fault on MOE -MW7 (655900) 115 kV Bus a. Apply fault at the MOE -MW7 (655900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 b.4. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 b.5. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.6. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.7. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_117 | 3 Phase fault on MOE -MW7 (655900) 115 kV Bus a. Apply fault at the MOE -MW7 (655900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 b.4. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 b.5. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.6. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.7. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_118 | 3 Phase fault on PALERMO -MW7 (655916) 115 kV Bus a. Apply fault at the PALERMO -MW7 (655916) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_118 | 3 Phase fault on PALERMO -MW7 (655916) 115 kV Bus a. Apply fault at the PALERMO -MW7 (655916) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_119 | 3 Phase fault on ROSEGLEN-CP7 (655662) 115 kV Bus a. Apply fault at the ROSEGLEN-CP7 (655662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLS.C-CP7 (655661) 115.0 kV to ROSEGLEN-CP7 (655662) 115.0 kV Transmission Circuit #1 b.2. ROSEGLEN-CP7 (655662) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.3. RAUB TAP-CP7 (655663) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.4. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_119 | 3 Phase fault on ROSEGLEN-CP7 (655662) 115 kV Bus a. Apply fault at the ROSEGLEN-CP7 (655662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLS.C-CP7 (655661) 115.0 kV to ROSEGLEN-CP7 (655662) 115.0 kV Transmission Circuit #1 b.2. ROSEGLEN-CP7 (655662) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.3. RAUB TAP-CP7 (655663) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.4. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_12 | 3 Phase fault on MERRCRT4 (661093) 230 kV Bus a. Apply fault at the MERRCRT4 (661093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRCRT4 (661093) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_12 | 3 Phase fault on MERRCRT4 (661093) 230 kV Bus a. Apply fault at the MERRCRT4 (661093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRCRT4 (661093) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_120 | 3 Phase fault on WATERTN-LNX3 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN-LNX3 (652829) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_120 | 3 Phase fault on WATERTN-LNX3 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN-LNX3 (652829) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_121 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_121 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_122 | 3 Phase fault on TN.LS-JD-BE3 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_122 | 3 Phase fault on TN.LS-JD-BE3 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_123 | 3 Phase fault on WTRWEST7 (658092) 115 kV Bus a. Apply fault at the WTRWEST7 (658092) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTRWEST7 (658092) 115.0 kV to WATERTOWN WA (660092) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_123 | 3 Phase fault on WTRWEST7 (658092) 115 kV Bus a. Apply fault at the WTRWEST7 (658092) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTRWEST7 (658092) 115.0 kV to WATERTOWN WA (660092) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_124 | 3 Phase fault on GARRISN4 (652441) 230 kV Bus a. Apply fault at the GARRISN4 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_124 | 3 Phase fault on GARRISN4 (652441) 230 kV Bus a. Apply fault at the GARRISN4 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_125 | 3 Phase fault on WATERTN7 (652531) 115 kV Bus a. Apply fault at the WATERTN7 (652531) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN7 (652531) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_125 | 3 Phase fault on WATERTN7 (652531) 115 kV Bus a. Apply fault at the WATERTN7 (652531) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN7 (652531) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_126 | 3 Phase fault on OLIVER -MW7 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_126 | 3 Phase fault on OLIVER -MW7 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_127 | 3 Phase fault on GARRISN4 (652441) 230 kV Bus a. Apply fault at the GARRISN4 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_127 | 3 Phase fault on GARRISN4 (652441) 230 kV Bus a. Apply fault at the GARRISN4 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_128 | 3 Phase fault on GARRISN4 (652441) 230 kV Bus a. Apply fault at the GARRISN4 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_128 | 3 Phase fault on GARRISN4 (652441) 230 kV Bus a. Apply fault at the GARRISN4 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_129 | 3 Phase fault on GARRISN4 (652441) 230 kV Bus a. Apply fault at the GARRISN4 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_129 | 3 Phase fault on GARRISN4 (652441) 230 kV Bus a. Apply fault at the GARRISN4 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_13 | 3 Phase fault on STANLEY7 (661080) 115 kV Bus a. Apply fault at the STANLEY7 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_13 | 3 Phase fault on STANLEY7 (661080) 115 kV Bus a. Apply fault at the STANLEY7 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_130 | 3 Phase fault on ELLISVIL-MW7 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_130 | 3 Phase fault on ELLISVIL-MW7 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_131 | 3 Phase fault on NESET___-BE4 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_131 | 3 Phase fault on NESET___-BE4 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_132 | 3 Phase fault on SATTER -MW7 (655967) 115 kV Bus a. Apply fault at the SATTER -MW7 (655967) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATTER -MW7 (655967) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_132 | 3 Phase fault on SATTER -MW7 (655967) 115 kV Bus a. Apply fault at the SATTER -MW7 (655967) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATTER -MW7 (655967) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_133 | 3 Phase fault on G17-094-TAP (589324) 230 kV Bus a. Apply fault at the G17-094-TAP (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_133 | 3 Phase fault on G17-094-TAP (589324) 230 kV Bus a. Apply fault at the G17-094-TAP (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_134 | 3 Phase fault on G17-094-TAP (589324) 230 kV Bus a. Apply fault at the G17-094-TAP (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_134 | 3 Phase fault on G17-094-TAP (589324) 230 kV Bus a. Apply fault at the G17-094-TAP (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_135 | 3 Phase fault on SQBP1DC4 (608597) 230 kV Bus a. Apply fault at the SQBP1DC4 (608597) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBP1DC4 (608597) 230.0 kV to SQBEAST4 (608602) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_135 | 3 Phase fault on SQBP1DC4 (608597) 230 kV Bus a. Apply fault at the SQBP1DC4 (608597) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBP1DC4 (608597) 230.0 kV to SQBEAST4 (608602) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_136 | 3 Phase fault on SQBP2DC4 (608599) 230 kV Bus a. Apply fault at the SQBP2DC4 (608599) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBP2DC4 (608599) 230.0 kV to SQBEAST4 (608602) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_136 | 3 Phase fault on SQBP2DC4 (608599) 230 kV Bus a. Apply fault at the SQBP2DC4 (608599) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBP2DC4 (608599) 230.0 kV to SQBEAST4 (608602) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_137 | 3 Phase fault on GWINNER7 (620262) 115 kV Bus a. Apply fault at the GWINNER7 (620262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GWINNER7 (620262) 115.0 kV to HOVING__-CP7 (655698) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_137 | 3 Phase fault on GWINNER7 (620262) 115 kV Bus a. Apply fault at the GWINNER7 (620262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GWINNER7 (620262) 115.0 kV to HOVING__-CP7 (655698) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_138 | 3 Phase fault on VALLEYC8 (652204) 69 kV Bus a. Apply fault at the VALLEYC8 (652204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC8 (652204) 69.0 kV to MPC-VCY8 (657804) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_138 | 3 Phase fault on VALLEYC8 (652204) 69 kV Bus a. Apply fault at the VALLEYC8 (652204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC8 (652204) 69.0 kV to MPC-VCY8 (657804) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_139 | 3 Phase fault on SUMMIT-8 (652209) 69 kV Bus a. Apply fault at the SUMMIT-8 (652209) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-8 (652209) 69.0 kV to MOS-WLMT-ER8 (655113) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_139 | 3 Phase fault on SUMMIT-8 (652209) 69 kV Bus a. Apply fault at the SUMMIT-8 (652209) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-8 (652209) 69.0 kV to MOS-WLMT-ER8 (655113) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_14 | 3 Phase fault on KENMARE7 (661052) 115 kV Bus a. Apply fault at the KENMARE7 (661052) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_14 | 3 Phase fault on KENMARE7 (661052) 115 kV Bus a. Apply fault at the KENMARE7 (661052) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_140 | 3 Phase fault on SUMMIT-8 (652209) 69 kV Bus a. Apply fault at the SUMMIT-8 (652209) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-8 (652209) 69.0 kV to MOS-MARV-ER8 (655118) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_140 | 3 Phase fault on SUMMIT-8 (652209) 69 kV Bus a. Apply fault at the SUMMIT-8 (652209) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-8 (652209) 69.0 kV to MOS-MARV-ER8 (655118) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_141 | 3 Phase fault on SUMMIT-8 (652209) 69 kV Bus a. Apply fault at the SUMMIT-8 (652209) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-8 (652209) 69.0 kV to MOS-ORTY-ER8 (655125) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_141 | 3 Phase fault on SUMMIT-8 (652209) 69 kV Bus a. Apply fault at the SUMMIT-8 (652209) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-8 (652209) 69.0 kV to MOS-ORTY-ER8 (655125) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_142 | 3 Phase fault on WATERT18 (652242) 69 kV Bus a. Apply fault at the WATERT18 (652242) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERT18 (652242) 69.0 kV to MOS-RVLE-ER8 (655108) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_142 | 3 Phase fault on WATERT18 (652242) 69 kV Bus a. Apply fault at the WATERT18 (652242) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERT18 (652242) 69.0 kV to MOS-RVLE-ER8 (655108) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_143 | 3 Phase fault on WATERT18 (652242) 69 kV Bus a. Apply fault at the WATERT18 (652242) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERT18 (652242) 69.0 kV to SW-SHERI-ER8 (655111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_143 | 3 Phase fault on WATERT18 (652242) 69 kV Bus a. Apply fault at the WATERT18 (652242) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERT18 (652242) 69.0 kV to SW-SHERI-ER8 (655111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_144 | 3 Phase fault on GROTON18 (652250) 69 kV Bus a. Apply fault at the GROTON18 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_144 | 3 Phase fault on GROTON18 (652250) 69 kV Bus a. Apply fault at the GROTON18 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_145 | 3 Phase fault on HURON 8 (652284) 69 kV Bus a. Apply fault at the HURON 8 (652284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to SW-HURN2-ER8 (655066) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_145 | 3 Phase fault on HURON 8 (652284) 69 kV Bus a. Apply fault at the HURON 8 (652284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to SW-HURN2-ER8 (655066) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_146 | 3 Phase fault on HURON 8 (652284) 69 kV Bus a. Apply fault at the HURON 8 (652284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to SW-HURN3-ER8 (655067) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_146 | 3 Phase fault on HURON 8 (652284) 69 kV Bus a. Apply fault at the HURON 8 (652284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to SW-HURN3-ER8 (655067) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_147 | 3 Phase fault on ROBERTSCTY8 (652361) 69 kV Bus a. Apply fault at the ROBERTSCTY8 (652361) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROBERTSCTY8 (652361) 69.0 kV to SISSETON-ER8 (655303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_147 | 3 Phase fault on ROBERTSCTY8 (652361) 69 kV Bus a. Apply fault at the ROBERTSCTY8 (652361) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROBERTSCTY8 (652361) 69.0 kV to SISSETON-ER8 (655303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_148 | 3 Phase fault on ROBERTSCTY8 (652361) 69 kV Bus a. Apply fault at the ROBERTSCTY8 (652361) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROBERTSCTY8 (652361) 69.0 kV to VEBLEN-ER8 (655455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_148 | 3 Phase fault on ROBERTSCTY8 (652361) 69 kV Bus a. Apply fault at the ROBERTSCTY8 (652361) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROBERTSCTY8 (652361) 69.0 kV to VEBLEN-ER8 (655455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_149 | 3 Phase fault on WILISTN4 (652400) 230 kV Bus a. Apply fault at the WILISTN4 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_149 | 3 Phase fault on WILISTN4 (652400) 230 kV Bus a. Apply fault at the WILISTN4 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_15 | 3 Phase fault on TIOGA4 7 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_15 | 3 Phase fault on TIOGA4 7 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_150 | 3 Phase fault on WILISTN4 (652400) 230 kV Bus a. Apply fault at the WILISTN4 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_150 | 3 Phase fault on WILISTN4 (652400) 230 kV Bus a. Apply fault at the WILISTN4 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_151 | 3 Phase fault on BISMARK4 (652426) 230 kV Bus a. Apply fault at the BISMARK4 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_151 | 3 Phase fault on BISMARK4 (652426) 230 kV Bus a. Apply fault at the BISMARK4 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_152 | 3 Phase fault on CARNGTN7 (652428) 115 kV Bus a. Apply fault at the CARNGTN7 (652428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_152 | 3 Phase fault on CARNGTN7 (652428) 115 kV Bus a. Apply fault at the CARNGTN7 (652428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_153 | 3 Phase fault on EDGELEY7 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_153 | 3 Phase fault on EDGELEY7 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_154 | 3 Phase fault on EDGELEY7 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_154 | 3 Phase fault on EDGELEY7 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_155 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_155 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_156 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_156 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_157 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV to ROBERTSCTY7 (652455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_157 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV to ROBERTSCTY7 (652455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_158 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_158 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_159 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV to LUDDEN -CP7 (659172) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_159 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV to LUDDEN -CP7 (659172) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_16 | 3 Phase fault on TIOGA7 7 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_16 | 3 Phase fault on TIOGA7 7 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_160 | 3 Phase fault on JAMESTN7 (652445) 115 kV Bus a. Apply fault at the JAMESTN7 (652445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_160 | 3 Phase fault on JAMESTN7 (652445) 115 kV Bus a. Apply fault at the JAMESTN7 (652445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_161 | 3 Phase fault on ROBERTSCTY7 (652455) 115 kV Bus a. Apply fault at the ROBERTSCTY7 (652455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_161 | 3 Phase fault on ROBERTSCTY7 (652455) 115 kV Bus a. Apply fault at the ROBERTSCTY7 (652455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_162 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_162 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_163 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_163 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_164 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_164 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_165 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_165 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_166 | 3 Phase fault on HURON 4 (652514) 230 kV Bus a. Apply fault at the HURON 4 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_166 | 3 Phase fault on HURON 4 (652514) 230 kV Bus a. Apply fault at the HURON 4 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_167 | 3 Phase fault on HURON 7 (652515) 115 kV Bus a. Apply fault at the HURON 7 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_167 | 3 Phase fault on HURON 7 (652515) 115 kV Bus a. Apply fault at the HURON 7 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_168 | 3 Phase fault on SUMMIT-7 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_168 | 3 Phase fault on SUMMIT-7 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_169 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_169 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_17 | 3 Phase fault on RAY JCT7 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_17 | 3 Phase fault on RAY JCT7 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_170 | 3 Phase fault on GROTONSOUTH7 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_170 | 3 Phase fault on GROTONSOUTH7 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_171 | 3 Phase fault on GROTONSOUTH7 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_171 | 3 Phase fault on GROTONSOUTH7 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_172 | 3 Phase fault on GROTONSOUTH7 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_172 | 3 Phase fault on GROTONSOUTH7 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_173 | 3 Phase fault on GROTONSOUTH7 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_173 | 3 Phase fault on GROTONSOUTH7 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_174 | 3 Phase fault on MOS-MILR-ER8 (655053) 69 kV Bus a. Apply fault at the MOS-MILR-ER8 (655053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-MILR-ER8 (655053) 69.0 kV to SW-HURN4-ER8 (655064) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_174 | 3 Phase fault on MOS-MILR-ER8 (655053) 69 kV Bus a. Apply fault at the MOS-MILR-ER8 (655053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-MILR-ER8 (655053) 69.0 kV to SW-HURN4-ER8 (655064) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_175 | 3 Phase fault on MOS-HRON-ER8 (655058) 69 kV Bus a. Apply fault at the MOS-HRON-ER8 (655058) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-HRON-ER8 (655058) 69.0 kV to HURON-ER8 (655231) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_175 | 3 Phase fault on MOS-HRON-ER8 (655058) 69 kV Bus a. Apply fault at the MOS-HRON-ER8 (655058) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-HRON-ER8 (655058) 69.0 kV to HURON-ER8 (655231) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_176 | 3 Phase fault on SW-HURN4-ER8 (655064) 69 kV Bus a. Apply fault at the SW-HURN4-ER8 (655064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-HURN4-ER8 (655064) 69.0 kV to SW-HURN2-ER8 (655066) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_176 | 3 Phase fault on SW-HURN4-ER8 (655064) 69 kV Bus a. Apply fault at the SW-HURN4-ER8 (655064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-HURN4-ER8 (655064) 69.0 kV to SW-HURN2-ER8 (655066) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_177 | 3 Phase fault on MOS-YLTI-ER8 (655065) 69 kV Bus a. Apply fault at the MOS-YLTI-ER8 (655065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-YLTI-ER8 (655065) 69.0 kV to MORNINGS-ER8 (655236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_177 | 3 Phase fault on MOS-YLTI-ER8 (655065) 69 kV Bus a. Apply fault at the MOS-YLTI-ER8 (655065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-YLTI-ER8 (655065) 69.0 kV to MORNINGS-ER8 (655236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_178 | 3 Phase fault on SW-HURN3-ER8 (655067) 69 kV Bus a. Apply fault at the SW-HURN3-ER8 (655067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-HURN3-ER8 (655067) 69.0 kV to MORNINGS-ER8 (655236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_178 | 3 Phase fault on SW-HURN3-ER8 (655067) 69 kV Bus a. Apply fault at the SW-HURN3-ER8 (655067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-HURN3-ER8 (655067) 69.0 kV to MORNINGS-ER8 (655236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_179 | 3 Phase fault on MOS-WOLS-ER8 (655069) 69 kV Bus a. Apply fault at the MOS-WOLS-ER8 (655069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-WOLS-ER8 (655069) 69.0 kV to VIRGIL-ER8 (655241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_179 | 3 Phase fault on MOS-WOLS-ER8 (655069) 69 kV Bus a. Apply fault at the MOS-WOLS-ER8 (655069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-WOLS-ER8 (655069) 69.0 kV to VIRGIL-ER8 (655241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_18 | 3 Phase fault on KENMARE7 (661052) 115 kV Bus a. Apply fault at the KENMARE7 (661052) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_18 | 3 Phase fault on KENMARE7 (661052) 115 kV Bus a. Apply fault at the KENMARE7 (661052) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_180 | 3 Phase fault on MOS-VRCV-ER8 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER8 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to MOS-DAK-ER8 (655071) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_180 | 3 Phase fault on MOS-VRCV-ER8 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER8 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to MOS-DAK-ER8 (655071) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_181 | 3 Phase fault on MOS-VRCV-ER8 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER8 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to VIRGIL-ER8 (655241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_181 | 3 Phase fault on MOS-VRCV-ER8 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER8 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to VIRGIL-ER8 (655241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_182 | 3 Phase fault on MOS-VRCV-ER8 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER8 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to CAVOUR-ER8 (655242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_182 | 3 Phase fault on MOS-VRCV-ER8 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER8 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to CAVOUR-ER8 (655242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_183 | 3 Phase fault on MOS-DAK-ER8 (655071) 69 kV Bus a. Apply fault at the MOS-DAK-ER8 (655071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-DAK-ER8 (655071) 69.0 kV to DAKOTA-ER8 (655244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_183 | 3 Phase fault on MOS-DAK-ER8 (655071) 69 kV Bus a. Apply fault at the MOS-DAK-ER8 (655071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-DAK-ER8 (655071) 69.0 kV to DAKOTA-ER8 (655244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_184 | 3 Phase fault on MOS-CLRM-ER8 (655082) 69 kV Bus a. Apply fault at the MOS-CLRM-ER8 (655082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CLRM-ER8 (655082) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_184 | 3 Phase fault on MOS-CLRM-ER8 (655082) 69 kV Bus a. Apply fault at the MOS-CLRM-ER8 (655082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CLRM-ER8 (655082) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_185 | 3 Phase fault on MOS-BRTO-ER8 (655083) 69 kV Bus a. Apply fault at the MOS-BRTO-ER8 (655083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-BRTO-ER8 (655083) 69.0 kV to SW-LANGF-ER8 (655433) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_185 | 3 Phase fault on MOS-BRTO-ER8 (655083) 69 kV Bus a. Apply fault at the MOS-BRTO-ER8 (655083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-BRTO-ER8 (655083) 69.0 kV to SW-LANGF-ER8 (655433) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_186 | 3 Phase fault on MOS-BRTO-ER8 (655083) 69 kV Bus a. Apply fault at the MOS-BRTO-ER8 (655083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-BRTO-ER8 (655083) 69.0 kV to BRISTOL-ER8 (655458) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_186 | 3 Phase fault on MOS-BRTO-ER8 (655083) 69 kV Bus a. Apply fault at the MOS-BRTO-ER8 (655083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-BRTO-ER8 (655083) 69.0 kV to BRISTOL-ER8 (655458) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_187 | 3 Phase fault on MOS-SWAB-ER8 (655085) 69 kV Bus a. Apply fault at the MOS-SWAB-ER8 (655085) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-SWAB-ER8 (655085) 69.0 kV to BATH-ER8 (655269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_187 | 3 Phase fault on MOS-SWAB-ER8 (655085) 69 kV Bus a. Apply fault at the MOS-SWAB-ER8 (655085) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-SWAB-ER8 (655085) 69.0 kV to BATH-ER8 (655269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_188 | 3 Phase fault on MOS-IPAB-ER8 (655086) 69 kV Bus a. Apply fault at the MOS-IPAB-ER8 (655086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-IPAB-ER8 (655086) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_188 | 3 Phase fault on MOS-IPAB-ER8 (655086) 69 kV Bus a. Apply fault at the MOS-IPAB-ER8 (655086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-IPAB-ER8 (655086) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_189 | 3 Phase fault on MOS-ABDN-ER8 (655087) 69 kV Bus a. Apply fault at the MOS-ABDN-ER8 (655087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ABDN-ER8 (655087) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_189 | 3 Phase fault on MOS-ABDN-ER8 (655087) 69 kV Bus a. Apply fault at the MOS-ABDN-ER8 (655087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ABDN-ER8 (655087) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_19 | 3 Phase fault on TIOGA4 7 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_19 | 3 Phase fault on TIOGA4 7 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_190 | 3 Phase fault on SW-IPABD-ER8 (655089) 69 kV Bus a. Apply fault at the SW-IPABD-ER8 (655089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-IPABD-ER8 (655089) 69.0 kV to IPABRDEN-ER8 (655264) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_190 | 3 Phase fault on SW-IPABD-ER8 (655089) 69 kV Bus a. Apply fault at the SW-IPABD-ER8 (655089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-IPABD-ER8 (655089) 69.0 kV to IPABRDEN-ER8 (655264) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_191 | 3 Phase fault on SW-IPABD-ER8 (655089) 69 kV Bus a. Apply fault at the SW-IPABD-ER8 (655089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-IPABD-ER8 (655089) 69.0 kV to BATH-ER8 (655269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_191 | 3 Phase fault on SW-IPABD-ER8 (655089) 69 kV Bus a. Apply fault at the SW-IPABD-ER8 (655089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-IPABD-ER8 (655089) 69.0 kV to BATH-ER8 (655269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_192 | 3 Phase fault on MOS-CSTL-ER8 (655107) 69 kV Bus a. Apply fault at the MOS-CSTL-ER8 (655107) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CSTL-ER8 (655107) 69.0 kV to SW-SHERI-ER8 (655111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_192 | 3 Phase fault on MOS-CSTL-ER8 (655107) 69 kV Bus a. Apply fault at the MOS-CSTL-ER8 (655107) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CSTL-ER8 (655107) 69.0 kV to SW-SHERI-ER8 (655111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_193 | 3 Phase fault on MOS-CSTL-ER8 (655107) 69 kV Bus a. Apply fault at the MOS-CSTL-ER8 (655107) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CSTL-ER8 (655107) 69.0 kV to MOS-DMPS-ER8 (655112) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_193 | 3 Phase fault on MOS-CSTL-ER8 (655107) 69 kV Bus a. Apply fault at the MOS-CSTL-ER8 (655107) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CSTL-ER8 (655107) 69.0 kV to MOS-DMPS-ER8 (655112) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_194 | 3 Phase fault on MOS-RVLE-ER8 (655108) 69 kV Bus a. Apply fault at the MOS-RVLE-ER8 (655108) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RVLE-ER8 (655108) 69.0 kV to WAVERLY-ER8 (655297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_194 | 3 Phase fault on MOS-RVLE-ER8 (655108) 69 kV Bus a. Apply fault at the MOS-RVLE-ER8 (655108) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RVLE-ER8 (655108) 69.0 kV to WAVERLY-ER8 (655297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_195 | 3 Phase fault on MOS-PEEV-ER8 (655109) 69 kV Bus a. Apply fault at the MOS-PEEV-ER8 (655109) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-PEEV-ER8 (655109) 69.0 kV to WILMOT-ER8 (655302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_195 | 3 Phase fault on MOS-PEEV-ER8 (655109) 69 kV Bus a. Apply fault at the MOS-PEEV-ER8 (655109) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-PEEV-ER8 (655109) 69.0 kV to WILMOT-ER8 (655302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_196 | 3 Phase fault on MOS-PEEV-ER8 (655109) 69 kV Bus a. Apply fault at the MOS-PEEV-ER8 (655109) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-PEEV-ER8 (655109) 69.0 kV to MOS-GRNV-ER8 (655392) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_196 | 3 Phase fault on MOS-PEEV-ER8 (655109) 69 kV Bus a. Apply fault at the MOS-PEEV-ER8 (655109) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-PEEV-ER8 (655109) 69.0 kV to MOS-GRNV-ER8 (655392) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_197 | 3 Phase fault on MOS-BGST-ER8 (655110) 69 kV Bus a. Apply fault at the MOS-BGST-ER8 (655110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-BGST-ER8 (655110) 69.0 kV to SW-BIGST-ER8 (655114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_197 | 3 Phase fault on MOS-BGST-ER8 (655110) 69 kV Bus a. Apply fault at the MOS-BGST-ER8 (655110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-BGST-ER8 (655110) 69.0 kV to SW-BIGST-ER8 (655114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_198 | 3 Phase fault on MOS-BGST-ER8 (655110) 69 kV Bus a. Apply fault at the MOS-BGST-ER8 (655110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-BGST-ER8 (655110) 69.0 kV to BIGSTONE-ER8 (655287) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_198 | 3 Phase fault on MOS-BGST-ER8 (655110) 69 kV Bus a. Apply fault at the MOS-BGST-ER8 (655110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-BGST-ER8 (655110) 69.0 kV to BIGSTONE-ER8 (655287) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_199 | 3 Phase fault on SW-SHERI-ER8 (655111) 69 kV Bus a. Apply fault at the SW-SHERI-ER8 (655111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-SHERI-ER8 (655111) 69.0 kV to SHERIDAN-ER8 (655288) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_199 | 3 Phase fault on SW-SHERI-ER8 (655111) 69 kV Bus a. Apply fault at the SW-SHERI-ER8 (655111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-SHERI-ER8 (655111) 69.0 kV to SHERIDAN-ER8 (655288) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_2 | 3 Phase fault on BROOKNG7 (652504) 115 kV Bus a. Apply fault at the BROOKNG7 (652504) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKNG7 (652504) 115.0 kV to WHITE 7 (652538) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_2 | 3 Phase fault on BROOKNG7 (652504) 115 kV Bus a. Apply fault at the BROOKNG7 (652504) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKNG7 (652504) 115.0 kV to WHITE 7 (652538) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_20 | 3 Phase fault on TIOGA7 7 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_20 | 3 Phase fault on TIOGA7 7 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_200 | 3 Phase fault on MOS-WLMT-ER8 (655113) 69 kV Bus a. Apply fault at the MOS-WLMT-ER8 (655113) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-WLMT-ER8 (655113) 69.0 kV to WILMOT-ER8 (655302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_200 | 3 Phase fault on MOS-WLMT-ER8 (655113) 69 kV Bus a. Apply fault at the MOS-WLMT-ER8 (655113) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-WLMT-ER8 (655113) 69.0 kV to WILMOT-ER8 (655302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_201 | 3 Phase fault on SW-BIGST-ER8 (655114) 69 kV Bus a. Apply fault at the SW-BIGST-ER8 (655114) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-BIGST-ER8 (655114) 69.0 kV to MOS-MARV-ER8 (655118) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_201 | 3 Phase fault on SW-BIGST-ER8 (655114) 69 kV Bus a. Apply fault at the SW-BIGST-ER8 (655114) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-BIGST-ER8 (655114) 69.0 kV to MOS-MARV-ER8 (655118) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_202 | 3 Phase fault on MOS-MARV-ER8 (655118) 69 kV Bus a. Apply fault at the MOS-MARV-ER8 (655118) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-MARV-ER8 (655118) 69.0 kV to MARVIN-ER8 (655292) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_202 | 3 Phase fault on MOS-MARV-ER8 (655118) 69 kV Bus a. Apply fault at the MOS-MARV-ER8 (655118) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-MARV-ER8 (655118) 69.0 kV to MARVIN-ER8 (655292) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_203 | 3 Phase fault on SW-PEEVR-ER8 (655121) 69 kV Bus a. Apply fault at the SW-PEEVR-ER8 (655121) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-PEEVR-ER8 (655121) 69.0 kV to MOS-SISS-ER8 (655123) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_203 | 3 Phase fault on SW-PEEVR-ER8 (655121) 69 kV Bus a. Apply fault at the SW-PEEVR-ER8 (655121) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-PEEVR-ER8 (655121) 69.0 kV to MOS-SISS-ER8 (655123) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_204 | 3 Phase fault on SW-PEEVR-ER8 (655121) 69 kV Bus a. Apply fault at the SW-PEEVR-ER8 (655121) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-PEEVR-ER8 (655121) 69.0 kV to PEEVER-ER8 (655299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_204 | 3 Phase fault on SW-PEEVR-ER8 (655121) 69 kV Bus a. Apply fault at the SW-PEEVR-ER8 (655121) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-PEEVR-ER8 (655121) 69.0 kV to PEEVER-ER8 (655299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_205 | 3 Phase fault on MOS-FLRN-ER8 (655122) 69 kV Bus a. Apply fault at the MOS-FLRN-ER8 (655122) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-FLRN-ER8 (655122) 69.0 kV to WAVERLY-ER8 (655297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_205 | 3 Phase fault on MOS-FLRN-ER8 (655122) 69 kV Bus a. Apply fault at the MOS-FLRN-ER8 (655122) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-FLRN-ER8 (655122) 69.0 kV to WAVERLY-ER8 (655297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_206 | 3 Phase fault on MOS-FLRN-ER8 (655122) 69 kV Bus a. Apply fault at the MOS-FLRN-ER8 (655122) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-FLRN-ER8 (655122) 69.0 kV to RAUVILLE-ER8 (655305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_206 | 3 Phase fault on MOS-FLRN-ER8 (655122) 69 kV Bus a. Apply fault at the MOS-FLRN-ER8 (655122) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-FLRN-ER8 (655122) 69.0 kV to RAUVILLE-ER8 (655305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_207 | 3 Phase fault on MOS-SISS-ER8 (655123) 69 kV Bus a. Apply fault at the MOS-SISS-ER8 (655123) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-SISS-ER8 (655123) 69.0 kV to VICTOR-ER8 (655301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_207 | 3 Phase fault on MOS-SISS-ER8 (655123) 69 kV Bus a. Apply fault at the MOS-SISS-ER8 (655123) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-SISS-ER8 (655123) 69.0 kV to VICTOR-ER8 (655301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_208 | 3 Phase fault on MOS-SISS-ER8 (655123) 69 kV Bus a. Apply fault at the MOS-SISS-ER8 (655123) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-SISS-ER8 (655123) 69.0 kV to SISSETON-ER8 (655303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_208 | 3 Phase fault on MOS-SISS-ER8 (655123) 69 kV Bus a. Apply fault at the MOS-SISS-ER8 (655123) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-SISS-ER8 (655123) 69.0 kV to SISSETON-ER8 (655303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_209 | 3 Phase fault on MOS-ORTY-ER8 (655125) 69 kV Bus a. Apply fault at the MOS-ORTY-ER8 (655125) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ORTY-ER8 (655125) 69.0 kV to ORTLEY-ER8 (655306) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_209 | 3 Phase fault on MOS-ORTY-ER8 (655125) 69 kV Bus a. Apply fault at the MOS-ORTY-ER8 (655125) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ORTY-ER8 (655125) 69.0 kV to ORTLEY-ER8 (655306) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_21 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_21 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_210 | 3 Phase fault on ANDOVER-ER8 (655257) 69 kV Bus a. Apply fault at the ANDOVER-ER8 (655257) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDOVER-ER8 (655257) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_210 | 3 Phase fault on ANDOVER-ER8 (655257) 69 kV Bus a. Apply fault at the ANDOVER-ER8 (655257) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDOVER-ER8 (655257) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_211 | 3 Phase fault on LANGFORD-ER8 (655258) 69 kV Bus a. Apply fault at the LANGFORD-ER8 (655258) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANGFORD-ER8 (655258) 69.0 kV to SW-LANGF-ER8 (655433) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_211 | 3 Phase fault on LANGFORD-ER8 (655258) 69 kV Bus a. Apply fault at the LANGFORD-ER8 (655258) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANGFORD-ER8 (655258) 69.0 kV to SW-LANGF-ER8 (655433) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_212 | 3 Phase fault on WEBSTER-ER8 (655260) 69 kV Bus a. Apply fault at the WEBSTER-ER8 (655260) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBSTER-ER8 (655260) 69.0 kV to IPWEBSTR-ER8 (655263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_212 | 3 Phase fault on WEBSTER-ER8 (655260) 69 kV Bus a. Apply fault at the WEBSTER-ER8 (655260) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBSTER-ER8 (655260) 69.0 kV to IPWEBSTR-ER8 (655263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_213 | 3 Phase fault on WEBSTER-ER8 (655260) 69 kV Bus a. Apply fault at the WEBSTER-ER8 (655260) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBSTER-ER8 (655260) 69.0 kV to BRISTOL-ER8 (655458) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_213 | 3 Phase fault on WEBSTER-ER8 (655260) 69 kV Bus a. Apply fault at the WEBSTER-ER8 (655260) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBSTER-ER8 (655260) 69.0 kV to BRISTOL-ER8 (655458) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_214 | 3 Phase fault on ABERDEEN-ER8 (655262) 69 kV Bus a. Apply fault at the ABERDEEN-ER8 (655262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_214 | 3 Phase fault on ABERDEEN-ER8 (655262) 69 kV Bus a. Apply fault at the ABERDEEN-ER8 (655262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_215 | 3 Phase fault on IPWEBSTR-ER8 (655263) 69 kV Bus a. Apply fault at the IPWEBSTR-ER8 (655263) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPWEBSTR-ER8 (655263) 69.0 kV to NWPS6661-ER8 (655369) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_215 | 3 Phase fault on IPWEBSTR-ER8 (655263) 69 kV Bus a. Apply fault at the IPWEBSTR-ER8 (655263) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPWEBSTR-ER8 (655263) 69.0 kV to NWPS6661-ER8 (655369) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_216 | 3 Phase fault on BATH-ER8 (655269) 69 kV Bus a. Apply fault at the BATH-ER8 (655269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATH-ER8 (655269) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_216 | 3 Phase fault on BATH-ER8 (655269) 69 kV Bus a. Apply fault at the BATH-ER8 (655269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATH-ER8 (655269) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_217 | 3 Phase fault on PLSNTV_T-MW7 (655902) 115 kV Bus a. Apply fault at the PLSNTV_T-MW7 (655902) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to PLSNTVAL-MW7 (655913) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_217 | 3 Phase fault on PLSNTV_T-MW7 (655902) 115 kV Bus a. Apply fault at the PLSNTV_T-MW7 (655902) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to PLSNTVAL-MW7 (655913) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_218 | 3 Phase fault on HESS GAS-MW7 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_218 | 3 Phase fault on HESS GAS-MW7 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_219 | 3 Phase fault on W.BANK__-MW7 (655922) 115 kV Bus a. Apply fault at the W.BANK__-MW7 (655922) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_219 | 3 Phase fault on W.BANK__-MW7 (655922) 115 kV Bus a. Apply fault at the W.BANK__-MW7 (655922) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_22 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_22 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_220 | 3 Phase fault on TWELVE_M-MW7 (655939) 115 kV Bus a. Apply fault at the TWELVE_M-MW7 (655939) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_220 | 3 Phase fault on TWELVE_M-MW7 (655939) 115 kV Bus a. Apply fault at the TWELVE_M-MW7 (655939) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_221 | 3 Phase fault on PLAZA -MW7 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV to BLAISDEL-MW7 (655949) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_221 | 3 Phase fault on PLAZA -MW7 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV to BLAISDEL-MW7 (655949) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_222 | 3 Phase fault on BLAISDEL-MW7 (655949) 115 kV Bus a. Apply fault at the BLAISDEL-MW7 (655949) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_222 | 3 Phase fault on BLAISDEL-MW7 (655949) 115 kV Bus a. Apply fault at the BLAISDEL-MW7 (655949) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_223 | 3 Phase fault on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_223 | 3 Phase fault on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_224 | 3 Phase fault on W.BANK_T-MW7 (655953) 115 kV Bus a. Apply fault at the W.BANK_T-MW7 (655953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK_T-MW7 (655953) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_224 | 3 Phase fault on W.BANK_T-MW7 (655953) 115 kV Bus a. Apply fault at the W.BANK_T-MW7 (655953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK_T-MW7 (655953) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_225 | 3 Phase fault on HESSRAIL-MW7 (655961) 115 kV Bus a. Apply fault at the HESSRAIL-MW7 (655961) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESSRAIL-MW7 (655961) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_225 | 3 Phase fault on HESSRAIL-MW7 (655961) 115 kV Bus a. Apply fault at the HESSRAIL-MW7 (655961) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESSRAIL-MW7 (655961) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_226 | 3 Phase fault on WTREAST7 (658088) 115 kV Bus a. Apply fault at the WTREAST7 (658088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTREAST7 (658088) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_226 | 3 Phase fault on WTREAST7 (658088) 115 kV Bus a. Apply fault at the WTREAST7 (658088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTREAST7 (658088) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_227 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_227 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_228 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_228 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_229 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_229 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_23 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_23 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_230 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_230 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_231 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_231 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_232 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_232 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_233 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_233 | 3 Phase fault on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_234 | 3 Phase fault on LELAND_O-BE4 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_234 | 3 Phase fault on LELAND_O-BE4 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_235 | 3 Phase fault on LOGAN___-BE4 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_235 | 3 Phase fault on LOGAN___-BE4 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_236 | 3 Phase fault on CHAPELLE-BE3 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_236 | 3 Phase fault on CHAPELLE-BE3 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_237 | 3 Phase fault on NESET___-BE4 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_237 | 3 Phase fault on NESET___-BE4 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_238 | 3 Phase fault on NESET___-BE4 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_238 | 3 Phase fault on NESET___-BE4 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_239 | 3 Phase fault on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_239 | 3 Phase fault on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_24 | 3 Phase fault on SHEYNNE4 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_24 | 3 Phase fault on SHEYNNE4 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_240 | 3 Phase fault on GROTON__-BE3 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_240 | 3 Phase fault on GROTON__-BE3 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_241 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_241 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_242 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_242 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_243 | 3 Phase fault on COTEAU_1-RR8 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR8 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_243 | 3 Phase fault on COTEAU_1-RR8 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR8 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_244 | 3 Phase fault on JUDSON__-BE3 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_244 | 3 Phase fault on JUDSON__-BE3 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_245 | 3 Phase fault on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_245 | 3 Phase fault on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_246 | 3 Phase fault on PATENTGT-MK7 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_246 | 3 Phase fault on PATENTGT-MK7 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_247 | 3 Phase fault on PATENTGT-MK7 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_247 | 3 Phase fault on PATENTGT-MK7 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_248 | 3 Phase fault on CC.LS-LO-BE3 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_248 | 3 Phase fault on CC.LS-LO-BE3 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_249 | 3 Phase fault on ABERDN SIEB7 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_249 | 3 Phase fault on ABERDN SIEB7 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_25 | 3 Phase fault on MALLARD7 (603023) 115 kV Bus a. Apply fault at the MALLARD7 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_25 | 3 Phase fault on MALLARD7 (603023) 115 kV Bus a. Apply fault at the MALLARD7 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_250 | 3 Phase fault on TIOGA4 4 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_250 | 3 Phase fault on TIOGA4 4 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_251 | 3 Phase fault on BD 4 (672601) 230 kV Bus a. Apply fault at the BD 4 (672601) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BD 4 (672601) 230.0 kV to SHAND 4 (672621) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Odd behavior at generator SHAND1 (672321), angle drift | Remove reclose event.
01 - North | 25W | Transfer | GROUP1_P1_FAULT_251 | 3 Phase fault on BD 4 (672601) 230 kV Bus a. Apply fault at the BD 4 (672601) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BD 4 (672601) 230.0 kV to SHAND 4 (672621) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_252 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_252 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_253 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_253 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_254 | 3 Phase fault on VALLEYC7 (652454) 115 kV Bus a. Apply fault at the VALLEYC7 (652454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC8 (652204) 69.0 kV to VALLEYC7 (652454) 115.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_254 | 3 Phase fault on VALLEYC7 (652454) 115 kV Bus a. Apply fault at the VALLEYC7 (652454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC8 (652204) 69.0 kV to VALLEYC7 (652454) 115.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_255 | 3 Phase fault on SUMMIT-7 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-8 (652209) 69.0 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_255 | 3 Phase fault on SUMMIT-7 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-8 (652209) 69.0 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_256 | 3 Phase fault on WATERTN7 (652531) 115 kV Bus a. Apply fault at the WATERTN7 (652531) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERT18 (652242) 69.0 kV to WATERTN7 (652531) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_256 | 3 Phase fault on WATERTN7 (652531) 115 kV Bus a. Apply fault at the WATERTN7 (652531) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERT18 (652242) 69.0 kV to WATERTN7 (652531) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_257 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_257 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_258 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_258 | 3 Phase fault on GROTON 7 (652512) 115 kV Bus a. Apply fault at the GROTON 7 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_259 | 3 Phase fault on WILISTN4 (652400) 230 kV Bus a. Apply fault at the WILISTN4 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_259 | 3 Phase fault on WILISTN4 (652400) 230 kV Bus a. Apply fault at the WILISTN4 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_26 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_26 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_260 | 3 Phase fault on WILISTN4 (652400) 230 kV Bus a. Apply fault at the WILISTN4 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_260 | 3 Phase fault on WILISTN4 (652400) 230 kV Bus a. Apply fault at the WILISTN4 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_261 | 3 Phase fault on BISMARK4 (652426) 230 kV Bus a. Apply fault at the BISMARK4 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_261 | 3 Phase fault on BISMARK4 (652426) 230 kV Bus a. Apply fault at the BISMARK4 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_262 | 3 Phase fault on BISMARK4 (652426) 230 kV Bus a. Apply fault at the BISMARK4 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_262 | 3 Phase fault on BISMARK4 (652426) 230 kV Bus a. Apply fault at the BISMARK4 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_263 | 3 Phase fault on EDGELEY7 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_263 | 3 Phase fault on EDGELEY7 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_264 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_264 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_265 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_265 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_266 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV to FORMAN 8 (652439) 69.0 kV to FORMAN9 (652393) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_266 | 3 Phase fault on FORMAN 7 (652438) 115 kV Bus a. Apply fault at the FORMAN 7 (652438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 7 (652438) 115.0 kV to FORMAN 8 (652439) 69.0 kV to FORMAN9 (652393) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_267 | 3 Phase fault on JAMESTN4 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_267 | 3 Phase fault on JAMESTN4 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_268 | 3 Phase fault on JAMESTN4 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_268 | 3 Phase fault on JAMESTN4 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_269 | 3 Phase fault on ROBERTSCTY7 (652455) 115 kV Bus a. Apply fault at the ROBERTSCTY7 (652455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to ROBERTSCTY8 (652361) 69.0 kV to ROBERTSCTY9 (652362) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_269 | 3 Phase fault on ROBERTSCTY7 (652455) 115 kV Bus a. Apply fault at the ROBERTSCTY7 (652455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to ROBERTSCTY8 (652361) 69.0 kV to ROBERTSCTY9 (652362) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_27 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_27 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_270 | 3 Phase fault on HURON 4 (652514) 230 kV Bus a. Apply fault at the HURON 4 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_270 | 3 Phase fault on HURON 4 (652514) 230 kV Bus a. Apply fault at the HURON 4 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_271 | 3 Phase fault on HURON 4 (652514) 230 kV Bus a. Apply fault at the HURON 4 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_271 | 3 Phase fault on HURON 4 (652514) 230 kV Bus a. Apply fault at the HURON 4 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_272 | 3 Phase fault on WATERTN3 (652529) 345 kV Bus a. Apply fault at the WATERTN3 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_272 | 3 Phase fault on WATERTN3 (652529) 345 kV Bus a. Apply fault at the WATERTN3 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_273 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_273 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_274 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_274 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_275 | 3 Phase fault on WHITE 3 (652537) 345 kV Bus a. Apply fault at the WHITE 3 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_275 | 3 Phase fault on WHITE 3 (652537) 345 kV Bus a. Apply fault at the WHITE 3 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_276 | 3 Phase fault on APPLEDORN 4 (652582) 230 kV Bus a. Apply fault at the APPLEDORN 4 (652582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_276 | 3 Phase fault on APPLEDORN 4 (652582) 230 kV Bus a. Apply fault at the APPLEDORN 4 (652582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_277 | 3 Phase fault on BRISTOL-ER7 (655457) 115 kV Bus a. Apply fault at the BRISTOL-ER7 (655457) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_277 | 3 Phase fault on BRISTOL-ER7 (655457) 115 kV Bus a. Apply fault at the BRISTOL-ER7 (655457) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_278 | 3 Phase fault on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_278 | 3 Phase fault on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_279 | 3 Phase fault on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_279 | 3 Phase fault on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_28 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_28 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_280 | 3 Phase fault on LELAND_O-BE3 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_280 | 3 Phase fault on LELAND_O-BE3 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_281 | 3 Phase fault on LELAND_O-BE3 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_281 | 3 Phase fault on LELAND_O-BE3 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_282 | 3 Phase fault on LOGAN___-BE4 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_282 | 3 Phase fault on LOGAN___-BE4 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_283 | 3 Phase fault on NESET___-BE4 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_283 | 3 Phase fault on NESET___-BE4 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_284 | 3 Phase fault on NRTSHORE-BE4 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_284 | 3 Phase fault on NRTSHORE-BE4 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_285 | 3 Phase fault on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_285 | 3 Phase fault on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_286 | 3 Phase fault on GROTON__-BE3 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_286 | 3 Phase fault on GROTON__-BE3 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_287 | 3 Phase fault on GROTON__-BE3 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_287 | 3 Phase fault on GROTON__-BE3 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_288 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_288 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_289 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_289 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_29 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_29 | 3 Phase fault on GRE-COAL CR4 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_290 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_290 | 3 Phase fault on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_291 | 3 Phase fault on BASIN___-BE4 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_291 | 3 Phase fault on BASIN___-BE4 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_292 | 3 Phase fault on DGC_____-BE3 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_292 | 3 Phase fault on DGC_____-BE3 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_293 | 3 Phase fault on COTEAU__-RR3 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_293 | 3 Phase fault on COTEAU__-RR3 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_294 | 3 Phase fault on COTEAU__-RR3 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_294 | 3 Phase fault on COTEAU__-RR3 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_295 | 3 Phase fault on JUDSON__-BE3 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_295 | 3 Phase fault on JUDSON__-BE3 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_296 | 3 Phase fault on TANDE___-BE3 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_296 | 3 Phase fault on TANDE___-BE3 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_297 | 3 Phase fault on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_297 | 3 Phase fault on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_298 | 3 Phase fault on ROUNDUP_-BE3 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_298 | 3 Phase fault on ROUNDUP_-BE3 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_299 | 3 Phase fault on KUMMERDG-BE3 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_299 | 3 Phase fault on KUMMERDG-BE3 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_3 | 3 Phase fault on BROOKNG7 (652504) 115 kV Bus a. Apply fault at the BROOKNG7 (652504) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKNG7 (652504) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_3 | 3 Phase fault on BROOKNG7 (652504) 115 kV Bus a. Apply fault at the BROOKNG7 (652504) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKNG7 (652504) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_30 | 3 Phase fault on GRE-STANTON4 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_30 | 3 Phase fault on GRE-STANTON4 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_300 | 3 Phase fault on KUMMERDG-BE3 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_300 | 3 Phase fault on KUMMERDG-BE3 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_301 | 3 Phase fault on PATENTGT-BE3 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_301 | 3 Phase fault on PATENTGT-BE3 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_302 | 3 Phase fault on PATENTGT-BE3 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_302 | 3 Phase fault on PATENTGT-BE3 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_303 | 3 Phase fault on TIOGA4 4 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_303 | 3 Phase fault on TIOGA4 4 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_304 | 3 Phase fault on ELLENDL345 3 (661097) 345 kV Bus a. Apply fault at the ELLENDL345 3 (661097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELLENDL345 3 (661097) 345.0 kV to ELLENDL345 4 (661098) 230.0 kV to ELLENDL345 9 (661907) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_304 | 3 Phase fault on ELLENDL345 3 (661097) 345 kV Bus a. Apply fault at the ELLENDL345 3 (661097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELLENDL345 3 (661097) 345.0 kV to ELLENDL345 4 (661098) 230.0 kV to ELLENDL345 9 (661907) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_305 | 3 Phase fault on BDX 4 (672602) 230 kV Bus a. Apply fault at the BDX 4 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_305 | 3 Phase fault on BDX 4 (672602) 230 kV Bus a. Apply fault at the BDX 4 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_306 | 3 Phase fault on BDV 4 (672603) 230 kV Bus a. Apply fault at the BDV 4 (672603) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_306 | 3 Phase fault on BDV 4 (672603) 230 kV Bus a. Apply fault at the BDV 4 (672603) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_307 | 3 Phase fault on SQBEAST4 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 67030 [MPC04000MPT 230.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P1_FAULT_307 | 3 Phase fault on SQBEAST4 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_308 | 3 Phase fault on CROWN CAP (620317) 230 kV Bus a. Apply fault at the CROWN CAP (620317) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROWN CAP (620317) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_308 | 3 Phase fault on CROWN CAP (620317) 230 kV Bus a. Apply fault at the CROWN CAP (620317) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROWN CAP (620317) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_309 | 3 Phase fault on BROOKNG7 (652504) 115 kV Bus a. Apply fault at the BROOKNG7 (652504) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKNG7 (652504) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_309 | 3 Phase fault on BROOKNG7 (652504) 115 kV Bus a. Apply fault at the BROOKNG7 (652504) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKNG7 (652504) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_31 | 3 Phase fault on GRE-STANTON4 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_31 | 3 Phase fault on GRE-STANTON4 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_310 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_310 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_311 | 3 Phase fault on PLAZA -MW7 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_311 | 3 Phase fault on PLAZA -MW7 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_312 | 3 Phase fault on CC.LS-LO-BE3 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_312 | 3 Phase fault on CC.LS-LO-BE3 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_313 | 3 Phase fault on TRIPLEH__UA3 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_313 | 3 Phase fault on TRIPLEH__UA3 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_314 | 3 Phase fault on ELLENDL345 4 (661098) 230 kV Bus a. Apply fault at the ELLENDL345 4 (661098) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLENDL345 4 (661098) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_314 | 3 Phase fault on ELLENDL345 4 (661098) 230 kV Bus a. Apply fault at the ELLENDL345 4 (661098) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLENDL345 4 (661098) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_315 | 3 Phase fault on G18-008-TAP (659423) 345 kV Bus a. Apply fault at the G18-008-TAP (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) to GROTON -BE3 (659160) 345.0 kV Transmission Circuit #Z b.2. G18-008-TAP (762544) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_315 | 3 Phase fault on G18-008-TAP (659423) 345 kV Bus a. Apply fault at the G18-008-TAP (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) to GROTON -BE3 (659160) 345.0 kV Transmission Circuit #Z b.2. G18-008-TAP (762544) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_316 | 3 Phase fault on LO.LS-GR-BE3 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-008-TAP (762544) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_316 | 3 Phase fault on LO.LS-GR-BE3 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-008-TAP (762544) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_317 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_317 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_318 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_318 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_319 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_319 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_32 | 3 Phase fault on GWINNER7 (620262) 115 kV Bus a. Apply fault at the GWINNER7 (620262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GWINNER7 (620262) 115.0 kV to FORMN 7 (620263) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_32 | 3 Phase fault on GWINNER7 (620262) 115 kV Bus a. Apply fault at the GWINNER7 (620262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GWINNER7 (620262) 115.0 kV to FORMN 7 (620263) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_320 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_320 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_321 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_321 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_322 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_322 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_323 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_323 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_324 | 3 Phase fault on SHEYNNE4 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_324 | 3 Phase fault on SHEYNNE4 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_325 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_325 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_326 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_326 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_327 | 3 Phase fault on BSSOUTH3 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_327 | 3 Phase fault on BSSOUTH3 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_328 | 3 Phase fault on BSSOUTH3 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_328 | 3 Phase fault on BSSOUTH3 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_329 | 3 Phase fault on PRAIRIE3 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_329 | 3 Phase fault on PRAIRIE3 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_33 | 3 Phase fault on FORMN 7 (620263) 115 kV Bus a. Apply fault at the FORMN 7 (620263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMN 7 (620263) 115.0 kV to FORMAN 7 (652438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_33 | 3 Phase fault on FORMN 7 (620263) 115 kV Bus a. Apply fault at the FORMN 7 (620263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMN 7 (620263) 115.0 kV to FORMAN 7 (652438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_330 | 3 Phase fault on PRAIRIE3 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_330 | 3 Phase fault on PRAIRIE3 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_331 | 3 Phase fault on CNTSHNT3 (657951) 345 kV Bus a. Apply fault at the CNTSHNT3 (657951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_331 | 3 Phase fault on CNTSHNT3 (657951) 345 kV Bus a. Apply fault at the CNTSHNT3 (657951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_332 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_332 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_333 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_333 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_334 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_334 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_335 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_335 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_336 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_336 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_337 | 3 Phase fault on BUFFALO3 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.3. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_337 | 3 Phase fault on BUFFALO3 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.3. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 67022 [MPC03839TL 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P1_FAULT_338 | 3 Phase fault on GRANITF4 (652550) 230 kV Bus a. Apply fault at the GRANITF4 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_338 | 3 Phase fault on GRANITF4 (652550) 230 kV Bus a. Apply fault at the GRANITF4 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_339 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_339 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_34 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BSSOUTH4 (620322) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_34 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BSSOUTH4 (620322) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_340 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_340 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_341 | 3 Phase fault on NUNDRWD-LNX3 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_341 | 3 Phase fault on NUNDRWD-LNX3 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_342 | 3 Phase fault on SIOUXCY-LNX3 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_342 | 3 Phase fault on SIOUXCY-LNX3 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_343 | 3 Phase fault on WATERTN-LNX3 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_343 | 3 Phase fault on WATERTN-LNX3 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_344 | 3 Phase fault on DRYCREEK-BE4 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_344 | 3 Phase fault on DRYCREEK-BE4 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_345 | 3 Phase fault on MI CTYE4 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_345 | 3 Phase fault on MI CTYE4 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_346 | 3 Phase fault on MEADOWGROVE4 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_346 | 3 Phase fault on MEADOWGROVE4 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_347 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_347 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_348 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_348 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_349 | 3 Phase fault on BUFFALO3 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_349 | 3 Phase fault on BUFFALO3 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_35 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BSSOUTH4 (620322) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_35 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BSSOUTH4 (620322) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_350 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_350 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_351 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_351 | 3 Phase fault on FARGO 4 (652435) 230 kV Bus a. Apply fault at the FARGO 4 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_352 | 3 Phase fault on NUNDRWD4 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_352 | 3 Phase fault on NUNDRWD4 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_353 | 3 Phase fault on NUNDRWD4 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_353 | 3 Phase fault on NUNDRWD4 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_354 | 3 Phase fault on WHITE 3 (652537) 345 kV Bus a. Apply fault at the WHITE 3 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_354 | 3 Phase fault on WHITE 3 (652537) 345 kV Bus a. Apply fault at the WHITE 3 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_355 | 3 Phase fault on TIOGA4 4 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_355 | 3 Phase fault on TIOGA4 4 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_356 | 3 Phase fault on MI CTYE4 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_356 | 3 Phase fault on MI CTYE4 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_357 | 3 Phase fault on NUNDRWD4 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_357 | 3 Phase fault on NUNDRWD4 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_36 | 3 Phase fault on JAMESTN3 (620369) 345 kV Bus a. Apply fault at the JAMESTN3 (620369) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_36 | 3 Phase fault on JAMESTN3 (620369) 345 kV Bus a. Apply fault at the JAMESTN3 (620369) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_37 | 3 Phase fault on CENTER 4 (657751) 230 kV Bus a. Apply fault at the CENTER 4 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_37 | 3 Phase fault on CENTER 4 (657751) 230 kV Bus a. Apply fault at the CENTER 4 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_38 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_38 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_39 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_39 | 3 Phase fault on BRKNGCO3 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_4 | 3 Phase fault on GRANITF4 (652550) 230 kV Bus a. Apply fault at the GRANITF4 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_4 | 3 Phase fault on GRANITF4 (652550) 230 kV Bus a. Apply fault at the GRANITF4 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_40 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_40 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_41 | 3 Phase fault on BSSOUTH3 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_41 | 3 Phase fault on BSSOUTH3 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_42 | 3 Phase fault on BSSOUTH3 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_42 | 3 Phase fault on BSSOUTH3 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_43 | 3 Phase fault on CENTER 3 (657791) 345 kV Bus a. Apply fault at the CENTER 3 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_43 | 3 Phase fault on CENTER 3 (657791) 345 kV Bus a. Apply fault at the CENTER 3 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_44 | 3 Phase fault on CENTER 3 (657791) 345 kV Bus a. Apply fault at the CENTER 3 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_44 | 3 Phase fault on CENTER 3 (657791) 345 kV Bus a. Apply fault at the CENTER 3 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_45 | 3 Phase fault on GRE-COALFB14 (615604) 230 kV Bus a. Apply fault at the GRE-COALFB14 (615604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB14 (615604) 230.0 kV Fixed Shunt Device #//bp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_45 | 3 Phase fault on GRE-COALFB14 (615604) 230 kV Bus a. Apply fault at the GRE-COALFB14 (615604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB14 (615604) 230.0 kV Fixed Shunt Device #//bp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_46 | 3 Phase fault on GRE-COALFB14 (615604) 230 kV Bus a. Apply fault at the GRE-COALFB14 (615604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB14 (615604) 230.0 kV Fixed Shunt Device #//hp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_46 | 3 Phase fault on GRE-COALFB14 (615604) 230 kV Bus a. Apply fault at the GRE-COALFB14 (615604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB14 (615604) 230.0 kV Fixed Shunt Device #//hp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_47 | 3 Phase fault on GRE-COALFB24 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Fixed Shunt Device #//bp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_47 | 3 Phase fault on GRE-COALFB24 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Fixed Shunt Device #//bp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_48 | 3 Phase fault on GRE-COALFB24 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Fixed Shunt Device #//hp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_48 | 3 Phase fault on GRE-COALFB24 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Fixed Shunt Device #//hp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_49 | 3 Phase fault on GRE-COALFB24 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_49 | 3 Phase fault on GRE-COALFB24 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_5 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_5 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_50 | 3 Phase fault on GRE-COALFB34 (615606) 230 kV Bus a. Apply fault at the GRE-COALFB34 (615606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB34 (615606) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_50 | 3 Phase fault on GRE-COALFB34 (615606) 230 kV Bus a. Apply fault at the GRE-COALFB34 (615606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB34 (615606) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_51 | 3 Phase fault on GWINNER7 (620262) 115 kV Bus a. Apply fault at the GWINNER7 (620262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GWINNER7 (620262) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_51 | 3 Phase fault on GWINNER7 (620262) 115 kV Bus a. Apply fault at the GWINNER7 (620262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GWINNER7 (620262) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_52 | 3 Phase fault on GRE-COAL TP4 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_52 | 3 Phase fault on GRE-COAL TP4 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_53 | 3 Phase fault on GRE-MCHENRY4 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_53 | 3 Phase fault on GRE-MCHENRY4 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_54 | 3 Phase fault on CNTSHNT3 (657951) 345 kV Bus a. Apply fault at the CNTSHNT3 (657951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_54 | 3 Phase fault on CNTSHNT3 (657951) 345 kV Bus a. Apply fault at the CNTSHNT3 (657951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_55 | 3 Phase fault on BROWNSV4 (620325) 230 kV Bus a. Apply fault at the BROWNSV4 (620325) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_55 | 3 Phase fault on BROWNSV4 (620325) 230 kV Bus a. Apply fault at the BROWNSV4 (620325) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_56 | 3 Phase fault on UNDERWD4 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1456 POI (44568) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_56 | 3 Phase fault on UNDERWD4 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1456 POI (44568) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_57 | 3 Phase fault on JAMETAP7 (620273) 115 kV Bus a. Apply fault at the JAMETAP7 (620273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.2. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.3. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.4. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_57 | 3 Phase fault on JAMETAP7 (620273) 115 kV Bus a. Apply fault at the JAMETAP7 (620273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.2. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.3. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.4. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_58 | 3 Phase fault on AVIKO 7 (620271) 115 kV Bus a. Apply fault at the AVIKO 7 (620271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.2. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_58 | 3 Phase fault on AVIKO 7 (620271) 115 kV Bus a. Apply fault at the AVIKO 7 (620271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.2. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_59 | 3 Phase fault on STANTN.T-BE7 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_59 | 3 Phase fault on STANTN.T-BE7 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_6 | 3 Phase fault on HURON 4 (652514) 230 kV Bus a. Apply fault at the HURON 4 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_6 | 3 Phase fault on HURON 4 (652514) 230 kV Bus a. Apply fault at the HURON 4 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_60 | 3 Phase fault on FORMAN 4 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_60 | 3 Phase fault on FORMAN 4 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_61 | 3 Phase fault on NESET___-BE7 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_61 | 3 Phase fault on NESET___-BE7 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_62 | 3 Phase fault on GRANITF4 (652550) 230 kV Bus a. Apply fault at the GRANITF4 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_62 | 3 Phase fault on GRANITF4 (652550) 230 kV Bus a. Apply fault at the GRANITF4 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_63 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_63 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_64 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_64 | 3 Phase fault on BIGSTON4 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_65 | 3 Phase fault on WATERTN7 (652531) 115 kV Bus a. Apply fault at the WATERTN7 (652531) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN7 (652531) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_65 | 3 Phase fault on WATERTN7 (652531) 115 kV Bus a. Apply fault at the WATERTN7 (652531) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN7 (652531) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_66 | 3 Phase fault on WTREAST7 (658088) 115 kV Bus a. Apply fault at the WTREAST7 (658088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTREAST7 (658088) 115.0 kV to WTRTNPP (658090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_66 | 3 Phase fault on WTREAST7 (658088) 115 kV Bus a. Apply fault at the WTREAST7 (658088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTREAST7 (658088) 115.0 kV to WTRTNPP (658090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_67 | 3 Phase fault on WTRTNPP (658090) 115 kV Bus a. Apply fault at the WTRTNPP (658090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTRTNPP (658090) 115.0 kV to WTRWEST7 (658092) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_67 | 3 Phase fault on WTRTNPP (658090) 115 kV Bus a. Apply fault at the WTRTNPP (658090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTRTNPP (658090) 115.0 kV to WTRWEST7 (658092) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_68 | 3 Phase fault on WTRWEST7 (658092) 115 kV Bus a. Apply fault at the WTRWEST7 (658092) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTRWEST7 (658092) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_68 | 3 Phase fault on WTRWEST7 (658092) 115 kV Bus a. Apply fault at the WTRWEST7 (658092) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WTRWEST7 (658092) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_69 | 3 Phase fault on WASHBRN4 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_69 | 3 Phase fault on WASHBRN4 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_7 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_7 | 3 Phase fault on WATERTN4 (652530) 230 kV Bus a. Apply fault at the WATERTN4 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_70 | 3 Phase fault on HERBERTW-KM4 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_70 | 3 Phase fault on HERBERTW-KM4 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_71 | 3 Phase fault on BARLOW -CP7 (655610) 115 kV Bus a. Apply fault at the BARLOW -CP7 (655610) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_71 | 3 Phase fault on BARLOW -CP7 (655610) 115 kV Bus a. Apply fault at the BARLOW -CP7 (655610) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_72 | 3 Phase fault on PICKERT4 (657759) 230 kV Bus a. Apply fault at the PICKERT4 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT9 (620167) 41.6 kV to PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV Three Winding #1 b.5. PICKERT8 (657923) 69.0 kV to PICKERT4 (657759) 230.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_72 | 3 Phase fault on PICKERT4 (657759) 230 kV Bus a. Apply fault at the PICKERT4 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT9 (620167) 41.6 kV to PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV Three Winding #1 b.5. PICKERT8 (657923) 69.0 kV to PICKERT4 (657759) 230.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_73 | 3 Phase fault on ENDERLIN 7 (652638) 115 kV Bus a. Apply fault at the ENDERLIN 7 (652638) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_73 | 3 Phase fault on ENDERLIN 7 (652638) 115 kV Bus a. Apply fault at the ENDERLIN 7 (652638) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_74 | 3 Phase fault on ARLNGTN-ER7 (655462) 115 kV Bus a. Apply fault at the ARLNGTN-ER7 (655462) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKNG7 (652504) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.2. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.3. ARLNGTN-ER7 (655462) 115.0 kV to ARLNGTN-ER8 (655463) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_74 | 3 Phase fault on ARLNGTN-ER7 (655462) 115 kV Bus a. Apply fault at the ARLNGTN-ER7 (655462) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKNG7 (652504) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.2. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.3. ARLNGTN-ER7 (655462) 115.0 kV to ARLNGTN-ER8 (655463) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_75 | 3 Phase fault on HURON BTAP 7 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_75 | 3 Phase fault on HURON BTAP 7 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_76 | 3 Phase fault on DICKEYTP-CP8 (655625) 69 kV Bus a. Apply fault at the DICKEYTP-CP8 (655625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.3. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_76 | 3 Phase fault on DICKEYTP-CP8 (655625) 69 kV Bus a. Apply fault at the DICKEYTP-CP8 (655625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.3. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_77 | 3 Phase fault on OMEGATAP-CP8 (655626) 69 kV Bus a. Apply fault at the OMEGATAP-CP8 (655626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.2. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 b.3. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_77 | 3 Phase fault on OMEGATAP-CP8 (655626) 69 kV Bus a. Apply fault at the OMEGATAP-CP8 (655626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.2. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 b.3. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_78 | 3 Phase fault on LAMOURTP-CP8 (655627) 69 kV Bus a. Apply fault at the LAMOURTP-CP8 (655627) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 b.2. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 b.3. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_78 | 3 Phase fault on LAMOURTP-CP8 (655627) 69 kV Bus a. Apply fault at the LAMOURTP-CP8 (655627) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 b.2. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 b.3. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_79 | 3 Phase fault on WESTOAKS-CP8 (655628) 69 kV Bus a. Apply fault at the WESTOAKS-CP8 (655628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 b.2. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 b.3. NRTHOAKS-CP8 (655629) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_79 | 3 Phase fault on WESTOAKS-CP8 (655628) 69 kV Bus a. Apply fault at the WESTOAKS-CP8 (655628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 b.2. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 b.3. NRTHOAKS-CP8 (655629) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_8 | 3 Phase fault on SUMMIT-7 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_8 | 3 Phase fault on SUMMIT-7 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_80 | 3 Phase fault on COGSWELL-CP8 (655630) 69 kV Bus a. Apply fault at the COGSWELL-CP8 (655630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 8 (652439) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 b.2. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 b.3. NRTHOAKS-CP8 (655629) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_80 | 3 Phase fault on COGSWELL-CP8 (655630) 69 kV Bus a. Apply fault at the COGSWELL-CP8 (655630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 8 (652439) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 b.2. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 b.3. NRTHOAKS-CP8 (655629) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_81 | 3 Phase fault on KENASTON-BE7 (659308) 115 kV Bus a. Apply fault at the KENASTON-BE7 (659308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENASTON-BE7 (659308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_81 | 3 Phase fault on KENASTON-BE7 (659308) 115 kV Bus a. Apply fault at the KENASTON-BE7 (659308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENASTON-BE7 (659308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_82 | 3 Phase fault on WHTEARTH-MW7 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_82 | 3 Phase fault on WHTEARTH-MW7 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_83 | 3 Phase fault on FARMVL_T-MW7 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.3. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_83 | 3 Phase fault on FARMVL_T-MW7 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.3. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_84 | 3 Phase fault on N.WLST_T-MW7 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_84 | 3 Phase fault on N.WLST_T-MW7 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_85 | 3 Phase fault on GR.LS-LO-BE3 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. G18-008-TAP (762544) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_85 | 3 Phase fault on GR.LS-LO-BE3 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. G18-008-TAP (762544) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_86 | 3 Phase fault on TN.LS-JD-BE3 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_86 | 3 Phase fault on TN.LS-JD-BE3 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_87 | 3 Phase fault on WATERTN-LNX3 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_87 | 3 Phase fault on WATERTN-LNX3 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_88 | 3 Phase fault on BROADLND-BE3 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_88 | 3 Phase fault on BROADLND-BE3 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_89 | 3 Phase fault on FTTHOM1-LNX3 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_89 | 3 Phase fault on FTTHOM1-LNX3 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_9 | 3 Phase fault on WILLISTON27 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_9 | 3 Phase fault on WILLISTON27 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_90 | 3 Phase fault on LO.LS-GR-BE3 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_90 | 3 Phase fault on LO.LS-GR-BE3 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_91 | 3 Phase fault on EDGELEY8 (652433) 69 kV Bus a. Apply fault at the EDGELEY8 (652433) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. FORMAN 8 (652439) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_91 | 3 Phase fault on EDGELEY8 (652433) 69 kV Bus a. Apply fault at the EDGELEY8 (652433) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. FORMAN 8 (652439) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_92 | 3 Phase fault on WOONSKT7 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.3. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_92 | 3 Phase fault on WOONSKT7 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.3. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_93 | 3 Phase fault on ABERDN JCT 7 (660000) 115 kV Bus a. Apply fault at the ABERDN JCT 7 (660000) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_93 | 3 Phase fault on ABERDN JCT 7 (660000) 115 kV Bus a. Apply fault at the ABERDN JCT 7 (660000) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_94 | 3 Phase fault on ABERDN SIEB7 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_94 | 3 Phase fault on ABERDN SIEB7 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_95 | 3 Phase fault on HURON WPARK7 (660003) 115 kV Bus a. Apply fault at the HURON WPARK7 (660003) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON WPARK7 (660003) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_95 | 3 Phase fault on HURON WPARK7 (660003) 115 kV Bus a. Apply fault at the HURON WPARK7 (660003) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON WPARK7 (660003) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_96 | 3 Phase fault on BROADLND-BE3 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_96 | 3 Phase fault on BROADLND-BE3 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_97 | 3 Phase fault on AV.LS-BD-BE3 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_97 | 3 Phase fault on AV.LS-BD-BE3 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_98 | 3 Phase fault on BD.LS-AV-BE3 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_98 | 3 Phase fault on BD.LS-AV-BE3 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P1_FAULT_99 | 3 Phase fault on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P1_FAULT_99 | 3 Phase fault on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on JAMESTN3 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on JAMESTN3 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on BISMARK4 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.5. BISMARK9 (652392) 12.5 kV to BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on BISMARK4 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.5. BISMARK9 (652392) 12.5 kV to BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT18 (652242) 69.0 kV to WATERTN7 (652531) 115.0 kV Two Winding #1 b.2. WATERT18 (652242) 69.0 kV to MOS-RVLE-ER8 (655108) 69.0 kV Transmission Circuit #1 b.3. WATERT18 (652242) 69.0 kV to SW-SHERI-ER8 (655111) 69.0 kV Transmission Circuit #1 b.4. BROOKNG7 (652504) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.5. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.6. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.7. WATERTN7 (652531) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 b.8. ARLNGTN-ER7 (655462) 115.0 kV to ARLNGTN-ER8 (655463) 69.0 kV Two Winding #1 b.9. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT18 (652242) 69.0 kV to WATERTN7 (652531) 115.0 kV Two Winding #1 b.2. WATERT18 (652242) 69.0 kV to MOS-RVLE-ER8 (655108) 69.0 kV Transmission Circuit #1 b.3. WATERT18 (652242) 69.0 kV to SW-SHERI-ER8 (655111) 69.0 kV Transmission Circuit #1 b.4. BROOKNG7 (652504) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.5. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.6. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.7. WATERTN7 (652531) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 b.8. ARLNGTN-ER7 (655462) 115.0 kV to ARLNGTN-ER8 (655463) 69.0 kV Two Winding #1 b.9. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on WHEELS_T-MW7 (655945) 115 kV Bus a. Apply Fault at the WHEELS_T-MW7 (655945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.6. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.7. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on WHEELS_T-MW7 (655945) 115 kV Bus a. Apply Fault at the WHEELS_T-MW7 (655945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.6. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.7. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on SW561-ER7 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on SW561-ER7 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on G09_001IST (659165) 345 kV Bus a. Apply Fault at the G09_001IST (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on G09_001IST (659165) 345 kV Bus a. Apply Fault at the G09_001IST (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on TIOGA7 7 (661086) 115 kV Bus a. Apply Fault at the TIOGA7 7 (661086) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 b.2. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on TIOGA7 7 (661086) 115 kV Bus a. Apply Fault at the TIOGA7 7 (661086) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 b.2. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on OLIVER -MW7 (655966) 115 kV Bus a. Apply Fault at the OLIVER -MW7 (655966) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 b.2. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on OLIVER -MW7 (655966) 115 kV Bus a. Apply Fault at the OLIVER -MW7 (655966) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 b.2. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.3. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.3. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.3. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on SATTER -MW7 (655967) 115 kV Bus a. Apply Fault at the SATTER -MW7 (655967) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SATTER -MW7 (655967) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on SATTER -MW7 (655967) 115 kV Bus a. Apply Fault at the SATTER -MW7 (655967) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SATTER -MW7 (655967) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.9. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 b.10. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.9. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 b.10. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on FORMAN 4 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 661000 [LEOLA 7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on FORMAN 4 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 661000 [LEOLA 7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] - VOLT 652454 [VALLEYC7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.2. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.3. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.5. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.6. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.7. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.8. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.9. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.2. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.3. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.5. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.6. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.7. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.8. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.9. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on BROADLND-BE3 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on BROADLND-BE3 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on KENMARE7 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.2. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.3. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 b.4. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on KENMARE7 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.2. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.3. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 b.4. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on DEVILSL7 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 b.3. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.5. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.6. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on DEVILSL7 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 b.3. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.5. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.6. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on BISMARK4 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on BISMARK4 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 652436 [FARGO 7 115.00] - VOLT 658160 [MPSBROOK 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 652436 [FARGO 7 115.00] - VOLT 658160 [MPSBROOK 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on KENMARE7 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.4. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on KENMARE7 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.4. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to SHEYNNE4 (602006) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to SHEYNNE4 (602006) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 67022 [MPC03839TL 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to WAYSIDE4 (640404) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to WAYSIDE4 (640404) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 652395 [SHIRLEY TAP 115.00] - VOLT 652411 [MI CTYE4 230.00] - VOLT 652412 [MI CTYE7 115.00] - VOLT 661010 [MILESCITYSW7115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to MPC03839POI (67020) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to MPC03839POI (67020) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 67022 [MPC03839TL 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on NESET___-BE4 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on NESET___-BE4 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on EDGELEY7 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY8 (652433) 69.0 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 b.2. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on EDGELEY7 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY8 (652433) 69.0 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 b.2. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on EDGELEY7 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on EDGELEY7 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on FORMAN 7 (652438) 115 kV Bus a. Apply Fault at the FORMAN 7 (652438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to FORMN 7 (620263) 115.0 kV Transmission Circuit #1 b.2. FORMAN 7 (652438) 115.0 kV to ROBERTSCTY7 (652455) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on FORMAN 7 (652438) 115 kV Bus a. Apply Fault at the FORMAN 7 (652438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to FORMN 7 (620263) 115.0 kV Transmission Circuit #1 b.2. FORMAN 7 (652438) 115.0 kV to ROBERTSCTY7 (652455) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 652438 [FORMAN 7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on ROBERTSCTY7 (652455) 115 kV Bus a. Apply Fault at the ROBERTSCTY7 (652455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.2. ROBERTSCTY7 (652455) 115.0 kV to FORMAN 7 (652438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on ROBERTSCTY7 (652455) 115 kV Bus a. Apply Fault at the ROBERTSCTY7 (652455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.2. ROBERTSCTY7 (652455) 115.0 kV to FORMAN 7 (652438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #1 b.2. BRISTOL-ER7 (655457) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #1 b.2. BRISTOL-ER7 (655457) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on GROTON__-BE3 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on GROTON__-BE3 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on DICKEYTP-CP8 (655625) 69 kV Bus a. Apply Fault at the DICKEYTP-CP8 (655625) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to EDGELEY8 (652433) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on DICKEYTP-CP8 (655625) 69 kV Bus a. Apply Fault at the DICKEYTP-CP8 (655625) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to EDGELEY8 (652433) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 b.3. TIOGA4 7 (661085) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 b.3. TIOGA4 7 (661085) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on BDV 4 (672603) 230 kV Bus a. Apply Fault at the BDV 4 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on BDV 4 (672603) 230 kV Bus a. Apply Fault at the BDV 4 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on VALLEYC7 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. VALLEYC7 (652454) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on VALLEYC7 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. VALLEYC7 (652454) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on FORMAN 7 (652438) 115 kV Bus a. Apply Fault at the FORMAN 7 (652438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 8 (652439) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 b.2. FORMAN 8 (652439) 69.0 kV to FORMAN 7 (652438) 115.0 kV to FORMAN9 (652393) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on FORMAN 7 (652438) 115 kV Bus a. Apply Fault at the FORMAN 7 (652438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 8 (652439) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 b.2. FORMAN 8 (652439) 69.0 kV to FORMAN 7 (652438) 115.0 kV to FORMAN9 (652393) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN7 (652445) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN7 (652445) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on WATERTN7 (652531) 115 kV Bus a. Apply Fault at the WATERTN7 (652531) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.2. WATERTN7 (652531) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on WATERTN7 (652531) 115 kV Bus a. Apply Fault at the WATERTN7 (652531) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.2. WATERTN7 (652531) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE7 (659141) 115 kV Bus a. Apply Fault at the NRTSHORE-BE7 (659141) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE7 (659141) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE7 (659141) 115 kV Bus a. Apply Fault at the NRTSHORE-BE7 (659141) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE7 (659141) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to BLAISDEL-BE4 (659143) 230.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to BLAISDEL-BE4 (659143) 230.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on GROTON__-BE7 (659187) 115 kV Bus a. Apply Fault at the GROTON__-BE7 (659187) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on GROTON__-BE7 (659187) 115 kV Bus a. Apply Fault at the GROTON__-BE7 (659187) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on SUMMIT-8 (652209) 69 kV Bus a. Apply Fault at the SUMMIT-8 (652209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT-8 (652209) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on SUMMIT-8 (652209) 69 kV Bus a. Apply Fault at the SUMMIT-8 (652209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT-8 (652209) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on EDGELEY8 (652433) 69 kV Bus a. Apply Fault at the EDGELEY8 (652433) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY8 (652433) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on EDGELEY8 (652433) 69 kV Bus a. Apply Fault at the EDGELEY8 (652433) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY8 (652433) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on MOS-HRON-ER8 (655058) 69 kV Bus a. Apply Fault at the MOS-HRON-ER8 (655058) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-HRON-ER8 (655058) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on MOS-HRON-ER8 (655058) 69 kV Bus a. Apply Fault at the MOS-HRON-ER8 (655058) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-HRON-ER8 (655058) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on MOS-WOLS-ER8 (655069) 69 kV Bus a. Apply Fault at the MOS-WOLS-ER8 (655069) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-WOLS-ER8 (655069) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on MOS-WOLS-ER8 (655069) 69 kV Bus a. Apply Fault at the MOS-WOLS-ER8 (655069) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-WOLS-ER8 (655069) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on VALLEYC8 (652204) 69 kV Bus a. Apply Fault at the VALLEYC8 (652204) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC8 (652204) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on VALLEYC8 (652204) 69 kV Bus a. Apply Fault at the VALLEYC8 (652204) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC8 (652204) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on STANLEY7 (661080) 115 kV Bus a. Apply Fault at the STANLEY7 (661080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on STANLEY7 (661080) 115 kV Bus a. Apply Fault at the STANLEY7 (661080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on EDGELEY7 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on EDGELEY7 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on FORMAN 7 (652438) 115 kV Bus a. Apply Fault at the FORMAN 7 (652438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on FORMAN 7 (652438) 115 kV Bus a. Apply Fault at the FORMAN 7 (652438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] - VOLT 652454 [VALLEYC7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] - VOLT 652454 [VALLEYC7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on ROBERTSCTY7 (652455) 115 kV Bus a. Apply Fault at the ROBERTSCTY7 (652455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY7 (652455) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on ROBERTSCTY7 (652455) 115 kV Bus a. Apply Fault at the ROBERTSCTY7 (652455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY7 (652455) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER7 (655457) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER7 (655457) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 7 (661085) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 7 (661085) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on GROTON__-BE3 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on GROTON__-BE3 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 760683 [GEN-2017-199345.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on TANDE___-BE3 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on MOS-WLMT-ER8 (655113) 69 kV Bus a. Apply Fault at the MOS-WLMT-ER8 (655113) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-WLMT-ER8 (655113) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on MOS-WLMT-ER8 (655113) 69 kV Bus a. Apply Fault at the MOS-WLMT-ER8 (655113) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-WLMT-ER8 (655113) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on MOS-MARV-ER8 (655118) 69 kV Bus a. Apply Fault at the MOS-MARV-ER8 (655118) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-MARV-ER8 (655118) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on MOS-MARV-ER8 (655118) 69 kV Bus a. Apply Fault at the MOS-MARV-ER8 (655118) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-MARV-ER8 (655118) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on MOS-ORTY-ER8 (655125) 69 kV Bus a. Apply Fault at the MOS-ORTY-ER8 (655125) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-ORTY-ER8 (655125) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on MOS-ORTY-ER8 (655125) 69 kV Bus a. Apply Fault at the MOS-ORTY-ER8 (655125) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-ORTY-ER8 (655125) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on DICKEYTP-CP8 (655625) 69 kV Bus a. Apply Fault at the DICKEYTP-CP8 (655625) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on DICKEYTP-CP8 (655625) 69 kV Bus a. Apply Fault at the DICKEYTP-CP8 (655625) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on VIRGIL-ER8 (655241) 69 kV Bus a. Apply Fault at the VIRGIL-ER8 (655241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIRGIL-ER8 (655241) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on VIRGIL-ER8 (655241) 69 kV Bus a. Apply Fault at the VIRGIL-ER8 (655241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIRGIL-ER8 (655241) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on BDV 4 (672603) 230 kV Bus a. Apply Fault at the BDV 4 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on BDV 4 (672603) 230 kV Bus a. Apply Fault at the BDV 4 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on RAY JCT7 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on RAY JCT7 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on VALLEYC7 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on VALLEYC7 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on FORMAN 8 (652439) 69 kV Bus a. Apply Fault at the FORMAN 8 (652439) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 8 (652439) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on FORMAN 8 (652439) 69 kV Bus a. Apply Fault at the FORMAN 8 (652439) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 8 (652439) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on JAMESTN7 (652445) 115 kV Bus a. Apply Fault at the JAMESTN7 (652445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN7 (652445) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on JAMESTN7 (652445) 115 kV Bus a. Apply Fault at the JAMESTN7 (652445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN7 (652445) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on ROBERTSCTY8 (652361) 69 kV Bus a. Apply Fault at the ROBERTSCTY8 (652361) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY8 (652361) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on ROBERTSCTY8 (652361) 69 kV Bus a. Apply Fault at the ROBERTSCTY8 (652361) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY8 (652361) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on WATERTN7 (652531) 115 kV Bus a. Apply Fault at the WATERTN7 (652531) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on WATERTN7 (652531) 115 kV Bus a. Apply Fault at the WATERTN7 (652531) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on BRISTOL-ER8 (655458) 69 kV Bus a. Apply Fault at the BRISTOL-ER8 (655458) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER8 (655458) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on BRISTOL-ER8 (655458) 69 kV Bus a. Apply Fault at the BRISTOL-ER8 (655458) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER8 (655458) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on ORDWAY-ER8 (655491) 69 kV Bus a. Apply Fault at the ORDWAY-ER8 (655491) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on ORDWAY-ER8 (655491) 69 kV Bus a. Apply Fault at the ORDWAY-ER8 (655491) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE7 (659141) 115 kV Bus a. Apply Fault at the NRTSHORE-BE7 (659141) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE7 (659141) 115 kV Bus a. Apply Fault at the NRTSHORE-BE7 (659141) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on LTLMUDY7 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on LTLMUDY7 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on GROTON__-BE7 (659187) 115 kV Bus a. Apply Fault at the GROTON__-BE7 (659187) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on GROTON__-BE7 (659187) 115 kV Bus a. Apply Fault at the GROTON__-BE7 (659187) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on TANDE___-BE4 (659337) 230 kV Bus a. Apply Fault at the TANDE___-BE4 (659337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on TANDE___-BE4 (659337) 230 kV Bus a. Apply Fault at the TANDE___-BE4 (659337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on SIOUXCY4 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on SIOUXCY4 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on WAYSIDE4 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on WAYSIDE4 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on GWINNER7 (620262) 115 kV Bus a. Apply Fault at the GWINNER7 (620262) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GWINNER7 (620262) 115.0 kV to FORMN 7 (620263) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on GWINNER7 (620262) 115 kV Bus a. Apply Fault at the GWINNER7 (620262) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GWINNER7 (620262) 115.0 kV to FORMN 7 (620263) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on JAMESTN4 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] - VOLT 652454 [VALLEYC7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on DAWSONC4 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on DAWSONC4 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on MT WEST4 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 652411 [MI CTYE4 230.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on MT WEST4 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 652395 [SHIRLEY TAP 115.00] - VOLT 652411 [MI CTYE4 230.00] - VOLT 652412 [MI CTYE7 115.00] - VOLT 659263 [LITTL_MS-BE7115.00] - VOLT 659265 [LITTL_MS-BE4230.00] - VOLT 661004 [BAKER 4 230.00] - VOLT 661010 [MILESCITYSW7115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on MT WEST4 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 652411 [MI CTYE4 230.00] - VOLT 652412 [MI CTYE7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on MT WEST4 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 652395 [SHIRLEY TAP 115.00] - VOLT 652403 [DAWSONC4 230.00] - VOLT 652404 [DAWSONC7 115.00] - VOLT 652411 [MI CTYE4 230.00] - VOLT 652412 [MI CTYE7 115.00] - VOLT 652616 [MINGUSVILLE4230.00] - VOLT 659535 [BEAVRHIL-GW4230.00] - VOLT 659536 [BEAVRHIL-GW7115.00] - VOLT 661010 [MILESCITYSW7115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on MI CTYE4 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on GRANITF4 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on GRANITF4 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on GRANITF4 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on GRANITF4 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on GARRISN4 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on GARRISN4 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on NUNDRWD4 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on MAURINE4 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on MAURINE4 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 652436 [FARGO 7 115.00] - VOLT 658160 [MPSBROOK 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 652436 [FARGO 7 115.00] - VOLT 658160 [MPSBROOK 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] - VOLT 652454 [VALLEYC7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] - VOLT 652454 [VALLEYC7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on GARRISN4 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on GARRISN4 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_273 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_273 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on FTRANDL7 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on FTRANDL7 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on SHEYNNE4 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on SHEYNNE4 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_290 | Single Phase Fault with Stuck Breaker on NOBLES 3 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_290 | Single Phase Fault with Stuck Breaker on NOBLES 3 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_291 | Single Phase Fault with Stuck Breaker on NOBLES 3 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_291 | Single Phase Fault with Stuck Breaker on NOBLES 3 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_292 | Single Phase Fault with Stuck Breaker on BRKNGCO3 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_292 | Single Phase Fault with Stuck Breaker on BRKNGCO3 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_293 | Single Phase Fault with Stuck Breaker on BRKNGCO3 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_293 | Single Phase Fault with Stuck Breaker on BRKNGCO3 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_294 | Single Phase Fault with Stuck Breaker on MAPLE R3 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_294 | Single Phase Fault with Stuck Breaker on MAPLE R3 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 89461 [J946 SUB 345.00] - VOLT 601067 [BISON 3 345.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_295 | Single Phase Fault with Stuck Breaker on CENTER 3 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_295 | Single Phase Fault with Stuck Breaker on CENTER 3 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_296 | Single Phase Fault with Stuck Breaker on CENTER 3 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_296 | Single Phase Fault with Stuck Breaker on CENTER 3 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_297 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_297 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_298 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_298 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_299 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_299 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on GRE-MCHENRY4 (615347) 230 kV Bus a. Apply Fault at the GRE-MCHENRY4 (615347) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1754 POI (47544) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.5. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.6. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.7. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on GRE-MCHENRY4 (615347) 230 kV Bus a. Apply Fault at the GRE-MCHENRY4 (615347) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1754 POI (47544) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.5. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.6. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.7. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_300 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_300 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_301 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_301 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_302 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_302 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_303 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_303 | Single Phase Fault with Stuck Breaker on PRAIRIE3 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_304 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_304 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 67022 [MPC03839TL 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_305 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_305 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_306 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_306 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_307 | Single Phase Fault with Stuck Breaker on JAMESTN3 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_307 | Single Phase Fault with Stuck Breaker on JAMESTN3 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_308 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_308 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_309 | Single Phase Fault with Stuck Breaker on BAKER 4 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_309 | Single Phase Fault with Stuck Breaker on BAKER 4 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low End of Sim Voltage (Near Faulted Bus) - VOLT 661005 [BAKER 7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.5. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.6. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.7. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.5. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.6. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.7. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_310 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_310 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_311 | Single Phase Fault with Stuck Breaker on NESET___-BE4 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_311 | Single Phase Fault with Stuck Breaker on NESET___-BE4 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_312 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_312 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_313 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_313 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_314 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_314 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_315 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_315 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_316 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_316 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_317 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_317 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_318 | Single Phase Fault with Stuck Breaker on EXIRA 5 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_318 | Single Phase Fault with Stuck Breaker on EXIRA 5 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_319 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_319 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_320 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_320 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_321 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_321 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_322 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_322 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_323 | Single Phase Fault with Stuck Breaker on GRANITF4 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_323 | Single Phase Fault with Stuck Breaker on GRANITF4 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_324 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_324 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_325 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_325 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_326 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_326 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_327 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_327 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_328 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_328 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_329 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_329 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.4. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.4. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_330 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_330 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_331 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_331 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on NESET___-BE4 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on NESET___-BE4 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on GROTON__-BE3 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GEN-2017-199 (760683) 345.0 kV Transmission Circuit #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.5. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on GROTON__-BE3 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GEN-2017-199 (760683) 345.0 kV Transmission Circuit #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.5. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on WTREAST7 (658088) 115 kV Bus a. Apply Fault at the WTREAST7 (658088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTREAST7 (658088) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 b.2. WTREAST7 (658088) 115.0 kV to WTRTNPP (658090) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on WTREAST7 (658088) 115 kV Bus a. Apply Fault at the WTREAST7 (658088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTREAST7 (658088) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 b.2. WTREAST7 (658088) 115.0 kV to WTRTNPP (658090) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on WTRPELI7 (658094) 115 kV Bus a. Apply Fault at the WTRPELI7 (658094) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 b.2. WTRWEST7 (658092) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on WTRPELI7 (658094) 115 kV Bus a. Apply Fault at the WTRPELI7 (658094) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 b.2. WTRWEST7 (658092) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on WTRTNPP (658090) 115 kV Bus a. Apply Fault at the WTRTNPP (658090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTREAST7 (658088) 115.0 kV to WTRTNPP (658090) 115.0 kV Transmission Circuit #1 b.2. WTRTNPP (658090) 115.0 kV to WTRTNPPG (658009) 13.8 kV Two Winding #1 b.3. WTRTNPP (658090) 115.0 kV to WTRWEST7 (658092) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on WTRTNPP (658090) 115 kV Bus a. Apply Fault at the WTRTNPP (658090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTREAST7 (658088) 115.0 kV to WTRTNPP (658090) 115.0 kV Transmission Circuit #1 b.2. WTRTNPP (658090) 115.0 kV to WTRTNPPG (658009) 13.8 kV Two Winding #1 b.3. WTRTNPP (658090) 115.0 kV to WTRWEST7 (658092) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on WTRWEST7 (658092) 115 kV Bus a. Apply Fault at the WTRWEST7 (658092) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTRTNPP (658090) 115.0 kV to WTRWEST7 (658092) 115.0 kV Transmission Circuit #1 b.2. WTRWEST7 (658092) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 b.3. WTRWEST7 (658092) 115.0 kV to WATERTOWN WA (660092) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on WTRWEST7 (658092) 115 kV Bus a. Apply Fault at the WTRWEST7 (658092) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WTRTNPP (658090) 115.0 kV to WTRWEST7 (658092) 115.0 kV Transmission Circuit #1 b.2. WTRWEST7 (658092) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 b.3. WTRWEST7 (658092) 115.0 kV to WATERTOWN WA (660092) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on ARLNGTN-ER7 (655462) 115 kV Bus a. Apply Fault at the ARLNGTN-ER7 (655462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKNG8 (652225) 69.0 kV to BROOKNG7 (652504) 115.0 kV Two Winding #1 b.2. AURORA 7 (652474) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 b.3. BROOKNG7 (652504) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.4. BROOKNG7 (652504) 115.0 kV to WHITE 7 (652538) 115.0 kV Transmission Circuit #1 b.5. BROOKNG7 (652504) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.6. BROOKNG7 (652504) 115.0 kV to BMUOLD77 (658148) 115.0 kV Transmission Circuit #1 b.7. BROOKNG7 (652504) 115.0 kV to BMU34AT7 (658154) 115.0 kV Transmission Circuit #1 b.8. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.9. ARLNGTN-ER7 (655462) 115.0 kV to ARLNGTN-ER8 (655463) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on ARLNGTN-ER7 (655462) 115 kV Bus a. Apply Fault at the ARLNGTN-ER7 (655462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKNG8 (652225) 69.0 kV to BROOKNG7 (652504) 115.0 kV Two Winding #1 b.2. AURORA 7 (652474) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 b.3. BROOKNG7 (652504) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.4. BROOKNG7 (652504) 115.0 kV to WHITE 7 (652538) 115.0 kV Transmission Circuit #1 b.5. BROOKNG7 (652504) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.6. BROOKNG7 (652504) 115.0 kV to BMUOLD77 (658148) 115.0 kV Transmission Circuit #1 b.7. BROOKNG7 (652504) 115.0 kV to BMU34AT7 (658154) 115.0 kV Transmission Circuit #1 b.8. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.9. ARLNGTN-ER7 (655462) 115.0 kV to ARLNGTN-ER8 (655463) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 652474 [AURORA 7 115.00] - VOLT 655379 [AURORAIP-ER7115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on EDGELEY7 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY9 (652322) 41.8 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.5. EDGELEY7 (652432) 115.0 kV to GEN-2018-039 (762735) 115.0 kV Transmission Circuit #1 b.6. EDGELEY 19 (652328) 13.2 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on EDGELEY7 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY9 (652322) 41.8 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.5. EDGELEY7 (652432) 115.0 kV to GEN-2018-039 (762735) 115.0 kV Transmission Circuit #1 b.6. EDGELEY 19 (652328) 13.2 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on ELLIOTT7 (652462) 115 kV Bus a. Apply Fault at the ELLIOTT7 (652462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.2. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on ELLIOTT7 (652462) 115 kV Bus a. Apply Fault at the ELLIOTT7 (652462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.2. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on FORMAN 7 (652438) 115 kV Bus a. Apply Fault at the FORMAN 7 (652438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMN 7 (620263) 115.0 kV to FORMAN 7 (652438) 115.0 kV Transmission Circuit #1 b.2. FORMAN 7 (652438) 115.0 kV to ROBERTSCTY7 (652455) 115.0 kV Transmission Circuit #1 b.3. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.4. FORMAN 7 (652438) 115.0 kV to LUDDEN -CP7 (659172) 115.0 kV Transmission Circuit #1 b.5. FORMAN 7 (652438) 115.0 kV to FORMAN 8 (652439) 69.0 kV to FORMAN9 (652393) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on FORMAN 7 (652438) 115 kV Bus a. Apply Fault at the FORMAN 7 (652438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMN 7 (620263) 115.0 kV to FORMAN 7 (652438) 115.0 kV Transmission Circuit #1 b.2. FORMAN 7 (652438) 115.0 kV to ROBERTSCTY7 (652455) 115.0 kV Transmission Circuit #1 b.3. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.4. FORMAN 7 (652438) 115.0 kV to LUDDEN -CP7 (659172) 115.0 kV Transmission Circuit #1 b.5. FORMAN 7 (652438) 115.0 kV to FORMAN 8 (652439) 69.0 kV to FORMAN9 (652393) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.2. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.3. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.4. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.5. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.6. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.2. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.3. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.4. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.5. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.6. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on SUMMIT-7 (652522) 115 kV Bus a. Apply Fault at the SUMMIT-7 (652522) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT-8 (652209) 69.0 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 b.2. SUMMIT-9 (652326) 43.8 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 b.3. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.4. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.5. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.6. SUMMIT-7 (652522) 115.0 kV to GEN-2018-007 (762449) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on SUMMIT-7 (652522) 115 kV Bus a. Apply Fault at the SUMMIT-7 (652522) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT-8 (652209) 69.0 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 b.2. SUMMIT-9 (652326) 43.8 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 b.3. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.4. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.5. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.6. SUMMIT-7 (652522) 115.0 kV to GEN-2018-007 (762449) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT9 (620167) 41.6 kV to PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT9 (620167) 41.6 kV to PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on VALLEYC7 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.5. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on VALLEYC7 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.5. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKNG7 (652504) 115.0 kV to WHITE 7 (652538) 115.0 kV Transmission Circuit #1 b.2. WHITE 7 (652538) 115.0 kV to IVANHOE-ER7 (655472) 115.0 kV Transmission Circuit #1 b.3. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 b.4. WHITE 7 (652538) 115.0 kV to WHITE 3 (652537) 345.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKNG7 (652504) 115.0 kV to WHITE 7 (652538) 115.0 kV Transmission Circuit #1 b.2. WHITE 7 (652538) 115.0 kV to IVANHOE-ER7 (655472) 115.0 kV Transmission Circuit #1 b.3. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 b.4. WHITE 7 (652538) 115.0 kV to WHITE 3 (652537) 345.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKNG7 (652504) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.2. WATERTN7 (652531) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 b.3. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKNG7 (652504) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.2. WATERTN7 (652531) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 b.3. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT18 (652242) 69.0 kV to WATERTN7 (652531) 115.0 kV Two Winding #1 b.2. BROOKNG7 (652504) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.3. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.4. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.5. WATERTN7 (652531) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 b.6. WATERTN7 (652531) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 b.7. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.8. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT18 (652242) 69.0 kV to WATERTN7 (652531) 115.0 kV Two Winding #1 b.2. BROOKNG7 (652504) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.3. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.4. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.5. WATERTN7 (652531) 115.0 kV to WTR15AV7 (658089) 115.0 kV Transmission Circuit #1 b.6. WATERTN7 (652531) 115.0 kV to WTRPELI7 (658094) 115.0 kV Transmission Circuit #1 b.7. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.8. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on GROTON__-BE3 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on GROTON__-BE3 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on STORLA__-BE4 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. MTVERN 7 (652518) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.3. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.4. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.5. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.6. STORLA__-BE7 (659123) 115.0 kV to STORLA__-BE4 (659122) 230.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on STORLA__-BE4 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. MTVERN 7 (652518) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.3. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.4. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.5. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.6. STORLA__-BE7 (659123) 115.0 kV to STORLA__-BE4 (659122) 230.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on HURON BTAP 7 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON WPARK8 (660012) 69.0 kV Two Winding #2 b.4. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on HURON BTAP 7 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON WPARK8 (660012) 69.0 kV Two Winding #2 b.4. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on BROWNSV4 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BIGSTN1G (620315) 24.0 kV Two Winding #1 b.3. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.4. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.5. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on BROWNSV4 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BIGSTN1G (620315) 24.0 kV Two Winding #1 b.3. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.4. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.5. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on CARPENTER 4 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on CARPENTER 4 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on FARGO 4 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.5. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GRNDFKS9 (652201) 12.5 kV to GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV Three Winding #1 b.6. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GRNDFKS9 (652201) 12.5 kV to GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV Three Winding #1 b.6. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_65 | Single Phase Fault with Stuck Breaker on BROADLND-BE3 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_65 | Single Phase Fault with Stuck Breaker on BROADLND-BE3 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_66 | Single Phase Fault with Stuck Breaker on BROADLND-BE3 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_66 | Single Phase Fault with Stuck Breaker on BROADLND-BE3 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_67 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_67 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_68 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_68 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_69 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_69 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_7 | Single Phase Fault with Stuck Breaker on BIGSTON4 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. MARIETT7 (620213) 115.0 kV to BIGSTON7 (620214) 115.0 kV Transmission Circuit #1 b.3. BIGSTON7 (620214) 115.0 kV to HIWY12 7 (620215) 115.0 kV Transmission Circuit #1 b.4. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.5. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.6. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.7. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #1 b.8. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #2 b.9. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #1 b.10. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_7 | Single Phase Fault with Stuck Breaker on BIGSTON4 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. MARIETT7 (620213) 115.0 kV to BIGSTON7 (620214) 115.0 kV Transmission Circuit #1 b.3. BIGSTON7 (620214) 115.0 kV to HIWY12 7 (620215) 115.0 kV Transmission Circuit #1 b.4. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.5. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.6. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.7. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #1 b.8. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #2 b.9. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #1 b.10. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_70 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_70 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_71 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_71 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_72 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_72 | Single Phase Fault with Stuck Breaker on HURON 4 (652514) 230 kV Bus a. Apply Fault at the HURON 4 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_73 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_73 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_74 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_74 | Single Phase Fault with Stuck Breaker on WATERTN3 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_75 | Single Phase Fault with Stuck Breaker on BISMARK4 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.11. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_75 | Single Phase Fault with Stuck Breaker on BISMARK4 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.11. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_76 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] - VOLT 652454 [VALLEYC7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_P4_FAULT_76 | Single Phase Fault with Stuck Breaker on PICKERT4 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High End of Sim Voltage (Near Faulted Bus) - VOLT 587050 [GEN-2016-007115.00] - VOLT 652445 [JAMESTN7 115.00] - VOLT 652454 [VALLEYC7 115.00] | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_P4_FAULT_77 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_77 | Single Phase Fault with Stuck Breaker on WATERTN4 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_78 | Single Phase Fault with Stuck Breaker on HURON WPARK7 (660003) 115 kV Bus a. Apply Fault at the HURON WPARK7 (660003) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.4. HURON WPARK7 (660003) 115.0 kV to HURON WPARK8 (660012) 69.0 kV Two Winding #1 b.5. HURON WPARK7 (660003) 115.0 kV to HURON WPARK8 (660012) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_78 | Single Phase Fault with Stuck Breaker on HURON WPARK7 (660003) 115 kV Bus a. Apply Fault at the HURON WPARK7 (660003) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.4. HURON WPARK7 (660003) 115.0 kV to HURON WPARK8 (660012) 69.0 kV Two Winding #1 b.5. HURON WPARK7 (660003) 115.0 kV to HURON WPARK8 (660012) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on ARLNGTN-ER7 (655462) 115 kV Bus a. Apply Fault at the ARLNGTN-ER7 (655462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA 7 (652474) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 b.2. AURORA 7 (652474) 115.0 kV to FLANDRU7 (652505) 115.0 kV Transmission Circuit #1 b.3. AURORA 7 (652474) 115.0 kV to AURORAIP-ER7 (655379) 115.0 kV Transmission Circuit #1 b.4. BROOKNG7 (652504) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.5. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.6. ARLNGTN-ER7 (655462) 115.0 kV to ARLNGTN-ER8 (655463) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on ARLNGTN-ER7 (655462) 115 kV Bus a. Apply Fault at the ARLNGTN-ER7 (655462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA 7 (652474) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 b.2. AURORA 7 (652474) 115.0 kV to FLANDRU7 (652505) 115.0 kV Transmission Circuit #1 b.3. AURORA 7 (652474) 115.0 kV to AURORAIP-ER7 (655379) 115.0 kV Transmission Circuit #1 b.4. BROOKNG7 (652504) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.5. WATERTN7 (652531) 115.0 kV to ARLNGTN-ER7 (655462) 115.0 kV Transmission Circuit #1 b.6. ARLNGTN-ER7 (655462) 115.0 kV to ARLNGTN-ER8 (655463) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_8 | Single Phase Fault with Stuck Breaker on BROWNSV4 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_8 | Single Phase Fault with Stuck Breaker on BROWNSV4 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on BROADLND-BE3 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on BROADLND-BE3 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_82 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_82 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_83 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_83 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_84 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to SLETTE -MW7 (655964) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_84 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to SLETTE -MW7 (655964) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_85 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_85 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_86 | Single Phase Fault with Stuck Breaker on WHTEARTH-MW7 (655930) 115 kV Bus a. Apply Fault at the WHTEARTH-MW7 (655930) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.3. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_86 | Single Phase Fault with Stuck Breaker on WHTEARTH-MW7 (655930) 115 kV Bus a. Apply Fault at the WHTEARTH-MW7 (655930) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.3. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_87 | Single Phase Fault with Stuck Breaker on PWRSLKTP-MW7 (655947) 115 kV Bus a. Apply Fault at the PWRSLKTP-MW7 (655947) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.3. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.4. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.5. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_87 | Single Phase Fault with Stuck Breaker on PWRSLKTP-MW7 (655947) 115 kV Bus a. Apply Fault at the PWRSLKTP-MW7 (655947) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.3. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.4. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.5. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_88 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.5. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.7. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.8. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.9. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_88 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.5. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.7. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.8. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.9. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_89 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_89 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_9 | Single Phase Fault with Stuck Breaker on BIGSTON4 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BSSOUTH4 (620322) 230.0 kV Transmission Circuit #2 b.3. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.4. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.5. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_9 | Single Phase Fault with Stuck Breaker on BIGSTON4 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 43.8 kV Two Winding #2 b.2. BIGSTON4 (620314) 230.0 kV to BSSOUTH4 (620322) 230.0 kV Transmission Circuit #2 b.3. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.4. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.5. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_90 | Single Phase Fault with Stuck Breaker on PALERMO -MW7 (655916) 115 kV Bus a. Apply Fault at the PALERMO -MW7 (655916) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.4. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_90 | Single Phase Fault with Stuck Breaker on PALERMO -MW7 (655916) 115 kV Bus a. Apply Fault at the PALERMO -MW7 (655916) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.4. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_91 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.4. BLAISDEL-BE7 (659144) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_91 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE7 (659144) 115 kV Bus a. Apply Fault at the BLAISDEL-BE7 (659144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.4. BLAISDEL-BE7 (659144) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_92 | Single Phase Fault with Stuck Breaker on MOE -MW7 (655900) 115 kV Bus a. Apply Fault at the MOE -MW7 (655900) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 b.4. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 b.5. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.6. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.7. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.8. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_92 | Single Phase Fault with Stuck Breaker on MOE -MW7 (655900) 115 kV Bus a. Apply Fault at the MOE -MW7 (655900) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 b.4. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 b.5. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.6. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.7. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.8. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_93 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_93 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_94 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_94 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_95 | Single Phase Fault with Stuck Breaker on CARNGTN7 (652428) 115 kV Bus a. Apply Fault at the CARNGTN7 (652428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN9 (652321) 41.8 kV to CARNGTN7 (652428) 115.0 kV Two Winding #1 b.2. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_95 | Single Phase Fault with Stuck Breaker on CARNGTN7 (652428) 115 kV Bus a. Apply Fault at the CARNGTN7 (652428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN9 (652321) 41.8 kV to CARNGTN7 (652428) 115.0 kV Two Winding #1 b.2. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_96 | Single Phase Fault with Stuck Breaker on WATFORD4 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_96 | Single Phase Fault with Stuck Breaker on WATFORD4 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_97 | Single Phase Fault with Stuck Breaker on WATFORD4 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_97 | Single Phase Fault with Stuck Breaker on WATFORD4 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_98 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_98 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_P4_FAULT_99 | Single Phase Fault with Stuck Breaker on DAKOTACCESS7 (660040) 115 kV Bus a. Apply Fault at the DAKOTACCESS7 (660040) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDFIELD 7 (660002) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.2. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_P4_FAULT_99 | Single Phase Fault with Stuck Breaker on DAKOTACCESS7 (660040) 115 kV Bus a. Apply Fault at the DAKOTACCESS7 (660040) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDFIELD 7 (660002) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.2. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_1 | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_1 | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_10 | 3 Phase fault on COLMB.E3 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_10 | 3 Phase fault on COLMB.E3 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_100 | 3 Phase fault on KNOLL 3 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_100 | 3 Phase fault on KNOLL 3 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_101 | 3 Phase fault on CHETOLAH3 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_101 | 3 Phase fault on CHETOLAH3 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_102 | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_102 | 3 Phase fault on POSTROCK6 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_103 | 3 Phase fault on CLRWATR7 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_103 | 3 Phase fault on CLRWATR7 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_104 | 3 Phase fault on BATTLCR7 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_104 | 3 Phase fault on BATTLCR7 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_105 | 3 Phase fault on KEAR.NE7 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_105 | 3 Phase fault on KEAR.NE7 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_106 | 3 Phase fault on DAVIDCY7 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_106 | 3 Phase fault on DAVIDCY7 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_107 | 3 Phase fault on STANTON7 (640357) 115 kV Bus a. Apply fault at the STANTON7 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_107 | 3 Phase fault on STANTON7 (640357) 115 kV Bus a. Apply fault at the STANTON7 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_108 | 3 Phase fault on MADISON7 (640263) 115 kV Bus a. Apply fault at the MADISON7 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_108 | 3 Phase fault on MADISON7 (640263) 115 kV Bus a. Apply fault at the MADISON7 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_109 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_109 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_11 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_11 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_110 | 3 Phase fault on COLMB.E3 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_110 | 3 Phase fault on COLMB.E3 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_111 | 3 Phase fault on E.COL. 4 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_111 | 3 Phase fault on E.COL. 4 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_112 | 3 Phase fault on COLMBUS4 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_112 | 3 Phase fault on COLMBUS4 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_113 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_113 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_114 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_114 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_115 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_115 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_116 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_116 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_117 | 3 Phase fault on GR ISLD3 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_117 | 3 Phase fault on GR ISLD3 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_118 | 3 Phase fault on KEYSTON3 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_118 | 3 Phase fault on KEYSTON3 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_119 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_119 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_12 | 3 Phase fault on NW68HOLDRG3 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_12 | 3 Phase fault on NW68HOLDRG3 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_120 | 3 Phase fault on PAULINE3 (640312) 345 kV Bus a. Apply fault at the PAULINE3 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_120 | 3 Phase fault on PAULINE3 (640312) 345 kV Bus a. Apply fault at the PAULINE3 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_121 | 3 Phase fault on SHELCRK3 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_121 | 3 Phase fault on SHELCRK3 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_122 | 3 Phase fault on TEKAMAH5 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_122 | 3 Phase fault on TEKAMAH5 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_123 | 3 Phase fault on ANTELOPE 3 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_123 | 3 Phase fault on ANTELOPE 3 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_124 | 3 Phase fault on THEDFRD3 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_124 | 3 Phase fault on THEDFRD3 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_125 | 3 Phase fault on MONOLITH 3 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_125 | 3 Phase fault on MONOLITH 3 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_126 | 3 Phase fault on MONOLITH 3 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_126 | 3 Phase fault on MONOLITH 3 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_127 | 3 Phase fault on GR ISLD3 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_127 | 3 Phase fault on GR ISLD3 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_128 | 3 Phase fault on GR ISLD3 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_128 | 3 Phase fault on GR ISLD3 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_129 | 3 Phase fault on CREITON7 (640149) 115 kV Bus a. Apply fault at the CREITON7 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_129 | 3 Phase fault on CREITON7 (640149) 115 kV Bus a. Apply fault at the CREITON7 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_13 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_13 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_130 | 3 Phase fault on HOLDREG7 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_130 | 3 Phase fault on HOLDREG7 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_131 | 3 Phase fault on KEARNEY7 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_131 | 3 Phase fault on KEARNEY7 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_132 | 3 Phase fault on NELIGH 7 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_132 | 3 Phase fault on NELIGH 7 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_133 | 3 Phase fault on NORFOLK7 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_133 | 3 Phase fault on NORFOLK7 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_134 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_134 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_135 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_135 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_136 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_136 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_137 | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_137 | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_138 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_138 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_139 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_139 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_14 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_14 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_140 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_140 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_141 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_141 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_142 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_142 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_143 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_143 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_144 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_144 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_145 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_145 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_146 | 3 Phase fault on S3458 3 (645458) 345 kV Bus a. Apply fault at the S3458 3 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_146 | 3 Phase fault on S3458 3 (645458) 345 kV Bus a. Apply fault at the S3458 3 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_147 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_147 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_148 | 3 Phase fault on TEKAMAH5 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_148 | 3 Phase fault on TEKAMAH5 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_149 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_149 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_15 | 3 Phase fault on NW68HOLDRG3 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_15 | 3 Phase fault on NW68HOLDRG3 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_150 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_150 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_151 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_151 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_152 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_152 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_153 | 3 Phase fault on S1216 5 (646216) 161 kV Bus a. Apply fault at the S1216 5 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_153 | 3 Phase fault on S1216 5 (646216) 161 kV Bus a. Apply fault at the S1216 5 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_154 | 3 Phase fault on S1206 5 (646206) 161 kV Bus a. Apply fault at the S1206 5 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_154 | 3 Phase fault on S1206 5 (646206) 161 kV Bus a. Apply fault at the S1206 5 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_155 | 3 Phase fault on S1206 5 (646206) 161 kV Bus a. Apply fault at the S1206 5 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_155 | 3 Phase fault on S1206 5 (646206) 161 kV Bus a. Apply fault at the S1206 5 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_156 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_156 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_157 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_157 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_158 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_158 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_159 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_159 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_16 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_16 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_160 | 3 Phase fault on S1211 5 (646211) 161 kV Bus a. Apply fault at the S1211 5 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_160 | 3 Phase fault on S1211 5 (646211) 161 kV Bus a. Apply fault at the S1211 5 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_161 | 3 Phase fault on S1250 5 (646250) 161 kV Bus a. Apply fault at the S1250 5 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_161 | 3 Phase fault on S1250 5 (646250) 161 kV Bus a. Apply fault at the S1250 5 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_162 | 3 Phase fault on S1211 5 (646211) 161 kV Bus a. Apply fault at the S1211 5 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_162 | 3 Phase fault on S1211 5 (646211) 161 kV Bus a. Apply fault at the S1211 5 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_163 | 3 Phase fault on S1299 5 (646299) 161 kV Bus a. Apply fault at the S1299 5 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_163 | 3 Phase fault on S1299 5 (646299) 161 kV Bus a. Apply fault at the S1299 5 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_164 | 3 Phase fault on S1214 5 (646214) 161 kV Bus a. Apply fault at the S1214 5 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_164 | 3 Phase fault on S1214 5 (646214) 161 kV Bus a. Apply fault at the S1214 5 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_165 | 3 Phase fault on S1221 5 (646221) 161 kV Bus a. Apply fault at the S1221 5 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_165 | 3 Phase fault on S1221 5 (646221) 161 kV Bus a. Apply fault at the S1221 5 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_166 | 3 Phase fault on S1222 5 (646222) 161 kV Bus a. Apply fault at the S1222 5 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_166 | 3 Phase fault on S1222 5 (646222) 161 kV Bus a. Apply fault at the S1222 5 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_167 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_167 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_168 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_168 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_169 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_169 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_17 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_17 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_170 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_170 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_171 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_171 | 3 Phase fault on S1226 5 (646226) 161 kV Bus a. Apply fault at the S1226 5 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_172 | 3 Phase fault on S1227 5 (646227) 161 kV Bus a. Apply fault at the S1227 5 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_172 | 3 Phase fault on S1227 5 (646227) 161 kV Bus a. Apply fault at the S1227 5 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_173 | 3 Phase fault on S1231 5 (646231) 161 kV Bus a. Apply fault at the S1231 5 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_173 | 3 Phase fault on S1231 5 (646231) 161 kV Bus a. Apply fault at the S1231 5 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_174 | 3 Phase fault on S1232 5 (646232) 161 kV Bus a. Apply fault at the S1232 5 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_174 | 3 Phase fault on S1232 5 (646232) 161 kV Bus a. Apply fault at the S1232 5 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_175 | 3 Phase fault on S1233 5 (646233) 161 kV Bus a. Apply fault at the S1233 5 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_175 | 3 Phase fault on S1233 5 (646233) 161 kV Bus a. Apply fault at the S1233 5 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_176 | 3 Phase fault on S1233 5 (646233) 161 kV Bus a. Apply fault at the S1233 5 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_176 | 3 Phase fault on S1233 5 (646233) 161 kV Bus a. Apply fault at the S1233 5 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_177 | 3 Phase fault on S1234 5 (646234) 161 kV Bus a. Apply fault at the S1234 5 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_177 | 3 Phase fault on S1234 5 (646234) 161 kV Bus a. Apply fault at the S1234 5 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_178 | 3 Phase fault on S1235 5 (646235) 161 kV Bus a. Apply fault at the S1235 5 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_178 | 3 Phase fault on S1235 5 (646235) 161 kV Bus a. Apply fault at the S1235 5 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_179 | 3 Phase fault on S1235 5 (646235) 161 kV Bus a. Apply fault at the S1235 5 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_179 | 3 Phase fault on S1235 5 (646235) 161 kV Bus a. Apply fault at the S1235 5 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_18 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_18 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_180 | 3 Phase fault on S1237 5 (646237) 161 kV Bus a. Apply fault at the S1237 5 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_180 | 3 Phase fault on S1237 5 (646237) 161 kV Bus a. Apply fault at the S1237 5 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_181 | 3 Phase fault on S1249 5 (646249) 161 kV Bus a. Apply fault at the S1249 5 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_181 | 3 Phase fault on S1249 5 (646249) 161 kV Bus a. Apply fault at the S1249 5 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_182 | 3 Phase fault on S1251 5 (646251) 161 kV Bus a. Apply fault at the S1251 5 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_182 | 3 Phase fault on S1251 5 (646251) 161 kV Bus a. Apply fault at the S1251 5 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_183 | 3 Phase fault on S1251 5 (646251) 161 kV Bus a. Apply fault at the S1251 5 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_183 | 3 Phase fault on S1251 5 (646251) 161 kV Bus a. Apply fault at the S1251 5 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_184 | 3 Phase fault on S1256 5 (646256) 161 kV Bus a. Apply fault at the S1256 5 (646256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_184 | 3 Phase fault on S1256 5 (646256) 161 kV Bus a. Apply fault at the S1256 5 (646256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_185 | 3 Phase fault on S1254 5 (646254) 161 kV Bus a. Apply fault at the S1254 5 (646254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_185 | 3 Phase fault on S1254 5 (646254) 161 kV Bus a. Apply fault at the S1254 5 (646254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_186 | 3 Phase fault on S1255 5 (646255) 161 kV Bus a. Apply fault at the S1255 5 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_186 | 3 Phase fault on S1255 5 (646255) 161 kV Bus a. Apply fault at the S1255 5 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_187 | 3 Phase fault on S1255 5 (646255) 161 kV Bus a. Apply fault at the S1255 5 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_187 | 3 Phase fault on S1255 5 (646255) 161 kV Bus a. Apply fault at the S1255 5 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_188 | 3 Phase fault on S1366 5 (646366) 161 kV Bus a. Apply fault at the S1366 5 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_188 | 3 Phase fault on S1366 5 (646366) 161 kV Bus a. Apply fault at the S1366 5 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_189 | 3 Phase fault on S1278 5 (646278) 161 kV Bus a. Apply fault at the S1278 5 (646278) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_189 | 3 Phase fault on S1278 5 (646278) 161 kV Bus a. Apply fault at the S1278 5 (646278) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_19 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_19 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_190 | 3 Phase fault on S1260 5 (646260) 161 kV Bus a. Apply fault at the S1260 5 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_190 | 3 Phase fault on S1260 5 (646260) 161 kV Bus a. Apply fault at the S1260 5 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_191 | 3 Phase fault on COOPER 5 (640140) 161 kV Bus a. Apply fault at the COOPER 5 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_191 | 3 Phase fault on COOPER 5 (640140) 161 kV Bus a. Apply fault at the COOPER 5 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_192 | 3 Phase fault on S1286 5 (646286) 161 kV Bus a. Apply fault at the S1286 5 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_192 | 3 Phase fault on S1286 5 (646286) 161 kV Bus a. Apply fault at the S1286 5 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_193 | 3 Phase fault on S1298 5 (646298) 161 kV Bus a. Apply fault at the S1298 5 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_193 | 3 Phase fault on S1298 5 (646298) 161 kV Bus a. Apply fault at the S1298 5 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_194 | 3 Phase fault on S1305 5 (646305) 161 kV Bus a. Apply fault at the S1305 5 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.4. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.6. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.7. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_194 | 3 Phase fault on S1305 5 (646305) 161 kV Bus a. Apply fault at the S1305 5 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.4. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.6. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.7. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_195 | 3 Phase fault on S1259 5 (646259) 161 kV Bus a. Apply fault at the S1259 5 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_195 | 3 Phase fault on S1259 5 (646259) 161 kV Bus a. Apply fault at the S1259 5 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_196 | 3 Phase fault on S1253 5 (646253) 161 kV Bus a. Apply fault at the S1253 5 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_196 | 3 Phase fault on S1253 5 (646253) 161 kV Bus a. Apply fault at the S1253 5 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_197 | 3 Phase fault on S1367 5 (646367) 161 kV Bus a. Apply fault at the S1367 5 (646367) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_197 | 3 Phase fault on S1367 5 (646367) 161 kV Bus a. Apply fault at the S1367 5 (646367) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_198 | 3 Phase fault on FC1A 5 (645100) 161 kV Bus a. Apply fault at the FC1A 5 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_198 | 3 Phase fault on FC1A 5 (645100) 161 kV Bus a. Apply fault at the FC1A 5 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_199 | 3 Phase fault on JCT205 8 (647105) 69 kV Bus a. Apply fault at the JCT205 8 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_199 | 3 Phase fault on JCT205 8 (647105) 69 kV Bus a. Apply fault at the JCT205 8 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_2 | 3 Phase fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_2 | 3 Phase fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_20 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_20 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_200 | 3 Phase fault on S901 8 (647901) 69 kV Bus a. Apply fault at the S901 8 (647901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_200 | 3 Phase fault on S901 8 (647901) 69 kV Bus a. Apply fault at the S901 8 (647901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_201 | 3 Phase fault on S937 8 (647937) 69 kV Bus a. Apply fault at the S937 8 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_201 | 3 Phase fault on S937 8 (647937) 69 kV Bus a. Apply fault at the S937 8 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_202 | 3 Phase fault on S904 8 (647904) 69 kV Bus a. Apply fault at the S904 8 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_202 | 3 Phase fault on S904 8 (647904) 69 kV Bus a. Apply fault at the S904 8 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_203 | 3 Phase fault on S906 S 8 (647906) 69 kV Bus a. Apply fault at the S906 S 8 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_203 | 3 Phase fault on S906 S 8 (647906) 69 kV Bus a. Apply fault at the S906 S 8 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_204 | 3 Phase fault on S906 S 8 (647906) 69 kV Bus a. Apply fault at the S906 S 8 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_204 | 3 Phase fault on S906 S 8 (647906) 69 kV Bus a. Apply fault at the S906 S 8 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_205 | 3 Phase fault on S907 8 (647907) 69 kV Bus a. Apply fault at the S907 8 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_205 | 3 Phase fault on S907 8 (647907) 69 kV Bus a. Apply fault at the S907 8 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_206 | 3 Phase fault on S907 8 (647907) 69 kV Bus a. Apply fault at the S907 8 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_206 | 3 Phase fault on S907 8 (647907) 69 kV Bus a. Apply fault at the S907 8 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_207 | 3 Phase fault on S908 8 (647908) 69 kV Bus a. Apply fault at the S908 8 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_207 | 3 Phase fault on S908 8 (647908) 69 kV Bus a. Apply fault at the S908 8 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_208 | 3 Phase fault on S908 8 (647908) 69 kV Bus a. Apply fault at the S908 8 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_208 | 3 Phase fault on S908 8 (647908) 69 kV Bus a. Apply fault at the S908 8 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_209 | 3 Phase fault on S909 8 (647909) 69 kV Bus a. Apply fault at the S909 8 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_209 | 3 Phase fault on S909 8 (647909) 69 kV Bus a. Apply fault at the S909 8 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_21 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_21 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_210 | 3 Phase fault on S909 8 (647909) 69 kV Bus a. Apply fault at the S909 8 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_210 | 3 Phase fault on S909 8 (647909) 69 kV Bus a. Apply fault at the S909 8 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_211 | 3 Phase fault on S909 8 (647909) 69 kV Bus a. Apply fault at the S909 8 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_211 | 3 Phase fault on S909 8 (647909) 69 kV Bus a. Apply fault at the S909 8 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_212 | 3 Phase fault on S910 8 (647910) 69 kV Bus a. Apply fault at the S910 8 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_212 | 3 Phase fault on S910 8 (647910) 69 kV Bus a. Apply fault at the S910 8 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_213 | 3 Phase fault on S911 8 (647911) 69 kV Bus a. Apply fault at the S911 8 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_213 | 3 Phase fault on S911 8 (647911) 69 kV Bus a. Apply fault at the S911 8 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_214 | 3 Phase fault on S912 8 (647912) 69 kV Bus a. Apply fault at the S912 8 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_214 | 3 Phase fault on S912 8 (647912) 69 kV Bus a. Apply fault at the S912 8 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_215 | 3 Phase fault on S906 N 8 (647006) 69 kV Bus a. Apply fault at the S906 N 8 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_215 | 3 Phase fault on S906 N 8 (647006) 69 kV Bus a. Apply fault at the S906 N 8 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_216 | 3 Phase fault on S918 8 (647918) 69 kV Bus a. Apply fault at the S918 8 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_216 | 3 Phase fault on S918 8 (647918) 69 kV Bus a. Apply fault at the S918 8 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_217 | 3 Phase fault on S919 8 (647919) 69 kV Bus a. Apply fault at the S919 8 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_217 | 3 Phase fault on S919 8 (647919) 69 kV Bus a. Apply fault at the S919 8 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_218 | 3 Phase fault on S919 8 (647919) 69 kV Bus a. Apply fault at the S919 8 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_218 | 3 Phase fault on S919 8 (647919) 69 kV Bus a. Apply fault at the S919 8 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_219 | 3 Phase fault on S921 8 (647921) 69 kV Bus a. Apply fault at the S921 8 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_219 | 3 Phase fault on S921 8 (647921) 69 kV Bus a. Apply fault at the S921 8 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_22 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_22 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_220 | 3 Phase fault on S921 8 (647921) 69 kV Bus a. Apply fault at the S921 8 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_220 | 3 Phase fault on S921 8 (647921) 69 kV Bus a. Apply fault at the S921 8 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_221 | 3 Phase fault on S906 N 8 (647006) 69 kV Bus a. Apply fault at the S906 N 8 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_221 | 3 Phase fault on S906 N 8 (647006) 69 kV Bus a. Apply fault at the S906 N 8 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_222 | 3 Phase fault on S912 8 (647912) 69 kV Bus a. Apply fault at the S912 8 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_222 | 3 Phase fault on S912 8 (647912) 69 kV Bus a. Apply fault at the S912 8 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_223 | 3 Phase fault on 6815TP38 (647016) 69 kV Bus a. Apply fault at the 6815TP38 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_223 | 3 Phase fault on 6815TP38 (647016) 69 kV Bus a. Apply fault at the 6815TP38 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_224 | 3 Phase fault on 6815TP98 (647017) 69 kV Bus a. Apply fault at the 6815TP98 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_224 | 3 Phase fault on 6815TP98 (647017) 69 kV Bus a. Apply fault at the 6815TP98 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_225 | 3 Phase fault on S939 8 (647939) 69 kV Bus a. Apply fault at the S939 8 (647939) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_225 | 3 Phase fault on S939 8 (647939) 69 kV Bus a. Apply fault at the S939 8 (647939) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_226 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_226 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_227 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_227 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_228 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_228 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_229 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_229 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_23 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_23 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_230 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_230 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_231 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_231 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_232 | 3 Phase fault on S3459 3 (645459) 345 kV Bus a. Apply fault at the S3459 3 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_232 | 3 Phase fault on S3459 3 (645459) 345 kV Bus a. Apply fault at the S3459 3 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_233 | 3 Phase fault on S3459 3 (645459) 345 kV Bus a. Apply fault at the S3459 3 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_233 | 3 Phase fault on S3459 3 (645459) 345 kV Bus a. Apply fault at the S3459 3 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_234 | 3 Phase fault on S3761 3 (645761) 345 kV Bus a. Apply fault at the S3761 3 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_234 | 3 Phase fault on S3761 3 (645761) 345 kV Bus a. Apply fault at the S3761 3 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_235 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_235 | 3 Phase fault on S1201 5 (646201) 161 kV Bus a. Apply fault at the S1201 5 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_236 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_236 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_237 | 3 Phase fault on S1210 5 (646210) 161 kV Bus a. Apply fault at the S1210 5 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_237 | 3 Phase fault on S1210 5 (646210) 161 kV Bus a. Apply fault at the S1210 5 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_238 | 3 Phase fault on S1211 5 (646211) 161 kV Bus a. Apply fault at the S1211 5 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_238 | 3 Phase fault on S1211 5 (646211) 161 kV Bus a. Apply fault at the S1211 5 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_239 | 3 Phase fault on S1221 5 (646221) 161 kV Bus a. Apply fault at the S1221 5 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_239 | 3 Phase fault on S1221 5 (646221) 161 kV Bus a. Apply fault at the S1221 5 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_24 | 3 Phase fault on RIVRBND5 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_24 | 3 Phase fault on RIVRBND5 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_240 | 3 Phase fault on S1250 5 (646250) 161 kV Bus a. Apply fault at the S1250 5 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_240 | 3 Phase fault on S1250 5 (646250) 161 kV Bus a. Apply fault at the S1250 5 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_241 | 3 Phase fault on S1217 5 (646217) 161 kV Bus a. Apply fault at the S1217 5 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_241 | 3 Phase fault on S1217 5 (646217) 161 kV Bus a. Apply fault at the S1217 5 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_242 | 3 Phase fault on S1366 5 (646366) 161 kV Bus a. Apply fault at the S1366 5 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_242 | 3 Phase fault on S1366 5 (646366) 161 kV Bus a. Apply fault at the S1366 5 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_243 | 3 Phase fault on S1291 5 (646291) 161 kV Bus a. Apply fault at the S1291 5 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_243 | 3 Phase fault on S1291 5 (646291) 161 kV Bus a. Apply fault at the S1291 5 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_244 | 3 Phase fault on S1260 5 (646260) 161 kV Bus a. Apply fault at the S1260 5 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_244 | 3 Phase fault on S1260 5 (646260) 161 kV Bus a. Apply fault at the S1260 5 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_245 | 3 Phase fault on S906 N 8 (647006) 69 kV Bus a. Apply fault at the S906 N 8 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_245 | 3 Phase fault on S906 N 8 (647006) 69 kV Bus a. Apply fault at the S906 N 8 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_246 | 3 Phase fault on S906 S 8 (647906) 69 kV Bus a. Apply fault at the S906 S 8 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_246 | 3 Phase fault on S906 S 8 (647906) 69 kV Bus a. Apply fault at the S906 S 8 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_247 | 3 Phase fault on S909 8 (647909) 69 kV Bus a. Apply fault at the S909 8 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_247 | 3 Phase fault on S909 8 (647909) 69 kV Bus a. Apply fault at the S909 8 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_248 | 3 Phase fault on S995 8 (647995) 69 kV Bus a. Apply fault at the S995 8 (647995) 69 kV Bus b. Clear fault after cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_248 | 3 Phase fault on S995 8 (647995) 69 kV Bus a. Apply fault at the S995 8 (647995) 69 kV Bus b. Clear fault after cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_249 | 3 Phase fault on FTTHOM1-LNX3 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_249 | 3 Phase fault on FTTHOM1-LNX3 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_25 | 3 Phase fault on OBRIEN 3 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_25 | 3 Phase fault on OBRIEN 3 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_250 | 3 Phase fault on SIOUXCY3 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_250 | 3 Phase fault on SIOUXCY3 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_251 | 3 Phase fault on SIOUXCY-LNX3 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_251 | 3 Phase fault on SIOUXCY-LNX3 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_252 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_252 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_253 | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_253 | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_254 | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_254 | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_255 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_255 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_256 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_256 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_257 | 3 Phase fault on J748POI (87487) 345 kV Bus a. Apply fault at the J748POI (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_257 | 3 Phase fault on J748POI (87487) 345 kV Bus a. Apply fault at the J748POI (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_258 | 3 Phase fault on J748POI (87487) 345 kV Bus a. Apply fault at the J748POI (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_258 | 3 Phase fault on J748POI (87487) 345 kV Bus a. Apply fault at the J748POI (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_259 | 3 Phase fault on KNOLL N 6 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_259 | 3 Phase fault on KNOLL N 6 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_26 | 3 Phase fault on LAKEFLD3 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_26 | 3 Phase fault on LAKEFLD3 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_260 | 3 Phase fault on KNOLL 3 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_260 | 3 Phase fault on KNOLL 3 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_261 | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_261 | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_262 | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_262 | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_263 | 3 Phase fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_263 | 3 Phase fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_264 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_264 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_265 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_265 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_266 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_266 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_267 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_267 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_268 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_268 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_269 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_269 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_27 | 3 Phase fault on HASTING5 (635032) 161 kV Bus a. Apply fault at the HASTING5 (635032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNGE 5 (635031) 161.0 kV to HASTING5 (635032) 161.0 kV Transmission Circuit #1 b.2. HASTING5 (635032) 161.0 kV to HASTING8 (635033) 69.0 kV Two Winding #1 b.3. HASTING5 (635032) 161.0 kV to CLRNDA 5 (635034) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_27 | 3 Phase fault on HASTING5 (635032) 161 kV Bus a. Apply fault at the HASTING5 (635032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNGE 5 (635031) 161.0 kV to HASTING5 (635032) 161.0 kV Transmission Circuit #1 b.2. HASTING5 (635032) 161.0 kV to HASTING8 (635033) 69.0 kV Two Winding #1 b.3. HASTING5 (635032) 161.0 kV to CLRNDA 5 (635034) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_270 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_270 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_271 | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_271 | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_272 | 3 Phase fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_272 | 3 Phase fault on G16-050-TAP (560082) 345 kV Bus a. Apply fault at the G16-050-TAP (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_273 | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_273 | 3 Phase fault on G17-021-TAP (588654) 345 kV Bus a. Apply fault at the G17-021-TAP (588654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_274 | 3 Phase fault on OVRLND 5 (635015) 161 kV Bus a. Apply fault at the OVRLND 5 (635015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_274 | 3 Phase fault on OVRLND 5 (635015) 161 kV Bus a. Apply fault at the OVRLND 5 (635015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_275 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_275 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_276 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_276 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_277 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_277 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_278 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_278 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_279 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_279 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_28 | 3 Phase fault on KELLOGG5 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_28 | 3 Phase fault on KELLOGG5 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_280 | 3 Phase fault on NEAL S 5 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_280 | 3 Phase fault on NEAL S 5 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_281 | 3 Phase fault on NEAL S 5 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_281 | 3 Phase fault on NEAL S 5 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_282 | 3 Phase fault on IDA CO 3 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_282 | 3 Phase fault on IDA CO 3 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_283 | 3 Phase fault on IDA CO 3 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_283 | 3 Phase fault on IDA CO 3 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_284 | 3 Phase fault on GARD AVE 3 (635219) 345 kV Bus a. Apply fault at the GARD AVE 3 (635219) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_284 | 3 Phase fault on GARD AVE 3 (635219) 345 kV Bus a. Apply fault at the GARD AVE 3 (635219) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_285 | 3 Phase fault on REMSEN 3 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_285 | 3 Phase fault on REMSEN 3 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_286 | 3 Phase fault on CHEROKEE 3 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_286 | 3 Phase fault on CHEROKEE 3 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_287 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_287 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_288 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_288 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_289 | 3 Phase fault on AXTELL 7 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_289 | 3 Phase fault on AXTELL 7 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_29 | 3 Phase fault on MONONA 5 (635300) 161 kV Bus a. Apply fault at the MONONA 5 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_29 | 3 Phase fault on MONONA 5 (635300) 161 kV Bus a. Apply fault at the MONONA 5 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_290 | 3 Phase fault on AXTELL 7 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_290 | 3 Phase fault on AXTELL 7 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_291 | 3 Phase fault on AXTELL 7 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_291 | 3 Phase fault on AXTELL 7 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_292 | 3 Phase fault on BELDEN 7 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_292 | 3 Phase fault on BELDEN 7 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_293 | 3 Phase fault on COLMB.E3 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_293 | 3 Phase fault on COLMB.E3 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_294 | 3 Phase fault on COLMBUS4 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_294 | 3 Phase fault on COLMBUS4 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_295 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_295 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_296 | 3 Phase fault on CREITON7 (640149) 115 kV Bus a. Apply fault at the CREITON7 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_296 | 3 Phase fault on CREITON7 (640149) 115 kV Bus a. Apply fault at the CREITON7 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_297 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_297 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_298 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_298 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_299 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_299 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_3 | 3 Phase fault on 33SUPERIOR7 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.6. 33SUPERIOR7 (650233) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_3 | 3 Phase fault on 33SUPERIOR7 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.6. 33SUPERIOR7 (650233) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_30 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_30 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_300 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_300 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_301 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_301 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_302 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_302 | 3 Phase fault on HOSKINS3 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_303 | 3 Phase fault on HOSKINS4 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_303 | 3 Phase fault on HOSKINS4 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_304 | 3 Phase fault on HOSKINS7 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_304 | 3 Phase fault on HOSKINS7 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_305 | 3 Phase fault on HOSKINS7 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_305 | 3 Phase fault on HOSKINS7 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_306 | 3 Phase fault on HOSKINS7 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_306 | 3 Phase fault on HOSKINS7 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_307 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_307 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_308 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_308 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_309 | 3 Phase fault on NELIGH 7 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_309 | 3 Phase fault on NELIGH 7 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_31 | 3 Phase fault on LEHIGH 3 (636010) 345 kV Bus a. Apply fault at the LEHIGH 3 (636010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEHIGH 3 (636010) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_31 | 3 Phase fault on LEHIGH 3 (636010) 345 kV Bus a. Apply fault at the LEHIGH 3 (636010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEHIGH 3 (636010) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_310 | 3 Phase fault on NELIGH 7 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_310 | 3 Phase fault on NELIGH 7 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_311 | 3 Phase fault on NORFK.N7 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_311 | 3 Phase fault on NORFK.N7 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_312 | 3 Phase fault on PAULINE3 (640312) 345 kV Bus a. Apply fault at the PAULINE3 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_312 | 3 Phase fault on PAULINE3 (640312) 345 kV Bus a. Apply fault at the PAULINE3 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_313 | 3 Phase fault on SWEET W3 (640374) 345 kV Bus a. Apply fault at the SWEET W3 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_313 | 3 Phase fault on SWEET W3 (640374) 345 kV Bus a. Apply fault at the SWEET W3 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_314 | 3 Phase fault on TEKAMAH5 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_314 | 3 Phase fault on TEKAMAH5 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_315 | 3 Phase fault on THEDFRD3 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_315 | 3 Phase fault on THEDFRD3 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_316 | 3 Phase fault on HOLT.CO3 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_316 | 3 Phase fault on HOLT.CO3 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_316 | 3 Phase fault on HOLT.CO3 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_316 | 3 Phase fault on HOLT.CO3 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_316 | 3 Phase fault on HOLT.CO3 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_317 | 3 Phase fault on ANTELOPE 3 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_317 | 3 Phase fault on ANTELOPE 3 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_318 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_318 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_319 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_319 | 3 Phase fault on S1209 5 (646209) 161 kV Bus a. Apply fault at the S1209 5 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_32 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_32 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_320 | 3 Phase fault on S1236 5 (646236) 161 kV Bus a. Apply fault at the S1236 5 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_320 | 3 Phase fault on S1236 5 (646236) 161 kV Bus a. Apply fault at the S1236 5 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_321 | 3 Phase fault on S1252 5 (646252) 161 kV Bus a. Apply fault at the S1252 5 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_321 | 3 Phase fault on S1252 5 (646252) 161 kV Bus a. Apply fault at the S1252 5 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_322 | 3 Phase fault on S1252 5 (646252) 161 kV Bus a. Apply fault at the S1252 5 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_322 | 3 Phase fault on S1252 5 (646252) 161 kV Bus a. Apply fault at the S1252 5 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_323 | 3 Phase fault on S1260 5 (646260) 161 kV Bus a. Apply fault at the S1260 5 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_323 | 3 Phase fault on S1260 5 (646260) 161 kV Bus a. Apply fault at the S1260 5 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_324 | 3 Phase fault on S1362 5 (646362) 161 kV Bus a. Apply fault at the S1362 5 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_324 | 3 Phase fault on S1362 5 (646362) 161 kV Bus a. Apply fault at the S1362 5 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_325 | 3 Phase fault on S1362 5 (646362) 161 kV Bus a. Apply fault at the S1362 5 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_325 | 3 Phase fault on S1362 5 (646362) 161 kV Bus a. Apply fault at the S1362 5 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_326 | 3 Phase fault on FTTHOMP3 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_326 | 3 Phase fault on FTTHOMP3 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_327 | 3 Phase fault on FTTHOM1-LNX5 (652808) 345 kV Bus a. Apply fault at the FTTHOM1-LNX5 (652808) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM1-LNX5 (652808) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_327 | 3 Phase fault on FTTHOM1-LNX5 (652808) 345 kV Bus a. Apply fault at the FTTHOM1-LNX5 (652808) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM1-LNX5 (652808) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_328 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_328 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_328 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_328 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_328 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_329 | 3 Phase fault on CHAPELLE-BE3 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_329 | 3 Phase fault on CHAPELLE-BE3 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_33 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_33 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_330 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_330 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_331 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_331 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_332 | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_332 | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_333 | 3 Phase fault on SUB701 5 (635003) 161 kV Bus a. Apply fault at the SUB701 5 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_333 | 3 Phase fault on SUB701 5 (635003) 161 kV Bus a. Apply fault at the SUB701 5 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_334 | 3 Phase fault on BATTLCR7 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_334 | 3 Phase fault on BATTLCR7 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_335 | 3 Phase fault on BELDEN 7 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_335 | 3 Phase fault on BELDEN 7 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_336 | 3 Phase fault on CREITON7 (640149) 115 kV Bus a. Apply fault at the CREITON7 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_336 | 3 Phase fault on CREITON7 (640149) 115 kV Bus a. Apply fault at the CREITON7 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_337 | 3 Phase fault on NELIGH 7 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_337 | 3 Phase fault on NELIGH 7 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_338 | 3 Phase fault on PAULINE7 (640313) 115 kV Bus a. Apply fault at the PAULINE7 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_338 | 3 Phase fault on PAULINE7 (640313) 115 kV Bus a. Apply fault at the PAULINE7 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_339 | 3 Phase fault on COOPER 5 (640140) 161 kV Bus a. Apply fault at the COOPER 5 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_339 | 3 Phase fault on COOPER 5 (640140) 161 kV Bus a. Apply fault at the COOPER 5 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_34 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_34 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_340 | 3 Phase fault on HOLDREG7 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_340 | 3 Phase fault on HOLDREG7 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_341 | 3 Phase fault on ANTELOPE 7 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_341 | 3 Phase fault on ANTELOPE 7 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_342 | 3 Phase fault on S1206 5 (646206) 161 kV Bus a. Apply fault at the S1206 5 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_342 | 3 Phase fault on S1206 5 (646206) 161 kV Bus a. Apply fault at the S1206 5 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_343 | 3 Phase fault on S1206 5 (646206) 161 kV Bus a. Apply fault at the S1206 5 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_343 | 3 Phase fault on S1206 5 (646206) 161 kV Bus a. Apply fault at the S1206 5 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_344 | 3 Phase fault on FTTHOMP3 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_344 | 3 Phase fault on FTTHOMP3 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_345 | 3 Phase fault on FTTHOMP3 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_345 | 3 Phase fault on FTTHOMP3 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_346 | 3 Phase fault on FTTHOMP3 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP39 (652275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_346 | 3 Phase fault on FTTHOMP3 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP39 (652275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_347 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_347 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_348 | 3 Phase fault on NEAL N 8 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_348 | 3 Phase fault on NEAL N 8 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_349 | 3 Phase fault on FTTHOM2-LNX3 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_349 | 3 Phase fault on FTTHOM2-LNX3 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_35 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_35 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_350 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_350 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_351 | 3 Phase fault on GRPRAR2-LNX3 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_351 | 3 Phase fault on GRPRAR2-LNX3 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_352 | 3 Phase fault on GR ISLD3 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_352 | 3 Phase fault on GR ISLD3 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_353 | 3 Phase fault on GR ISLD-LNX3 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_353 | 3 Phase fault on GR ISLD-LNX3 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_354 | 3 Phase fault on CC.LS-LO-BE3 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_354 | 3 Phase fault on CC.LS-LO-BE3 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_355 | 3 Phase fault on TRIPLEH__UA3 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_355 | 3 Phase fault on TRIPLEH__UA3 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_356 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. G18-056-TAP (762916) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_356 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. G18-056-TAP (762916) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_357 | 3 Phase fault on HOLT.CO3 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_357 | 3 Phase fault on HOLT.CO3 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_358 | 3 Phase fault on S6815T3 8 (647815) 69 kV Bus a. Apply fault at the S6815T3 8 (647815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.3. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_358 | 3 Phase fault on S6815T3 8 (647815) 69 kV Bus a. Apply fault at the S6815T3 8 (647815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.3. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_359 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_359 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_36 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_36 | 3 Phase fault on SPLT RK3 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_360 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_360 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_361 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_361 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_362 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_362 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_363 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_363 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_364 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_364 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_365 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_365 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_366 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_366 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_367 | 3 Phase fault on OVRLND 3 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_367 | 3 Phase fault on OVRLND 3 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_368 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_368 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_369 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_369 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_37 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_37 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_370 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_370 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_371 | 3 Phase fault on OVRLND 3 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_371 | 3 Phase fault on OVRLND 3 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_372 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_372 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_373 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_373 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_374 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_374 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_375 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_375 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_376 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_376 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_377 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_377 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_378 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_378 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_379 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_379 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_38 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_38 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_380 | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_380 | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_381 | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_381 | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_382 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_382 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_383 | 3 Phase fault on MEADOWGROVE4 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_383 | 3 Phase fault on MEADOWGROVE4 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_384 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_384 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_385 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_385 | 3 Phase fault on FTRANDL4 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_386 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_386 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_387 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_387 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_388 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_388 | 3 Phase fault on GENTLMN3 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_389 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_389 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_39 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_39 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_390 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_390 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_4 | 3 Phase fault on 56&Q 7 (650260) 115 kV Bus a. Apply fault at the 56&Q 7 (650260) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_4 | 3 Phase fault on 56&Q 7 (650260) 115 kV Bus a. Apply fault at the 56&Q 7 (650260) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_40 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_40 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_41 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_41 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_42 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_42 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_43 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_43 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_44 | 3 Phase fault on SUB701 5 (635003) 161 kV Bus a. Apply fault at the SUB701 5 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_44 | 3 Phase fault on SUB701 5 (635003) 161 kV Bus a. Apply fault at the SUB701 5 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_45 | 3 Phase fault on QUICK 5 (635012) 161 kV Bus a. Apply fault at the QUICK 5 (635012) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_45 | 3 Phase fault on QUICK 5 (635012) 161 kV Bus a. Apply fault at the QUICK 5 (635012) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_46 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_46 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_47 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_47 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_48 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_48 | 3 Phase fault on PNYCRK 3 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_49 | 3 Phase fault on OVRLND 3 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_49 | 3 Phase fault on OVRLND 3 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_5 | 3 Phase fault on 57&GARLAND7 (650262) 115 kV Bus a. Apply fault at the 57&GARLAND7 (650262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_5 | 3 Phase fault on 57&GARLAND7 (650262) 115 kV Bus a. Apply fault at the 57&GARLAND7 (650262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_50 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_50 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_51 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_51 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_52 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_52 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_53 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_53 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_54 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_54 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_55 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_55 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_56 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_56 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_57 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_57 | 3 Phase fault on RAUN 5 (635201) 161 kV Bus a. Apply fault at the RAUN 5 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_58 | 3 Phase fault on INTCHG 5 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_58 | 3 Phase fault on INTCHG 5 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_59 | 3 Phase fault on KELLOGG5 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_59 | 3 Phase fault on KELLOGG5 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_6 | 3 Phase fault on 93&O 7 (650273) 115 kV Bus a. Apply fault at the 93&O 7 (650273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_6 | 3 Phase fault on 93&O 7 (650273) 115 kV Bus a. Apply fault at the 93&O 7 (650273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_60 | 3 Phase fault on MORNSD 5 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_60 | 3 Phase fault on MORNSD 5 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_61 | 3 Phase fault on AIRPORT 5 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_61 | 3 Phase fault on AIRPORT 5 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_62 | 3 Phase fault on WEBSTER3 (636000) 345 kV Bus a. Apply fault at the WEBSTER3 (636000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_62 | 3 Phase fault on WEBSTER3 (636000) 345 kV Bus a. Apply fault at the WEBSTER3 (636000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_63 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_63 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_64 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_64 | 3 Phase fault on CBLUFFS5 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_65 | 3 Phase fault on OVRLND 3 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_65 | 3 Phase fault on OVRLND 3 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_66 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_66 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_67 | 3 Phase fault on NEAL N 5 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_67 | 3 Phase fault on NEAL N 5 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_68 | 3 Phase fault on SALIX 5 (635235) 161 kV Bus a. Apply fault at the SALIX 5 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_68 | 3 Phase fault on SALIX 5 (635235) 161 kV Bus a. Apply fault at the SALIX 5 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_69 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_69 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_7 | 3 Phase fault on 84FLETCHER7 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_7 | 3 Phase fault on 84FLETCHER7 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_70 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_70 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_71 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_71 | 3 Phase fault on RAUN 3 (635200) 345 kV Bus a. Apply fault at the RAUN 3 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_72 | 3 Phase fault on MANAWA 5 (635010) 161 kV Bus a. Apply fault at the MANAWA 5 (635010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_72 | 3 Phase fault on MANAWA 5 (635010) 161 kV Bus a. Apply fault at the MANAWA 5 (635010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_73 | 3 Phase fault on SUB701 5 (635003) 161 kV Bus a. Apply fault at the SUB701 5 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_73 | 3 Phase fault on SUB701 5 (635003) 161 kV Bus a. Apply fault at the SUB701 5 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_74 | 3 Phase fault on S3458 3 (645458) 345 kV Bus a. Apply fault at the S3458 3 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_74 | 3 Phase fault on S3458 3 (645458) 345 kV Bus a. Apply fault at the S3458 3 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_75 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_75 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_76 | 3 Phase fault on MC REAC3 (541413) 345 kV Bus a. Apply fault at the MC REAC3 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_76 | 3 Phase fault on MC REAC3 (541413) 345 kV Bus a. Apply fault at the MC REAC3 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_77 | 3 Phase fault on MC REAC2 (541412) 345 kV Bus a. Apply fault at the MC REAC2 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_77 | 3 Phase fault on MC REAC2 (541412) 345 kV Bus a. Apply fault at the MC REAC2 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_78 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_78 | 3 Phase fault on FTTHOMP4 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_79 | 3 Phase fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_79 | 3 Phase fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_8 | 3 Phase fault on 84LEIGHTON7 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_8 | 3 Phase fault on 84LEIGHTON7 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_80 | 3 Phase fault on 120&ALVO 7 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_80 | 3 Phase fault on 120&ALVO 7 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_81 | 3 Phase fault on 120&ALVO 7 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_81 | 3 Phase fault on 120&ALVO 7 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_82 | 3 Phase fault on 70&CALVERT7 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 70&CALVERT7 (650270) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_82 | 3 Phase fault on 70&CALVERT7 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 70&CALVERT7 (650270) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_83 | 3 Phase fault on SD.LS-KS-MB3 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_83 | 3 Phase fault on SD.LS-KS-MB3 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_84 | 3 Phase fault on SIOUXCY-LNX3 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_84 | 3 Phase fault on SIOUXCY-LNX3 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_85 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-056-TAP (762916) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_85 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-056-TAP (762916) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_85 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-056-TAP (762916) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Base Case | GROUP2_P1_FAULT_85 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-056-TAP (762916) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Base Case | GROUP2_P1_FAULT_85 | 3 Phase fault on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-056-TAP (762916) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_86 | 3 Phase fault on GR ISLD-LNX3 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_86 | 3 Phase fault on GR ISLD-LNX3 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_86 | 3 Phase fault on GR ISLD-LNX3 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_86 | 3 Phase fault on GR ISLD-LNX3 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_86 | 3 Phase fault on GR ISLD-LNX3 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_87 | 3 Phase fault on FTTHOM2-LNX3 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_87 | 3 Phase fault on FTTHOM2-LNX3 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_87 | 3 Phase fault on FTTHOM2-LNX3 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_87 | 3 Phase fault on FTTHOM2-LNX3 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_87 | 3 Phase fault on FTTHOM2-LNX3 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_88 | 3 Phase fault on REDLIN 3 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_88 | 3 Phase fault on REDLIN 3 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_89 | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_89 | 3 Phase fault on S HAYS 3 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_9 | 3 Phase fault on 81&OCHENEY7 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_9 | 3 Phase fault on 81&OCHENEY7 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_90 | 3 Phase fault on SALINE 3 (530551) 115 kV Bus a. Apply fault at the SALINE 3 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_90 | 3 Phase fault on SALINE 3 (530551) 115 kV Bus a. Apply fault at the SALINE 3 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_91 | 3 Phase fault on OGALATP3 (530677) 115 kV Bus a. Apply fault at the OGALATP3 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_91 | 3 Phase fault on OGALATP3 (530677) 115 kV Bus a. Apply fault at the OGALATP3 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_92 | 3 Phase fault on GORHAM 3 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_92 | 3 Phase fault on GORHAM 3 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_93 | 3 Phase fault on KNOLL N 6 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_93 | 3 Phase fault on KNOLL N 6 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_94 | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_94 | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_95 | 3 Phase fault on HEIZER 6 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_95 | 3 Phase fault on HEIZER 6 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_96 | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_96 | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_97 | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_97 | 3 Phase fault on POSTROCK7 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_98 | 3 Phase fault on KNOLL N 6 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_98 | 3 Phase fault on KNOLL N 6 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P1_FAULT_99 | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P1_FAULT_99 | 3 Phase fault on S HAYS6 (530582) 230 kV Bus a. Apply fault at the S HAYS6 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on S1232 5 (646232) 161 kV Bus a. Apply Fault at the S1232 5 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on S1232 5 (646232) 161 kV Bus a. Apply Fault at the S1232 5 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on S1233 5 (646233) 161 kV Bus a. Apply Fault at the S1233 5 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on S1233 5 (646233) 161 kV Bus a. Apply Fault at the S1233 5 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on S1235 5 (646235) 161 kV Bus a. Apply Fault at the S1235 5 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on S1235 5 (646235) 161 kV Bus a. Apply Fault at the S1235 5 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on S1235 5 (646235) 161 kV Bus a. Apply Fault at the S1235 5 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on S1235 5 (646235) 161 kV Bus a. Apply Fault at the S1235 5 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on S1237 5 (646237) 161 kV Bus a. Apply Fault at the S1237 5 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on S1237 5 (646237) 161 kV Bus a. Apply Fault at the S1237 5 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on S1249 5 (646249) 161 kV Bus a. Apply Fault at the S1249 5 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on S1249 5 (646249) 161 kV Bus a. Apply Fault at the S1249 5 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on S1297 5 (646297) 161 kV Bus a. Apply Fault at the S1297 5 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on S1297 5 (646297) 161 kV Bus a. Apply Fault at the S1297 5 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on S1211 5 (646211) 161 kV Bus a. Apply Fault at the S1211 5 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on S1211 5 (646211) 161 kV Bus a. Apply Fault at the S1211 5 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on S1297 5 (646297) 161 kV Bus a. Apply Fault at the S1297 5 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on S1297 5 (646297) 161 kV Bus a. Apply Fault at the S1297 5 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on S1252 5 (646252) 161 kV Bus a. Apply Fault at the S1252 5 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on S1252 5 (646252) 161 kV Bus a. Apply Fault at the S1252 5 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on S1253 5 (646253) 161 kV Bus a. Apply Fault at the S1253 5 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on S1253 5 (646253) 161 kV Bus a. Apply Fault at the S1253 5 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on S1259 5 (646259) 161 kV Bus a. Apply Fault at the S1259 5 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on S1259 5 (646259) 161 kV Bus a. Apply Fault at the S1259 5 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on S1278 5 (646278) 161 kV Bus a. Apply Fault at the S1278 5 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on S1278 5 (646278) 161 kV Bus a. Apply Fault at the S1278 5 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on S1278 5 (646278) 161 kV Bus a. Apply Fault at the S1278 5 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on S1278 5 (646278) 161 kV Bus a. Apply Fault at the S1278 5 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on S1278 5 (646278) 161 kV Bus a. Apply Fault at the S1278 5 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on S1278 5 (646278) 161 kV Bus a. Apply Fault at the S1278 5 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on S1286 5 (646286) 161 kV Bus a. Apply Fault at the S1286 5 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on S1286 5 (646286) 161 kV Bus a. Apply Fault at the S1286 5 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on S1287 5 (646287) 161 kV Bus a. Apply Fault at the S1287 5 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on S1287 5 (646287) 161 kV Bus a. Apply Fault at the S1287 5 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on S1305 5 (646305) 161 kV Bus a. Apply Fault at the S1305 5 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on S1305 5 (646305) 161 kV Bus a. Apply Fault at the S1305 5 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on S1305 5 (646305) 161 kV Bus a. Apply Fault at the S1305 5 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on S1305 5 (646305) 161 kV Bus a. Apply Fault at the S1305 5 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on SUB702 5 (635005) 161 kV Bus a. Apply Fault at the SUB702 5 (635005) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.2. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on SUB702 5 (635005) 161 kV Bus a. Apply Fault at the SUB702 5 (635005) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.2. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on S1299 5 (646299) 161 kV Bus a. Apply Fault at the S1299 5 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on S1299 5 (646299) 161 kV Bus a. Apply Fault at the S1299 5 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on S1291 5 (646291) 161 kV Bus a. Apply Fault at the S1291 5 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on S1291 5 (646291) 161 kV Bus a. Apply Fault at the S1291 5 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on S1341 5 (646341) 161 kV Bus a. Apply Fault at the S1341 5 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on S1341 5 (646341) 161 kV Bus a. Apply Fault at the S1341 5 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on TEKAMAH5 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on TEKAMAH5 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on SUB701 5 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on SUB701 5 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.5. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on LETCHER4 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 b.4. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.5. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on LETCHER4 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 b.4. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 b.5. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on STORLA__-BE4 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.5. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on STORLA__-BE4 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.5. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.3. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.8. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.3. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.8. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on OBRIEN 3 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.3. LAKEFLD3 (631138) 345.0 kV (Trip Shunt Device) b.4. OBRIEN 3 (635368) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on OBRIEN 3 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.3. LAKEFLD3 (631138) 345.0 kV (Trip Shunt Device) b.4. OBRIEN 3 (635368) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on BIGBND14 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding #1 b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on BIGBND14 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding #1 b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on BIGBND24 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding #1 b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on BIGBND24 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding #1 b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on AIRPORT 5 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on AIRPORT 5 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on SIOUXCY4 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on SIOUXCY4 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on SHAYS_230 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on SHAYS_230 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to None to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to None to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to None to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to None to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on OBRIEN 3 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on OBRIEN 3 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on SPLT RK3 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on OBRIEN 3 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B3 9 (635403) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on OBRIEN 3 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on TEKAMAH5 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on TEKAMAH5 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on S1201 5 (646201) 161 kV Bus a. Apply Fault at the S1201 5 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.2. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.3. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 b.4. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.5. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.6. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on S1201 5 (646201) 161 kV Bus a. Apply Fault at the S1201 5 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.2. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.3. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 b.4. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.5. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.6. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on S907 8 (647907) 69 kV Bus a. Apply Fault at the S907 8 (647907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on S907 8 (647907) 69 kV Bus a. Apply Fault at the S907 8 (647907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on S1210 5 (646210) 161 kV Bus a. Apply Fault at the S1210 5 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on S1210 5 (646210) 161 kV Bus a. Apply Fault at the S1210 5 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on S1211 5 (646211) 161 kV Bus a. Apply Fault at the S1211 5 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on S1211 5 (646211) 161 kV Bus a. Apply Fault at the S1211 5 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on S912 8 (647912) 69 kV Bus a. Apply Fault at the S912 8 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on S912 8 (647912) 69 kV Bus a. Apply Fault at the S912 8 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on S919 8 (647919) 69 kV Bus a. Apply Fault at the S919 8 (647919) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.3. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on S919 8 (647919) 69 kV Bus a. Apply Fault at the S919 8 (647919) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.3. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on S1221 5 (646221) 161 kV Bus a. Apply Fault at the S1221 5 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.3. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 b.4. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on S1221 5 (646221) 161 kV Bus a. Apply Fault at the S1221 5 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.3. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 b.4. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on S923 8 (647923) 69 kV Bus a. Apply Fault at the S923 8 (647923) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 b.3. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on S923 8 (647923) 69 kV Bus a. Apply Fault at the S923 8 (647923) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 b.3. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on S906 N 8 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on S906 N 8 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on S906 S 8 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on S906 S 8 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.6. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.7. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.8. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.11. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP39 (652275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on FTTHOMP3 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.6. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.7. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.8. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.11. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP39 (652275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on WEBSTER3 (636000) 345 kV Bus a. Apply Fault at the WEBSTER3 (636000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 b.2. WEBSTER3 (636000) 345.0 kV (Trip Shunt Device) b.3. IRVINGTON3 (635999) 345.0 kV to WEBSTER3 (636000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on WEBSTER3 (636000) 345 kV Bus a. Apply Fault at the WEBSTER3 (636000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 b.2. WEBSTER3 (636000) 345.0 kV (Trip Shunt Device) b.3. IRVINGTON3 (635999) 345.0 kV to WEBSTER3 (636000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.8. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.8. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.2. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.2. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on TEKAMAH5 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.5. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on TEKAMAH5 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.5. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on INTCHG 5 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on INTCHG 5 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to None Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to None Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. None to SPERVIL7 (531469) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. None to SPERVIL7 (531469) 345.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.8. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on OAHE 4 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.8. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.2. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.2. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on SALIX 5 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on SALIX 5 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to G17-094-TAP (589324) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on MONONA 5 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on MONONA 5 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on NEAL S 5 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on NEAL S 5 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on J748POI (87487) 345 kV Bus a. Apply Fault at the J748POI (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on J748POI (87487) 345 kV Bus a. Apply Fault at the J748POI (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on CO.LINE7 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CO.LINE7 (640115) 115.0 kV to BATTLCR7 (640072) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on CO.LINE7 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CO.LINE7 (640115) 115.0 kV to BATTLCR7 (640072) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on THEDFRD3 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on THEDFRD3 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on HOLT.CO3 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on HOLT.CO3 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on NEAL N 5 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on NEAL N 5 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_290 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_290 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_291 | Single Phase Fault with Stuck Breaker on G18-043-TAP (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_291 | Single Phase Fault with Stuck Breaker on G18-043-TAP (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_292 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_292 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_293 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_293 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_294 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_294 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_295 | Single Phase Fault with Stuck Breaker on PAULINE7 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to HASTING7 (640215) 115.0 kV Transmission Circuit #1 b.2. PAULINE7 (640313) 115.0 kV to HILDRTH7 (640222) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_295 | Single Phase Fault with Stuck Breaker on PAULINE7 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to HASTING7 (640215) 115.0 kV Transmission Circuit #1 b.2. PAULINE7 (640313) 115.0 kV to HILDRTH7 (640222) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_296 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK4 (640343) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_296 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK4 (640343) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_297 | Single Phase Fault with Stuck Breaker on THEDFRD3 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_297 | Single Phase Fault with Stuck Breaker on THEDFRD3 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_298 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_298 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_299 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_299 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on AIRPORT 5 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on AIRPORT 5 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on KELLOGG5 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on KELLOGG5 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_300 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_300 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_301 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_301 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_302 | Single Phase Fault with Stuck Breaker on REMSEN 3 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 b.2. REMSEN 3 (635398) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_302 | Single Phase Fault with Stuck Breaker on REMSEN 3 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 b.2. REMSEN 3 (635398) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_303 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_303 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to G18-056-TAP (762916) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_304 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_304 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_305 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_305 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_306 | Single Phase Fault with Stuck Breaker on CREITON7 (640149) 115 kV Bus a. Apply Fault at the CREITON7 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_306 | Single Phase Fault with Stuck Breaker on CREITON7 (640149) 115 kV Bus a. Apply Fault at the CREITON7 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_307 | Single Phase Fault with Stuck Breaker on NELIGH 7 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_307 | Single Phase Fault with Stuck Breaker on NELIGH 7 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_308 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_308 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_309 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_309 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on EXIRA 5 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on EXIRA 5 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_310 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 3 (640520) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_310 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 3 (640520) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_311 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.2. S1254 5 (646254) 161.0 kV to S1249 5 (646249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_311 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.2. S1254 5 (646254) 161.0 kV to S1249 5 (646249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_312 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_312 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_313 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_313 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_314 | Single Phase Fault with Stuck Breaker on J748POI (87487) 345 kV Bus a. Apply Fault at the J748POI (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_314 | Single Phase Fault with Stuck Breaker on J748POI (87487) 345 kV Bus a. Apply Fault at the J748POI (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_315 | Single Phase Fault with Stuck Breaker on GEN-2015-023 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_315 | Single Phase Fault with Stuck Breaker on GEN-2015-023 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_316 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_316 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_317 | Single Phase Fault with Stuck Breaker on CO.LINE7 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_317 | Single Phase Fault with Stuck Breaker on CO.LINE7 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_318 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_318 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_319 | Single Phase Fault with Stuck Breaker on THEDFRD3 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_319 | Single Phase Fault with Stuck Breaker on THEDFRD3 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on SUB701 5 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 b.5. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 b.7. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on SUB701 5 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 b.5. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 b.7. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_320 | Single Phase Fault with Stuck Breaker on HOLT.CO3 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_320 | Single Phase Fault with Stuck Breaker on HOLT.CO3 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_321 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_321 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_322 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_322 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_323 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_323 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_324 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_324 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_325 | Single Phase Fault with Stuck Breaker on G18-043-TAP (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_325 | Single Phase Fault with Stuck Breaker on G18-043-TAP (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_326 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_326 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_327 | Single Phase Fault with Stuck Breaker on CREITON8 (640150) 69 kV Bus a. Apply Fault at the CREITON8 (640150) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON8 (640150) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_327 | Single Phase Fault with Stuck Breaker on CREITON8 (640150) 69 kV Bus a. Apply Fault at the CREITON8 (640150) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON8 (640150) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_328 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_328 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_329 | Single Phase Fault with Stuck Breaker on HOSKINS7 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_329 | Single Phase Fault with Stuck Breaker on HOSKINS7 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_330 | Single Phase Fault with Stuck Breaker on NELIGH 8 (640294) 69 kV Bus a. Apply Fault at the NELIGH 8 (640294) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 8 (640294) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_330 | Single Phase Fault with Stuck Breaker on NELIGH 8 (640294) 69 kV Bus a. Apply Fault at the NELIGH 8 (640294) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 8 (640294) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_331 | Single Phase Fault with Stuck Breaker on PAULINE7 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_331 | Single Phase Fault with Stuck Breaker on PAULINE7 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_332 | Single Phase Fault with Stuck Breaker on SHELCRK4 (640343) 230 kV Bus a. Apply Fault at the SHELCRK4 (640343) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK4 (640343) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_332 | Single Phase Fault with Stuck Breaker on SHELCRK4 (640343) 230 kV Bus a. Apply Fault at the SHELCRK4 (640343) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK4 (640343) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_333 | Single Phase Fault with Stuck Breaker on THEDFRD7 (640381) 115 kV Bus a. Apply Fault at the THEDFRD7 (640381) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_333 | Single Phase Fault with Stuck Breaker on THEDFRD7 (640381) 115 kV Bus a. Apply Fault at the THEDFRD7 (640381) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_334 | Single Phase Fault with Stuck Breaker on ANTELOPE 8 (640522) 69 kV Bus a. Apply Fault at the ANTELOPE 8 (640522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 8 (640522) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_334 | Single Phase Fault with Stuck Breaker on ANTELOPE 8 (640522) 69 kV Bus a. Apply Fault at the ANTELOPE 8 (640522) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 8 (640522) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_335 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_335 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_336 | Single Phase Fault with Stuck Breaker on WAGENER 7 (650285) 115 kV Bus a. Apply Fault at the WAGENER 7 (650285) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_336 | Single Phase Fault with Stuck Breaker on WAGENER 7 (650285) 115 kV Bus a. Apply Fault at the WAGENER 7 (650285) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_337 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_337 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_338 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_338 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_339 | Single Phase Fault with Stuck Breaker on REMSEN 3 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REMSEN 3 (635398) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_339 | Single Phase Fault with Stuck Breaker on REMSEN 3 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REMSEN 3 (635398) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_340 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_340 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_341 | Single Phase Fault with Stuck Breaker on GEN-2017-144 (760767) 345 kV Bus a. Apply Fault at the GEN-2017-144 (760767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-144 (760767) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_341 | Single Phase Fault with Stuck Breaker on GEN-2017-144 (760767) 345 kV Bus a. Apply Fault at the GEN-2017-144 (760767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-144 (760767) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_342 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_342 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_343 | Single Phase Fault with Stuck Breaker on GEN-2018-025 (762603) 345 kV Bus a. Apply Fault at the GEN-2018-025 (762603) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-025 (762603) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_343 | Single Phase Fault with Stuck Breaker on GEN-2018-025 (762603) 345 kV Bus a. Apply Fault at the GEN-2018-025 (762603) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-025 (762603) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_344 | Single Phase Fault with Stuck Breaker on GEN-2018-044 (762790) 345 kV Bus a. Apply Fault at the GEN-2018-044 (762790) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-044 (762790) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_344 | Single Phase Fault with Stuck Breaker on GEN-2018-044 (762790) 345 kV Bus a. Apply Fault at the GEN-2018-044 (762790) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-044 (762790) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_345 | Single Phase Fault with Stuck Breaker on GEN-2018-033 (762691) 345 kV Bus a. Apply Fault at the GEN-2018-033 (762691) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-033 (762691) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_345 | Single Phase Fault with Stuck Breaker on GEN-2018-033 (762691) 345 kV Bus a. Apply Fault at the GEN-2018-033 (762691) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-033 (762691) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_346 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_346 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_347 | Single Phase Fault with Stuck Breaker on GEN-2018-043 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-043 (762780) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_347 | Single Phase Fault with Stuck Breaker on GEN-2018-043 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-043 (762780) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_348 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_348 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_349 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_349 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_350 | Single Phase Fault with Stuck Breaker on CREITON7 (640149) 115 kV Bus a. Apply Fault at the CREITON7 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_350 | Single Phase Fault with Stuck Breaker on CREITON7 (640149) 115 kV Bus a. Apply Fault at the CREITON7 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_351 | Single Phase Fault with Stuck Breaker on NELIGH 7 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_351 | Single Phase Fault with Stuck Breaker on NELIGH 7 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_352 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_352 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_353 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_353 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_354 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_354 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_355 | Single Phase Fault with Stuck Breaker on S1254 5 (646254) 161 kV Bus a. Apply Fault at the S1254 5 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_355 | Single Phase Fault with Stuck Breaker on S1254 5 (646254) 161 kV Bus a. Apply Fault at the S1254 5 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_356 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_356 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_357 | Single Phase Fault with Stuck Breaker on SIOUXCY2 (652552) 230 kV Bus a. Apply Fault at the SIOUXCY2 (652552) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_357 | Single Phase Fault with Stuck Breaker on SIOUXCY2 (652552) 230 kV Bus a. Apply Fault at the SIOUXCY2 (652552) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_358 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_358 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_359 | Single Phase Fault with Stuck Breaker on SIOUXCY4 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_359 | Single Phase Fault with Stuck Breaker on SIOUXCY4 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_360 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_360 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_361 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_361 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_362 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_362 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_363 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_363 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_364 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_364 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_365 | Single Phase Fault with Stuck Breaker on KEYSTON3 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_365 | Single Phase Fault with Stuck Breaker on KEYSTON3 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_366 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_366 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_367 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_367 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_368 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_368 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_369 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_369 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_370 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_370 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_371 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_371 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_372 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_372 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_373 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_373 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_374 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_374 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_375 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_375 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_376 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_376 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_377 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_377 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_378 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_378 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_379 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_379 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_380 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_380 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_381 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_381 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_382 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_382 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_383 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_383 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_384 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_384 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_385 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_385 | Single Phase Fault with Stuck Breaker on UTICAJC4 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_386 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_386 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_387 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_387 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_388 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_388 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_389 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_389 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_390 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_390 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_391 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_391 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_392 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_392 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_393 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_393 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_394 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_394 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_395 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_395 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_396 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_396 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_397 | Single Phase Fault with Stuck Breaker on FTRANDL7 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_397 | Single Phase Fault with Stuck Breaker on FTRANDL7 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_398 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_398 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_399 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_399 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on AIRPORT 5 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on AIRPORT 5 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_400 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_400 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_401 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_401 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_402 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_402 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_403 | Single Phase Fault with Stuck Breaker on RLHILLS3 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_403 | Single Phase Fault with Stuck Breaker on RLHILLS3 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_404 | Single Phase Fault with Stuck Breaker on RLHILLS3 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_404 | Single Phase Fault with Stuck Breaker on RLHILLS3 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_405 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_405 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_406 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_406 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_407 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_407 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_408 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_408 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_409 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_409 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_410 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_410 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_411 | Single Phase Fault with Stuck Breaker on FALLOW 3 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_411 | Single Phase Fault with Stuck Breaker on FALLOW 3 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_412 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_412 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_413 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_413 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_414 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_414 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_415 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_415 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_416 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_416 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_417 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_417 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_418 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_418 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_419 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_419 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on FTTHOMP4 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_420 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_420 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_421 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_421 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_422 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_422 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_423 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_423 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_424 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_424 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_425 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_425 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_426 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_426 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_427 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_427 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_428 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_428 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_429 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_429 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_430 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_430 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_431 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_431 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on BELDEN 7 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on BELDEN 7 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on CREITON7 (640149) 115 kV Bus a. Apply Fault at the CREITON7 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on CREITON7 (640149) 115 kV Bus a. Apply Fault at the CREITON7 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on MINDEN 7 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on MINDEN 7 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on NELIGH 7 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on NELIGH 7 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on MANAWA 5 (635010) 161 kV Bus a. Apply Fault at the MANAWA 5 (635010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on MANAWA 5 (635010) 161 kV Bus a. Apply Fault at the MANAWA 5 (635010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on NORFOLK7 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on NORFOLK7 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on NORFK.N7 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on NORFK.N7 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on STNTN.N7 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on STNTN.N7 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.6. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.7. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.8. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.10. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.14. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.15. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.16. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.18. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 b.22. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.23. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.24. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.25. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.28. KEARNEY7 (640250) 115.0 kV (Trip Shunt Device) b.29. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.30. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.31. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.32. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.37. HOLDREG7 (640224) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.6. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.7. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.8. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.10. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.14. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.15. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.16. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.18. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 b.22. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.23. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.24. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.25. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.28. KEARNEY7 (640250) 115.0 kV (Trip Shunt Device) b.29. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.30. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.31. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.32. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.37. HOLDREG7 (640224) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on HOSKINS7 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on HOSKINS7 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on KEARNEY7 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.8. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.9. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.10. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.11. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.12. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.13. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.14. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.15. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.16. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.17. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.18. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.19. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.20. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.21. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.22. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.25. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.26. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on KEARNEY7 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.8. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.9. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.10. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.11. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.12. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.13. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.14. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.15. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.16. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.17. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.18. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.19. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.20. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.21. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.22. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.25. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.26. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.4. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.5. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.6. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.7. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.8. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.9. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.10. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.11. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.12. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.4. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.5. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.6. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.7. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.8. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.9. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.10. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.11. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.12. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 b.6. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.7. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.8. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.9. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.12. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.13. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 b.16. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 b.6. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.7. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.8. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.9. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.12. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.13. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 b.16. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on S1256 5 (646256) 161 kV Bus a. Apply Fault at the S1256 5 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on S1256 5 (646256) 161 kV Bus a. Apply Fault at the S1256 5 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on S1254 5 (646254) 161 kV Bus a. Apply Fault at the S1254 5 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on S1254 5 (646254) 161 kV Bus a. Apply Fault at the S1254 5 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_65 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_65 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_66 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_66 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_67 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_67 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_68 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_68 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_69 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_69 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_7 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_7 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_70 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_70 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_71 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_71 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_72 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_72 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_73 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_73 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_74 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_74 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_75 | Single Phase Fault with Stuck Breaker on S3761 3 (645761) 345 kV Bus a. Apply Fault at the S3761 3 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_75 | Single Phase Fault with Stuck Breaker on S3761 3 (645761) 345 kV Bus a. Apply Fault at the S3761 3 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_76 | Single Phase Fault with Stuck Breaker on S1201 5 (646201) 161 kV Bus a. Apply Fault at the S1201 5 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_76 | Single Phase Fault with Stuck Breaker on S1201 5 (646201) 161 kV Bus a. Apply Fault at the S1201 5 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_77 | Single Phase Fault with Stuck Breaker on S1201 5 (646201) 161 kV Bus a. Apply Fault at the S1201 5 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_77 | Single Phase Fault with Stuck Breaker on S1201 5 (646201) 161 kV Bus a. Apply Fault at the S1201 5 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_78 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_78 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_79 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_8 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_8 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 b.4. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_80 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 b.4. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_81 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_82 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_82 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_83 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_83 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_84 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_84 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_85 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_85 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_86 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_86 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_87 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.7. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.8. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_87 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.7. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.8. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_88 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_88 | Single Phase Fault with Stuck Breaker on S1250 5 (646250) 161 kV Bus a. Apply Fault at the S1250 5 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_89 | Single Phase Fault with Stuck Breaker on S1211 5 (646211) 161 kV Bus a. Apply Fault at the S1211 5 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.5. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.6. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.7. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.8. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.9. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.10. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.11. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 b.12. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.13. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.14. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.16. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.17. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_89 | Single Phase Fault with Stuck Breaker on S1211 5 (646211) 161 kV Bus a. Apply Fault at the S1211 5 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.5. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.6. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.7. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.8. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.9. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.10. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.11. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 b.12. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.13. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.14. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.16. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.17. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_9 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_9 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_90 | Single Phase Fault with Stuck Breaker on S1220 5 (646220) 161 kV Bus a. Apply Fault at the S1220 5 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_90 | Single Phase Fault with Stuck Breaker on S1220 5 (646220) 161 kV Bus a. Apply Fault at the S1220 5 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_91 | Single Phase Fault with Stuck Breaker on S1221 5 (646221) 161 kV Bus a. Apply Fault at the S1221 5 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_91 | Single Phase Fault with Stuck Breaker on S1221 5 (646221) 161 kV Bus a. Apply Fault at the S1221 5 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_92 | Single Phase Fault with Stuck Breaker on S1222 5 (646222) 161 kV Bus a. Apply Fault at the S1222 5 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_92 | Single Phase Fault with Stuck Breaker on S1222 5 (646222) 161 kV Bus a. Apply Fault at the S1222 5 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_93 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_93 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_94 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_94 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_95 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_95 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_96 | Single Phase Fault with Stuck Breaker on S1227 5 (646227) 161 kV Bus a. Apply Fault at the S1227 5 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_96 | Single Phase Fault with Stuck Breaker on S1227 5 (646227) 161 kV Bus a. Apply Fault at the S1227 5 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_97 | Single Phase Fault with Stuck Breaker on S1229 5 (646229) 161 kV Bus a. Apply Fault at the S1229 5 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_97 | Single Phase Fault with Stuck Breaker on S1229 5 (646229) 161 kV Bus a. Apply Fault at the S1229 5 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_98 | Single Phase Fault with Stuck Breaker on S1231 5 (646231) 161 kV Bus a. Apply Fault at the S1231 5 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_98 | Single Phase Fault with Stuck Breaker on S1231 5 (646231) 161 kV Bus a. Apply Fault at the S1231 5 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_P4_FAULT_99 | Single Phase Fault with Stuck Breaker on S1231 5 (646231) 161 kV Bus a. Apply Fault at the S1231 5 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_P4_FAULT_99 | Single Phase Fault with Stuck Breaker on S1231 5 (646231) 161 kV Bus a. Apply Fault at the S1231 5 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1 | 3 Phase fault on CJ 366 5 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1 | 3 Phase fault on CJ 366 5 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_10 | 3 Phase fault on CANEYRV7 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_10 | 3 Phase fault on CANEYRV7 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_100 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_100 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1000 | 3 Phase fault on LAMAR7 (599950) 345 kV Bus a. Apply fault at the LAMAR7 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1000 | 3 Phase fault on LAMAR7 (599950) 345 kV Bus a. Apply fault at the LAMAR7 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1001 | 3 Phase fault on HILLS-DT-RX3 (636399) 345 kV Bus a. Apply fault at the HILLS-DT-RX3 (636399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS-DT-RX3 (636399) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1001 | 3 Phase fault on HILLS-DT-RX3 (636399) 345 kV Bus a. Apply fault at the HILLS-DT-RX3 (636399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS-DT-RX3 (636399) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1002 | 3 Phase fault on GEN-2018-058 (762937) 345 kV Bus a. Apply fault at the GEN-2018-058 (762937) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-058 (762937) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1002 | 3 Phase fault on GEN-2018-058 (762937) 345 kV Bus a. Apply fault at the GEN-2018-058 (762937) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-058 (762937) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1003 | 3 Phase fault on HILLS-DT-RX3 (636399) 345 kV Bus a. Apply fault at the HILLS-DT-RX3 (636399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS 3 (636400) 345.0 kV Switched Shunt Device #1 b.2. HILLS-DT-RX3 (636399) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #z b.3. DIAMOND TRL3 (635740) 345.0 kV to HILLS-DT-RX3 (636399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1003 | 3 Phase fault on HILLS-DT-RX3 (636399) 345 kV Bus a. Apply fault at the HILLS-DT-RX3 (636399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS 3 (636400) 345.0 kV Switched Shunt Device #1 b.2. HILLS-DT-RX3 (636399) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #z b.3. DIAMOND TRL3 (635740) 345.0 kV to HILLS-DT-RX3 (636399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1004 | 3 Phase fault on MNTZUMA3 (635730) 345 kV Bus a. Apply fault at the MNTZUMA3 (635730) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNTZUMA3 (635730) 345.0 kV to DIAMOND TRL3 (635740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1004 | 3 Phase fault on MNTZUMA3 (635730) 345 kV Bus a. Apply fault at the MNTZUMA3 (635730) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNTZUMA3 (635730) 345.0 kV to DIAMOND TRL3 (635740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1005 | 3 Phase fault on NEPARSN4 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1005 | 3 Phase fault on NEPARSN4 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1006 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1006 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1007 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1007 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1008 | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1008 | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1009 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1009 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_101 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_101 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1010 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1010 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1011 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1011 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1012 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1012 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1013 | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1013 | 3 Phase fault on WAVERLY7 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1014 | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1014 | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1015 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1015 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1016 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1016 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1017 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1017 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1018 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1018 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1019 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1019 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_102 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_102 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1020 | 3 Phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1020 | 3 Phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1021 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1021 | 3 Phase fault on AXTELL 3 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1022 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1022 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1023 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1023 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1024 | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1024 | 3 Phase fault on REDWILO3 (640325) 345 kV Bus a. Apply fault at the REDWILO3 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1025 | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1025 | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1026 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1026 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1027 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1027 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1028 | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1028 | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1029 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1029 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_103 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_103 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1030 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1030 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1031 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1031 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1032 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1032 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1033 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1033 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1034 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1034 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1035 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1035 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1036 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1036 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1037 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1037 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1038 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1038 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1039 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1039 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_104 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_104 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_1040 | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_1040 | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_105 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_105 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_106 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_106 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_107 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_107 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_108 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_108 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_109 | 3 Phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_109 | 3 Phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_11 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_11 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_110 | 3 Phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_110 | 3 Phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_111 | 3 Phase fault on 5MAURER 2 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_111 | 3 Phase fault on 5MAURER 2 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_112 | 3 Phase fault on 5ADAIR2 (344001) 161 kV Bus a. Apply fault at the 5ADAIR2 (344001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_112 | 3 Phase fault on 5ADAIR2 (344001) 161 kV Bus a. Apply fault at the 5ADAIR2 (344001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_113 | 3 Phase fault on 5CALIF UE 1 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_113 | 3 Phase fault on 5CALIF UE 1 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_114 | 3 Phase fault on 5MOBERLY (345221) 161 kV Bus a. Apply fault at the 5MOBERLY (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_114 | 3 Phase fault on 5MOBERLY (345221) 161 kV Bus a. Apply fault at the 5MOBERLY (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_115 | 3 Phase fault on 5MOBERLY (345221) 161 kV Bus a. Apply fault at the 5MOBERLY (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_115 | 3 Phase fault on 5MOBERLY (345221) 161 kV Bus a. Apply fault at the 5MOBERLY (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_116 | 3 Phase fault on 7CALAWY 1 (344224) 345 kV Bus a. Apply fault at the 7CALAWY 1 (344224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7CALAWY 1 (344224) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_116 | 3 Phase fault on 7CALAWY 1 (344224) 345 kV Bus a. Apply fault at the 7CALAWY 1 (344224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7CALAWY 1 (344224) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_117 | 3 Phase fault on 7CALAWY 1 (344224) 345 kV Bus a. Apply fault at the 7CALAWY 1 (344224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7CALAWY 1 (344224) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_117 | 3 Phase fault on 7CALAWY 1 (344224) 345 kV Bus a. Apply fault at the 7CALAWY 1 (344224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7CALAWY 1 (344224) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_118 | 3 Phase fault on 7BELLEAU (344102) 345 kV Bus a. Apply fault at the 7BELLEAU (344102) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BELLEAU (344102) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_118 | 3 Phase fault on 7BELLEAU (344102) 345 kV Bus a. Apply fault at the 7BELLEAU (344102) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BELLEAU (344102) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_119 | 3 Phase fault on 5HUNTSDL (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_119 | 3 Phase fault on 5HUNTSDL (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_12 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_12 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_120 | 3 Phase fault on 5ADAIR3 (344006) 161 kV Bus a. Apply fault at the 5ADAIR3 (344006) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #z b.3. 5ADAIR3 (344006) 161.0 kV to 5ZACHARY (344010) 161.0 kV Transmission Circuit #1 b.4. 2ADAIR 2 (346006) 69.0 kV to 5ADAIR3 (344006) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_120 | 3 Phase fault on 5ADAIR3 (344006) 161 kV Bus a. Apply fault at the 5ADAIR3 (344006) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #z b.3. 5ADAIR3 (344006) 161.0 kV to 5ZACHARY (344010) 161.0 kV Transmission Circuit #1 b.4. 2ADAIR 2 (346006) 69.0 kV to 5ADAIR3 (344006) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_121 | 3 Phase fault on 5ADAIR1 (344004) 161 kV Bus a. Apply fault at the 5ADAIR1 (344004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_121 | 3 Phase fault on 5ADAIR1 (344004) 161 kV Bus a. Apply fault at the 5ADAIR1 (344004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_122 | 3 Phase fault on 7OVERTON (345408) 345 kV Bus a. Apply fault at the 7OVERTON (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_122 | 3 Phase fault on 7OVERTON (345408) 345 kV Bus a. Apply fault at the 7OVERTON (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_123 | 3 Phase fault on 7MAYWOOD (345435) 345 kV Bus a. Apply fault at the 7MAYWOOD (345435) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MAYWOOD (345435) 345.0 kV to 7HERLEMAN (347010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_123 | 3 Phase fault on 7MAYWOOD (345435) 345 kV Bus a. Apply fault at the 7MAYWOOD (345435) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MAYWOOD (345435) 345.0 kV to 7HERLEMAN (347010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_124 | 3 Phase fault on 5MAURER 2 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_124 | 3 Phase fault on 5MAURER 2 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_125 | 3 Phase fault on 5OVERTON 2 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_125 | 3 Phase fault on 5OVERTON 2 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_126 | 3 Phase fault on 7BELLEAU (344102) 345 kV Bus a. Apply fault at the 7BELLEAU (344102) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_126 | 3 Phase fault on 7BELLEAU (344102) 345 kV Bus a. Apply fault at the 7BELLEAU (344102) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_127 | 3 Phase fault on 7MONTGMRY (345230) 345 kV Bus a. Apply fault at the 7MONTGMRY (345230) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MONTGMRY (345230) 345.0 kV to 5MONTGMRY 1 (345231) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_127 | 3 Phase fault on 7MONTGMRY (345230) 345 kV Bus a. Apply fault at the 7MONTGMRY (345230) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MONTGMRY (345230) 345.0 kV to 5MONTGMRY 1 (345231) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_128 | 3 Phase fault on 7OVERTON (345408) 345 kV Bus a. Apply fault at the 7OVERTON (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_128 | 3 Phase fault on 7OVERTON (345408) 345 kV Bus a. Apply fault at the 7OVERTON (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_129 | 3 Phase fault on 7ZACHARY (344000) 345 kV Bus a. Apply fault at the 7ZACHARY (344000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ZACHARY (344000) 345.0 kV to 5ZACHARY (344010) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_129 | 3 Phase fault on 7ZACHARY (344000) 345 kV Bus a. Apply fault at the 7ZACHARY (344000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ZACHARY (344000) 345.0 kV to 5ZACHARY (344010) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_13 | 3 Phase fault on JEC N 7 (532766) 345 kV Bus a. Apply fault at the JEC N 7 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_13 | 3 Phase fault on JEC N 7 (532766) 345 kV Bus a. Apply fault at the JEC N 7 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_130 | 3 Phase fault on 7SPENCER (345992) 345 kV Bus a. Apply fault at the 7SPENCER (345992) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPENCER (345992) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_130 | 3 Phase fault on 7SPENCER (345992) 345 kV Bus a. Apply fault at the 7SPENCER (345992) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPENCER (345992) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_131 | 3 Phase fault on TIFFIN 3 (636420) 345 kV Bus a. Apply fault at the TIFFIN 3 (636420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORGN VLLY 3 (631148) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.3. TIFFIN 5 (636421) 161.0 kV to TIFFIN 3 (636420) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_131 | 3 Phase fault on TIFFIN 3 (636420) 345 kV Bus a. Apply fault at the TIFFIN 3 (636420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORGN VLLY 3 (631148) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.3. TIFFIN 5 (636421) 161.0 kV to TIFFIN 3 (636420) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_132 | 3 Phase fault on HILLS 3 (636400) 345 kV Bus a. Apply fault at the HILLS 3 (636400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.3. HILLS 3 (636400) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_132 | 3 Phase fault on HILLS 3 (636400) 345 kV Bus a. Apply fault at the HILLS 3 (636400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.3. HILLS 3 (636400) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_133 | 3 Phase fault on HILLS 3 (636400) 345 kV Bus a. Apply fault at the HILLS 3 (636400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNTZUMA3 (635730) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_133 | 3 Phase fault on HILLS 3 (636400) 345 kV Bus a. Apply fault at the HILLS 3 (636400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNTZUMA3 (635730) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_134 | 3 Phase fault on SUB T HSK 3 (636645) 345 kV Bus a. Apply fault at the SUB T HSK 3 (636645) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MAYWOOD (345435) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. SUB T HSK 3 (636645) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_134 | 3 Phase fault on SUB T HSK 3 (636645) 345 kV Bus a. Apply fault at the SUB T HSK 3 (636645) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MAYWOOD (345435) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. SUB T HSK 3 (636645) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_135 | 3 Phase fault on SUB 92 3 (636630) 345 kV Bus a. Apply fault at the SUB 92 3 (636630) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.2. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.3. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_135 | 3 Phase fault on SUB 92 3 (636630) 345 kV Bus a. Apply fault at the SUB 92 3 (636630) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.2. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.3. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_136 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_136 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_137 | 3 Phase fault on APANOSE5 (631112) 161 kV Bus a. Apply fault at the APANOSE5 (631112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODY 5 (631110) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.2. APANOSE5 (631112) 161.0 kV to APANOSE8 (630033) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_137 | 3 Phase fault on APANOSE5 (631112) 161 kV Bus a. Apply fault at the APANOSE5 (631112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODY 5 (631110) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.2. APANOSE5 (631112) 161.0 kV to APANOSE8 (630033) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_138 | 3 Phase fault on 5HUNTSDL (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_138 | 3 Phase fault on 5HUNTSDL (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_139 | 3 Phase fault on JOHNSON3 (631208) 345 kV Bus a. Apply fault at the JOHNSON3 (631208) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNSON3 (631208) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_139 | 3 Phase fault on JOHNSON3 (631208) 345 kV Bus a. Apply fault at the JOHNSON3 (631208) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNSON3 (631208) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_14 | 3 Phase fault on GEARY 7 (532767) 345 kV Bus a. Apply fault at the GEARY 7 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_14 | 3 Phase fault on GEARY 7 (532767) 345 kV Bus a. Apply fault at the GEARY 7 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_140 | 3 Phase fault on JOHNSON3 (631208) 345 kV Bus a. Apply fault at the JOHNSON3 (631208) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNSON3 (631208) 345.0 kV to JOHNSON5 (631093) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_140 | 3 Phase fault on JOHNSON3 (631208) 345 kV Bus a. Apply fault at the JOHNSON3 (631208) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNSON3 (631208) 345.0 kV to JOHNSON5 (631093) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_141 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_141 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_142 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_142 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_143 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_143 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_144 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_144 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_145 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_145 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_146 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_146 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_147 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_147 | 3 Phase fault on CBLUFFS3 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_148 | 3 Phase fault on HILLS 3 (636400) 345 kV Bus a. Apply fault at the HILLS 3 (636400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS 3 (636400) 345.0 kV to HILLS 5 (636401) 161.0 kV to HILL1XT9 (636406) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_148 | 3 Phase fault on HILLS 3 (636400) 345 kV Bus a. Apply fault at the HILLS 3 (636400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS 3 (636400) 345.0 kV to HILLS 5 (636401) 161.0 kV to HILL1XT9 (636406) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_149 | 3 Phase fault on WINDSR 5 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_149 | 3 Phase fault on WINDSR 5 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_15 | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_15 | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_150 | 3 Phase fault on HARRIS (541313) 161 kV Bus a. Apply fault at the HARRIS (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_150 | 3 Phase fault on HARRIS (541313) 161 kV Bus a. Apply fault at the HARRIS (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_151 | 3 Phase fault on LEESUM 5 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_151 | 3 Phase fault on LEESUM 5 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_152 | 3 Phase fault on STROTHR5 (541246) 161 kV Bus a. Apply fault at the STROTHR5 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_152 | 3 Phase fault on STROTHR5 (541246) 161 kV Bus a. Apply fault at the STROTHR5 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_153 | 3 Phase fault on LKWINBG5 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_153 | 3 Phase fault on LKWINBG5 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_154 | 3 Phase fault on RICHMND5 (541236) 161 kV Bus a. Apply fault at the RICHMND5 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_154 | 3 Phase fault on RICHMND5 (541236) 161 kV Bus a. Apply fault at the RICHMND5 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_155 | 3 Phase fault on LKWOOD 5 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_155 | 3 Phase fault on LKWOOD 5 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_156 | 3 Phase fault on NCONGRS5 (541318) 161 kV Bus a. Apply fault at the NCONGRS5 (541318) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_156 | 3 Phase fault on NCONGRS5 (541318) 161 kV Bus a. Apply fault at the NCONGRS5 (541318) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_157 | 3 Phase fault on WINJT N5 (543009) 161 kV Bus a. Apply fault at the WINJT N5 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_157 | 3 Phase fault on WINJT N5 (543009) 161 kV Bus a. Apply fault at the WINJT N5 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_158 | 3 Phase fault on GRAND W5 (542988) 161 kV Bus a. Apply fault at the GRAND W5 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_158 | 3 Phase fault on GRAND W5 (542988) 161 kV Bus a. Apply fault at the GRAND W5 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_159 | 3 Phase fault on NAVY 5 (542989) 161 kV Bus a. Apply fault at the NAVY 5 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_159 | 3 Phase fault on NAVY 5 (542989) 161 kV Bus a. Apply fault at the NAVY 5 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_16 | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_16 | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_160 | 3 Phase fault on BRUNSWK5 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_160 | 3 Phase fault on BRUNSWK5 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_161 | 3 Phase fault on BUCYRUS5 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_161 | 3 Phase fault on BUCYRUS5 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_162 | 3 Phase fault on SHAWNEE5 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_162 | 3 Phase fault on SHAWNEE5 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_163 | 3 Phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_163 | 3 Phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_164 | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_164 | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_165 | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_165 | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_166 | 3 Phase fault on S3458 3 (645458) 345 kV Bus a. Apply fault at the S3458 3 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_166 | 3 Phase fault on S3458 3 (645458) 345 kV Bus a. Apply fault at the S3458 3 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_167 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_167 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_168 | 3 Phase fault on RIVRSID5 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_168 | 3 Phase fault on RIVRSID5 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_169 | 3 Phase fault on RANDLPH5 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_169 | 3 Phase fault on RANDLPH5 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_17 | 3 Phase fault on JEC N 7 (532766) 345 kV Bus a. Apply fault at the JEC N 7 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_17 | 3 Phase fault on JEC N 7 (532766) 345 kV Bus a. Apply fault at the JEC N 7 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_170 | 3 Phase fault on MARTCIT5 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_170 | 3 Phase fault on MARTCIT5 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_171 | 3 Phase fault on SIB REA1 (541414) 345 kV Bus a. Apply fault at the SIB REA1 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_171 | 3 Phase fault on SIB REA1 (541414) 345 kV Bus a. Apply fault at the SIB REA1 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_172 | 3 Phase fault on MC REAC3 (541413) 345 kV Bus a. Apply fault at the MC REAC3 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) High End of Sim Voltage (Near Faulted Bus) - VOLT 585241 [GEN-2015-088345.00] - VOLT 640525 [TOBIAS 3345.00] - VOLT 761292 [GEN-2017-181345.00] - VOLT 761313 [GEN-2017-182345.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_172 | 3 Phase fault on MC REAC3 (541413) 345 kV Bus a. Apply fault at the MC REAC3 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) High End of Sim Voltage (Near Faulted Bus) - VOLT 585241 [GEN-2015-088345.00] - VOLT 640525 [TOBIAS 3345.00] - VOLT 761292 [GEN-2017-181345.00] - VOLT 761313 [GEN-2017-182345.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_173 | 3 Phase fault on MC REAC2 (541412) 345 kV Bus a. Apply fault at the MC REAC2 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) High End of Sim Voltage (Near Faulted Bus) - VOLT 585241 [GEN-2015-088345.00] - VOLT 640525 [TOBIAS 3345.00] - VOLT 761292 [GEN-2017-181345.00] - VOLT 761313 [GEN-2017-182345.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_173 | 3 Phase fault on MC REAC2 (541412) 345 kV Bus a. Apply fault at the MC REAC2 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) High End of Sim Voltage (Near Faulted Bus) - VOLT 585241 [GEN-2015-088345.00] - VOLT 640525 [TOBIAS 3345.00] - VOLT 761292 [GEN-2017-181345.00] - VOLT 761313 [GEN-2017-182345.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_174 | 3 Phase fault on CONWAY (539009) 138 kV Bus a. Apply fault at the CONWAY (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_174 | 3 Phase fault on CONWAY (539009) 138 kV Bus a. Apply fault at the CONWAY (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_175 | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_175 | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_176 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_176 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_177 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_177 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_178 | 3 Phase fault on JARBALO3 (533244) 115 kV Bus a. Apply fault at the JARBALO3 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_178 | 3 Phase fault on JARBALO3 (533244) 115 kV Bus a. Apply fault at the JARBALO3 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_179 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_179 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_18 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_18 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_180 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_180 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_181 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_181 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_182 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_182 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_183 | 3 Phase fault on 12&CLAY3 (533184) 115 kV Bus a. Apply fault at the 12&CLAY3 (533184) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 12&CLAY3 (533184) 115.0 kV to 4VAN S 3 (533200) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_183 | 3 Phase fault on 12&CLAY3 (533184) 115 kV Bus a. Apply fault at the 12&CLAY3 (533184) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 12&CLAY3 (533184) 115.0 kV to 4VAN S 3 (533200) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_184 | 3 Phase fault on 41CALIF3 (533160) 115 kV Bus a. Apply fault at the 41CALIF3 (533160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_184 | 3 Phase fault on 41CALIF3 (533160) 115 kV Bus a. Apply fault at the 41CALIF3 (533160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_185 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_185 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_186 | 3 Phase fault on AMELIA 3 (533215) 115 kV Bus a. Apply fault at the AMELIA 3 (533215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMELIA 3 (533215) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_186 | 3 Phase fault on AMELIA 3 (533215) 115 kV Bus a. Apply fault at the AMELIA 3 (533215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMELIA 3 (533215) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_187 | 3 Phase fault on ENEMAHA3 (533210) 115 kV Bus a. Apply fault at the ENEMAHA3 (533210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENEMAHA3 (533210) 115.0 kV to KNGFISH3 (533212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_187 | 3 Phase fault on ENEMAHA3 (533210) 115 kV Bus a. Apply fault at the ENEMAHA3 (533210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENEMAHA3 (533210) 115.0 kV to KNGFISH3 (533212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_188 | 3 Phase fault on CORONAD3 (533394) 115 kV Bus a. Apply fault at the CORONAD3 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_188 | 3 Phase fault on CORONAD3 (533394) 115 kV Bus a. Apply fault at the CORONAD3 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_189 | 3 Phase fault on ENEMAHA3 (533210) 115 kV Bus a. Apply fault at the ENEMAHA3 (533210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENEMAHA3 (533210) 115.0 kV to KELLY 3 (533217) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_189 | 3 Phase fault on ENEMAHA3 (533210) 115 kV Bus a. Apply fault at the ENEMAHA3 (533210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENEMAHA3 (533210) 115.0 kV to KELLY 3 (533217) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_19 | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_19 | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_190 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_190 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_191 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_191 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_192 | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_192 | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_193 | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_193 | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_194 | 3 Phase fault on COMOTAR4 (533037) 138 kV Bus a. Apply fault at the COMOTAR4 (533037) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_194 | 3 Phase fault on COMOTAR4 (533037) 138 kV Bus a. Apply fault at the COMOTAR4 (533037) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_195 | 3 Phase fault on INTERST4 (533051) 138 kV Bus a. Apply fault at the INTERST4 (533051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_195 | 3 Phase fault on INTERST4 (533051) 138 kV Bus a. Apply fault at the INTERST4 (533051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_196 | 3 Phase fault on 43LORAN (533440) 115 kV Bus a. Apply fault at the 43LORAN (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_196 | 3 Phase fault on 43LORAN (533440) 115 kV Bus a. Apply fault at the 43LORAN (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_197 | 3 Phase fault on COWSKIN2 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_197 | 3 Phase fault on COWSKIN2 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_198 | 3 Phase fault on DEARING4 (533002) 138 kV Bus a. Apply fault at the DEARING4 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 b.5. DEARING1 (533089) 13.2 kV to DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_198 | 3 Phase fault on DEARING4 (533002) 138 kV Bus a. Apply fault at the DEARING4 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 b.5. DEARING1 (533089) 13.2 kV to DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_199 | 3 Phase fault on LIBERTY4 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.4. LIBERTY1 (533090) 13.2 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_199 | 3 Phase fault on LIBERTY4 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.4. LIBERTY1 (533090) 13.2 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_2 | 3 Phase fault on OAK432 5 (547494) 161 kV Bus a. Apply fault at the OAK432 5 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_2 | 3 Phase fault on OAK432 5 (547494) 161 kV Bus a. Apply fault at the OAK432 5 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_20 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_20 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_200 | 3 Phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_200 | 3 Phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_201 | 3 Phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_201 | 3 Phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_202 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_202 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_203 | 3 Phase fault on BYRONTP4 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.2. CHRKCTY4 (520431) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.3. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. BYRONTP4 (520432) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.5. BYRONTP4 (520432) 138.0 kV to BYRON 4 (520477) 138.0 kV Transmission Circuit #1 b.6. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.7. SANDYCR4 (520433) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.8. SANDYCR4 (520433) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.9. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_203 | 3 Phase fault on BYRONTP4 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.2. CHRKCTY4 (520431) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.3. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. BYRONTP4 (520432) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.5. BYRONTP4 (520432) 138.0 kV to BYRON 4 (520477) 138.0 kV Transmission Circuit #1 b.6. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.7. SANDYCR4 (520433) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.8. SANDYCR4 (520433) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.9. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_204 | 3 Phase fault on TONECE7 (512750) 345 kV Bus a. Apply fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_204 | 3 Phase fault on TONECE7 (512750) 345 kV Bus a. Apply fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_205 | 3 Phase fault on LACKMAN5 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_205 | 3 Phase fault on LACKMAN5 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_206 | 3 Phase fault on MISNJCT5 (543076) 161 kV Bus a. Apply fault at the MISNJCT5 (543076) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to MISNJCT5 (543076) 161.0 kV Transmission Circuit #1 b.2. SPRINT15 (543074) 161.0 kV to MISNJCT5 (543076) 161.0 kV Transmission Circuit #1 b.3. MISNJCT5 (543076) 161.0 kV to INDIAN_CK_5 (543127) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_206 | 3 Phase fault on MISNJCT5 (543076) 161 kV Bus a. Apply fault at the MISNJCT5 (543076) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to MISNJCT5 (543076) 161.0 kV Transmission Circuit #1 b.2. SPRINT15 (543074) 161.0 kV to MISNJCT5 (543076) 161.0 kV Transmission Circuit #1 b.3. MISNJCT5 (543076) 161.0 kV to INDIAN_CK_5 (543127) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_207 | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_207 | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_208 | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_208 | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_209 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_209 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_21 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_21 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_210 | 3 Phase fault on NWMAID5 (512757) 161 kV Bus a. Apply fault at the NWMAID5 (512757) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_210 | 3 Phase fault on NWMAID5 (512757) 161 kV Bus a. Apply fault at the NWMAID5 (512757) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_211 | 3 Phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_211 | 3 Phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_212 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_212 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_213 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_213 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_214 | 3 Phase fault on MIAMI 5 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_214 | 3 Phase fault on MIAMI 5 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_215 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_215 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_216 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_216 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_217 | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_217 | 3 Phase fault on DRYGULCH5 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_218 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_218 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_219 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_219 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_22 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_22 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_220 | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_220 | 3 Phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_221 | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_221 | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_222 | 3 Phase fault on FARML 4 (512734) 138 kV Bus a. Apply fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_222 | 3 Phase fault on FARML 4 (512734) 138 kV Bus a. Apply fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_223 | 3 Phase fault on GREC TAP5 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_223 | 3 Phase fault on GREC TAP5 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_224 | 3 Phase fault on LOCSTGVKM 5 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_224 | 3 Phase fault on LOCSTGVKM 5 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_225 | 3 Phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_225 | 3 Phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_226 | 3 Phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_226 | 3 Phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_227 | 3 Phase fault on FARML 4 (512734) 138 kV Bus a. Apply fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_227 | 3 Phase fault on FARML 4 (512734) 138 kV Bus a. Apply fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_228 | 3 Phase fault on FARML 4 (512734) 138 kV Bus a. Apply fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_228 | 3 Phase fault on FARML 4 (512734) 138 kV Bus a. Apply fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_229 | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_229 | 3 Phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_23 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_23 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_230 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_230 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_231 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_231 | 3 Phase fault on MAID 5 (512648) 161 kV Bus a. Apply fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_232 | 3 Phase fault on 5CLINTN (300071) 161 kV Bus a. Apply fault at the 5CLINTN (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_232 | 3 Phase fault on 5CLINTN (300071) 161 kV Bus a. Apply fault at the 5CLINTN (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_233 | 3 Phase fault on 5CLINTN (300071) 161 kV Bus a. Apply fault at the 5CLINTN (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_233 | 3 Phase fault on 5CLINTN (300071) 161 kV Bus a. Apply fault at the 5CLINTN (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_234 | 3 Phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_234 | 3 Phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_235 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_235 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_236 | 3 Phase fault on NEASTS_CAP5 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_236 | 3 Phase fault on NEASTS_CAP5 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_237 | 3 Phase fault on STHTOWN_CAP5 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_237 | 3 Phase fault on STHTOWN_CAP5 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_238 | 3 Phase fault on BARRY_CAP 5 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_238 | 3 Phase fault on BARRY_CAP 5 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_239 | 3 Phase fault on MERRIAM_CAP5 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_239 | 3 Phase fault on MERRIAM_CAP5 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_24 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_24 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_240 | 3 Phase fault on BYPASJT2 (543084) 69 kV Bus a. Apply fault at the BYPASJT2 (543084) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYJT2 (543079) 69.0 kV to BYPASJT2 (543084) 69.0 kV Transmission Circuit #1 b.2. BYPASJT2 (543084) 69.0 kV to IND WTR2 (543086) 69.0 kV Transmission Circuit #1 b.3. BYPASJT2 (543084) 69.0 kV to LIBRTYS2 (543095) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_240 | 3 Phase fault on BYPASJT2 (543084) 69 kV Bus a. Apply fault at the BYPASJT2 (543084) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYJT2 (543079) 69.0 kV to BYPASJT2 (543084) 69.0 kV Transmission Circuit #1 b.2. BYPASJT2 (543084) 69.0 kV to IND WTR2 (543086) 69.0 kV Transmission Circuit #1 b.3. BYPASJT2 (543084) 69.0 kV to LIBRTYS2 (543095) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_241 | 3 Phase fault on MILCKJT2 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_241 | 3 Phase fault on MILCKJT2 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_242 | 3 Phase fault on LANG 7 (532769) 345 kV Bus a. Apply fault at the LANG 7 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_242 | 3 Phase fault on LANG 7 (532769) 345 kV Bus a. Apply fault at the LANG 7 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_243 | 3 Phase fault on MIDLAND6 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_243 | 3 Phase fault on MIDLAND6 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_244 | 3 Phase fault on TECHILL6 (532857) 230 kV Bus a. Apply fault at the TECHILL6 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_244 | 3 Phase fault on TECHILL6 (532857) 230 kV Bus a. Apply fault at the TECHILL6 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_245 | 3 Phase fault on TAYLOR 4 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_245 | 3 Phase fault on TAYLOR 4 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_246 | 3 Phase fault on NEPARSN4 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_246 | 3 Phase fault on NEPARSN4 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_247 | 3 Phase fault on PARKCTY4 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_247 | 3 Phase fault on PARKCTY4 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_248 | 3 Phase fault on TALLGRS4 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_248 | 3 Phase fault on TALLGRS4 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_249 | 3 Phase fault on 45TH ST4 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_249 | 3 Phase fault on 45TH ST4 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_25 | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_25 | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_250 | 3 Phase fault on CENTENN4 (533034) 138 kV Bus a. Apply fault at the CENTENN4 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_250 | 3 Phase fault on CENTENN4 (533034) 138 kV Bus a. Apply fault at the CENTENN4 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_251 | 3 Phase fault on SCOFCTY4 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_251 | 3 Phase fault on SCOFCTY4 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_252 | 3 Phase fault on 59TH ST4 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_252 | 3 Phase fault on 59TH ST4 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_253 | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_253 | 3 Phase fault on LAKERDG4 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_254 | 3 Phase fault on BENTLEY4 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_254 | 3 Phase fault on BENTLEY4 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_255 | 3 Phase fault on TV1MNDV4 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_255 | 3 Phase fault on TV1MNDV4 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_256 | 3 Phase fault on ANDOVER4 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_256 | 3 Phase fault on ANDOVER4 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_257 | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_257 | 3 Phase fault on ANTHONY4 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_258 | 3 Phase fault on 29EVENG3 (533185) 115 kV Bus a. Apply fault at the 29EVENG3 (533185) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_258 | 3 Phase fault on 29EVENG3 (533185) 115 kV Bus a. Apply fault at the 29EVENG3 (533185) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_259 | 3 Phase fault on 27CROCO3 (533187) 115 kV Bus a. Apply fault at the 27CROCO3 (533187) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_259 | 3 Phase fault on 27CROCO3 (533187) 115 kV Bus a. Apply fault at the 27CROCO3 (533187) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_26 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_26 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_260 | 3 Phase fault on EUDORA 3 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.2. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_260 | 3 Phase fault on EUDORA 3 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.2. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_261 | 3 Phase fault on MNTCLLO3 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_261 | 3 Phase fault on MNTCLLO3 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_262 | 3 Phase fault on EABILEN3 (533365) 115 kV Bus a. Apply fault at the EABILEN3 (533365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_262 | 3 Phase fault on EABILEN3 (533365) 115 kV Bus a. Apply fault at the EABILEN3 (533365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_263 | 3 Phase fault on JCTCTY 3 (533330) 115 kV Bus a. Apply fault at the JCTCTY 3 (533330) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_263 | 3 Phase fault on JCTCTY 3 (533330) 115 kV Bus a. Apply fault at the JCTCTY 3 (533330) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_264 | 3 Phase fault on PARALEL3 (533218) 115 kV Bus a. Apply fault at the PARALEL3 (533218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_264 | 3 Phase fault on PARALEL3 (533218) 115 kV Bus a. Apply fault at the PARALEL3 (533218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_265 | 3 Phase fault on WJCCTYW3 (533344) 115 kV Bus a. Apply fault at the WJCCTYW3 (533344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_265 | 3 Phase fault on WJCCTYW3 (533344) 115 kV Bus a. Apply fault at the WJCCTYW3 (533344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_266 | 3 Phase fault on HUNTSVL3 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_266 | 3 Phase fault on HUNTSVL3 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_267 | 3 Phase fault on 54&MERI3 (533156) 115 kV Bus a. Apply fault at the 54&MERI3 (533156) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_267 | 3 Phase fault on 54&MERI3 (533156) 115 kV Bus a. Apply fault at the 54&MERI3 (533156) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_268 | 3 Phase fault on MUND 3 (533282) 115 kV Bus a. Apply fault at the MUND 3 (533282) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_268 | 3 Phase fault on MUND 3 (533282) 115 kV Bus a. Apply fault at the MUND 3 (533282) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_269 | 3 Phase fault on NTHLAND3 (533169) 115 kV Bus a. Apply fault at the NTHLAND3 (533169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.2. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_269 | 3 Phase fault on NTHLAND3 (533169) 115 kV Bus a. Apply fault at the NTHLAND3 (533169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.2. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_27 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_27 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_270 | 3 Phase fault on HTI JCT3 (533165) 115 kV Bus a. Apply fault at the HTI JCT3 (533165) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLVL3 (533152) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.2. CIRCLVL3 (533152) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HTI 3 (533164) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.5. KELLY 3 (533217) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_270 | 3 Phase fault on HTI JCT3 (533165) 115 kV Bus a. Apply fault at the HTI JCT3 (533165) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLVL3 (533152) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.2. CIRCLVL3 (533152) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HTI 3 (533164) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.5. KELLY 3 (533217) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_271 | 3 Phase fault on TONGATP3 (533219) 115 kV Bus a. Apply fault at the TONGATP3 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_271 | 3 Phase fault on TONGATP3 (533219) 115 kV Bus a. Apply fault at the TONGATP3 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_272 | 3 Phase fault on 166TH 3 (533233) 115 kV Bus a. Apply fault at the 166TH 3 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_272 | 3 Phase fault on 166TH 3 (533233) 115 kV Bus a. Apply fault at the 166TH 3 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_273 | 3 Phase fault on HALLMRK3 (533242) 115 kV Bus a. Apply fault at the HALLMRK3 (533242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_273 | 3 Phase fault on HALLMRK3 (533242) 115 kV Bus a. Apply fault at the HALLMRK3 (533242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_274 | 3 Phase fault on STULL T3 (533270) 115 kV Bus a. Apply fault at the STULL T3 (533270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.3. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.5. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_274 | 3 Phase fault on STULL T3 (533270) 115 kV Bus a. Apply fault at the STULL T3 (533270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.3. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.5. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_275 | 3 Phase fault on SMITTYV3 (533338) 115 kV Bus a. Apply fault at the SMITTYV3 (533338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHAL3 (533303) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 b.2. BAILEYV3 (533322) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.3. BAILEYV3 (533322) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_275 | 3 Phase fault on SMITTYV3 (533338) 115 kV Bus a. Apply fault at the SMITTYV3 (533338) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHAL3 (533303) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 b.2. BAILEYV3 (533322) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.3. BAILEYV3 (533322) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_276 | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_276 | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_277 | 3 Phase fault on WMBROSJ3 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_277 | 3 Phase fault on WMBROSJ3 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_278 | 3 Phase fault on NORTHST3 (533370) 115 kV Bus a. Apply fault at the NORTHST3 (533370) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #2 b.3. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.4. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_278 | 3 Phase fault on NORTHST3 (533370) 115 kV Bus a. Apply fault at the NORTHST3 (533370) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #2 b.3. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.4. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_279 | 3 Phase fault on FRTLEAV3 (533274) 115 kV Bus a. Apply fault at the FRTLEAV3 (533274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.2. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_279 | 3 Phase fault on FRTLEAV3 (533274) 115 kV Bus a. Apply fault at the FRTLEAV3 (533274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.2. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_28 | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Loss of synchronism for Wolfcreek Unit | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Remove reclose event. | 1) Tuned (if applicable) GEN-2018-058 developer model that provides VAR support 2) None
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_28 | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Loss of synchronism for Wolfcreek Unit | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Remove reclose event. | 1) Tuned (if applicable) GEN-2018-058 developer model that provides VAR support 2) None
03 - Central | 25S | Base Case | GROUP3_P1_FAULT_28 | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Loss of synchronism for Wolfcreek Unit | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Remove reclose event. | 1) Tuned (if applicable) GEN-2018-058 developer model that provides VAR support 2) None
03 - Central | 25W | Base Case | GROUP3_P1_FAULT_28 | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Loss of synchronism for Wolfcreek Unit | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Remove reclose event. | 1) Tuned (if applicable) GEN-2018-058 developer model that provides VAR support 2) None
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_280 | 3 Phase fault on LYONS 3 (530620) 115 kV Bus a. Apply fault at the LYONS 3 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_280 | 3 Phase fault on LYONS 3 (530620) 115 kV Bus a. Apply fault at the LYONS 3 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_281 | 3 Phase fault on 17TH TP2 (533835) 69 kV Bus a. Apply fault at the 17TH TP2 (533835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_281 | 3 Phase fault on 17TH TP2 (533835) 69 kV Bus a. Apply fault at the 17TH TP2 (533835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_282 | 3 Phase fault on ZILAJCT2 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_282 | 3 Phase fault on ZILAJCT2 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_283 | 3 Phase fault on CC4VERN2 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_283 | 3 Phase fault on CC4VERN2 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_284 | 3 Phase fault on SHERIDN2 (533841) 69 kV Bus a. Apply fault at the SHERIDN2 (533841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_284 | 3 Phase fault on SHERIDN2 (533841) 69 kV Bus a. Apply fault at the SHERIDN2 (533841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_285 | 3 Phase fault on WESTLNK2 (533854) 69 kV Bus a. Apply fault at the WESTLNK2 (533854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.3. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_285 | 3 Phase fault on WESTLNK2 (533854) 69 kV Bus a. Apply fault at the WESTLNK2 (533854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.3. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_286 | 3 Phase fault on COWSKIN2 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_286 | 3 Phase fault on COWSKIN2 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_287 | 3 Phase fault on SE4DEVO2 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_287 | 3 Phase fault on SE4DEVO2 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_288 | 3 Phase fault on CRAWFOR2 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_288 | 3 Phase fault on CRAWFOR2 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_289 | 3 Phase fault on WATER1 2 (533855) 69 kV Bus a. Apply fault at the WATER1 2 (533855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_289 | 3 Phase fault on WATER1 2 (533855) 69 kV Bus a. Apply fault at the WATER1 2 (533855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_29 | 3 Phase fault on AUBURN 6 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_29 | 3 Phase fault on AUBURN 6 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_290 | 3 Phase fault on WATER2 2 (533856) 69 kV Bus a. Apply fault at the WATER2 2 (533856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.2. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_290 | 3 Phase fault on WATER2 2 (533856) 69 kV Bus a. Apply fault at the WATER2 2 (533856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.2. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_291 | 3 Phase fault on RIPLEYW2 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.2. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.3. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_291 | 3 Phase fault on RIPLEYW2 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.2. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.3. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_292 | 3 Phase fault on GILLJCT2 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_292 | 3 Phase fault on GILLJCT2 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_293 | 3 Phase fault on SENECA 2 (533839) 69 kV Bus a. Apply fault at the SENECA 2 (533839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_293 | 3 Phase fault on SENECA 2 (533839) 69 kV Bus a. Apply fault at the SENECA 2 (533839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_294 | 3 Phase fault on ORDNJCT2 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_294 | 3 Phase fault on ORDNJCT2 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_295 | 3 Phase fault on ALTAMNS2 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_295 | 3 Phase fault on ALTAMNS2 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_296 | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_296 | 3 Phase fault on BUTLER 4 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_297 | 3 Phase fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_297 | 3 Phase fault on HOLT_REACT7 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_298 | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) High End of Sim Voltage (Near Faulted Bus) - VOLT 301342 [5BUTLER 161.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_298 | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_299 | 3 Phase fault on GRDVWTP2 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_299 | 3 Phase fault on GRDVWTP2 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_3 | 3 Phase fault on HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_3 | 3 Phase fault on HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_30 | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_30 | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_300 | 3 Phase fault on CLNTGRN2 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_300 | 3 Phase fault on CLNTGRN2 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_301 | 3 Phase fault on GRDWST 2 (541286) 69 kV Bus a. Apply fault at the GRDWST 2 (541286) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDWCTY2 (541285) 69.0 kV to GRDWST 2 (541286) 69.0 kV Transmission Circuit #1 b.2. GRDWST 2 (541286) 69.0 kV to MARTCTY2 (541287) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_301 | 3 Phase fault on GRDWST 2 (541286) 69 kV Bus a. Apply fault at the GRDWST 2 (541286) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDWCTY2 (541285) 69.0 kV to GRDWST 2 (541286) 69.0 kV Transmission Circuit #1 b.2. GRDWST 2 (541286) 69.0 kV to MARTCTY2 (541287) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_302 | 3 Phase fault on POSTOAK2 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_302 | 3 Phase fault on POSTOAK2 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_303 | 3 Phase fault on CLNTPLT_CAP2 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP2 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_303 | 3 Phase fault on CLNTPLT_CAP2 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP2 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_304 | 3 Phase fault on FROSTRD_CAP5 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_304 | 3 Phase fault on FROSTRD_CAP5 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_305 | 3 Phase fault on NASHUA_CAP5 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_305 | 3 Phase fault on NASHUA_CAP5 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_306 | 3 Phase fault on RNRIDGE_CAP5 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_306 | 3 Phase fault on RNRIDGE_CAP5 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_307 | 3 Phase fault on SEDLIAW_CAP5 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_307 | 3 Phase fault on SEDLIAW_CAP5 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_308 | 3 Phase fault on WSTELEC_CAP5 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_308 | 3 Phase fault on WSTELEC_CAP5 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_309 | 3 Phase fault on TERRACE5 (542991) 161 kV Bus a. Apply fault at the TERRACE5 (542991) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_309 | 3 Phase fault on TERRACE5 (542991) 161 kV Bus a. Apply fault at the TERRACE5 (542991) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_31 | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_31 | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_310 | 3 Phase fault on WETHRBY5 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_310 | 3 Phase fault on WETHRBY5 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_311 | 3 Phase fault on SHWNMSN5 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_311 | 3 Phase fault on SHWNMSN5 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_312 | 3 Phase fault on BARBER 5 (546651) 161 kV Bus a. Apply fault at the BARBER 5 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_312 | 3 Phase fault on BARBER 5 (546651) 161 kV Bus a. Apply fault at the BARBER 5 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_313 | 3 Phase fault on QUIND 5 (546652) 161 kV Bus a. Apply fault at the QUIND 5 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_313 | 3 Phase fault on QUIND 5 (546652) 161 kV Bus a. Apply fault at the QUIND 5 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_314 | 3 Phase fault on QUIND 5 (546652) 161 kV Bus a. Apply fault at the QUIND 5 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_314 | 3 Phase fault on QUIND 5 (546652) 161 kV Bus a. Apply fault at the QUIND 5 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_315 | 3 Phase fault on NEARMAN5 (546653) 161 kV Bus a. Apply fault at the NEARMAN5 (546653) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_315 | 3 Phase fault on NEARMAN5 (546653) 161 kV Bus a. Apply fault at the NEARMAN5 (546653) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_316 | 3 Phase fault on NEARMAN5 (546653) 161 kV Bus a. Apply fault at the NEARMAN5 (546653) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_316 | 3 Phase fault on NEARMAN5 (546653) 161 kV Bus a. Apply fault at the NEARMAN5 (546653) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_317 | 3 Phase fault on SUNSET 5 (546654) 161 kV Bus a. Apply fault at the SUNSET 5 (546654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_317 | 3 Phase fault on SUNSET 5 (546654) 161 kV Bus a. Apply fault at the SUNSET 5 (546654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_318 | 3 Phase fault on KAW W 5 (546655) 161 kV Bus a. Apply fault at the KAW W 5 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_318 | 3 Phase fault on KAW W 5 (546655) 161 kV Bus a. Apply fault at the KAW W 5 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_319 | 3 Phase fault on KAW W 5 (546655) 161 kV Bus a. Apply fault at the KAW W 5 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_319 | 3 Phase fault on KAW W 5 (546655) 161 kV Bus a. Apply fault at the KAW W 5 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_32 | 3 Phase fault on LAWHILL6 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_32 | 3 Phase fault on LAWHILL6 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_320 | 3 Phase fault on MAYWOOD5 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_320 | 3 Phase fault on MAYWOOD5 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_321 | 3 Phase fault on MAYWOOD5 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_321 | 3 Phase fault on MAYWOOD5 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_322 | 3 Phase fault on GIBBS 5 (546658) 161 kV Bus a. Apply fault at the GIBBS 5 (546658) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_322 | 3 Phase fault on GIBBS 5 (546658) 161 kV Bus a. Apply fault at the GIBBS 5 (546658) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_323 | 3 Phase fault on CTR CTY5 (546659) 161 kV Bus a. Apply fault at the CTR CTY5 (546659) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_323 | 3 Phase fault on CTR CTY5 (546659) 161 kV Bus a. Apply fault at the CTR CTY5 (546659) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_324 | 3 Phase fault on CTR CTY5 (546659) 161 kV Bus a. Apply fault at the CTR CTY5 (546659) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_324 | 3 Phase fault on CTR CTY5 (546659) 161 kV Bus a. Apply fault at the CTR CTY5 (546659) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_325 | 3 Phase fault on ARMDALE5 (546661) 161 kV Bus a. Apply fault at the ARMDALE5 (546661) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_325 | 3 Phase fault on ARMDALE5 (546661) 161 kV Bus a. Apply fault at the ARMDALE5 (546661) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_326 | 3 Phase fault on GM PLT 5 (546663) 161 kV Bus a. Apply fault at the GM PLT 5 (546663) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GM PLT 5 (546663) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_326 | 3 Phase fault on GM PLT 5 (546663) 161 kV Bus a. Apply fault at the GM PLT 5 (546663) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GM PLT 5 (546663) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_327 | 3 Phase fault on FAIRFX-5 (546667) 161 kV Bus a. Apply fault at the FAIRFX-5 (546667) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRFX-5 (546667) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_327 | 3 Phase fault on FAIRFX-5 (546667) 161 kV Bus a. Apply fault at the FAIRFX-5 (546667) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRFX-5 (546667) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_328 | 3 Phase fault on PIPER 5 (546668) 161 kV Bus a. Apply fault at the PIPER 5 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_328 | 3 Phase fault on PIPER 5 (546668) 161 kV Bus a. Apply fault at the PIPER 5 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_329 | 3 Phase fault on PIPER 5 (546668) 161 kV Bus a. Apply fault at the PIPER 5 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_329 | 3 Phase fault on PIPER 5 (546668) 161 kV Bus a. Apply fault at the PIPER 5 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_33 | 3 Phase fault on SWISVAL6 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_33 | 3 Phase fault on SWISVAL6 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_330 | 3 Phase fault on OAK KNOL (546670) 69 kV Bus a. Apply fault at the OAK KNOL (546670) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK KNOL (546670) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_330 | 3 Phase fault on OAK KNOL (546670) 69 kV Bus a. Apply fault at the OAK KNOL (546670) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK KNOL (546670) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_331 | 3 Phase fault on OAK KNOL (546670) 69 kV Bus a. Apply fault at the OAK KNOL (546670) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK KNOL (546670) 69.0 kV to MAYWOOD2 (546677) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_331 | 3 Phase fault on OAK KNOL (546670) 69 kV Bus a. Apply fault at the OAK KNOL (546670) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK KNOL (546670) 69.0 kV to MAYWOOD2 (546677) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_332 | 3 Phase fault on MORRIS 2 (546672) 69 kV Bus a. Apply fault at the MORRIS 2 (546672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 2 (546672) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_332 | 3 Phase fault on MORRIS 2 (546672) 69 kV Bus a. Apply fault at the MORRIS 2 (546672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 2 (546672) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_333 | 3 Phase fault on MORRIS 2 (546672) 69 kV Bus a. Apply fault at the MORRIS 2 (546672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_333 | 3 Phase fault on MORRIS 2 (546672) 69 kV Bus a. Apply fault at the MORRIS 2 (546672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_334 | 3 Phase fault on GR WHL 2 (546673) 69 kV Bus a. Apply fault at the GR WHL 2 (546673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR WHL 2 (546673) 69.0 kV to GW TAP 1 (546675) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_334 | 3 Phase fault on GR WHL 2 (546673) 69 kV Bus a. Apply fault at the GR WHL 2 (546673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR WHL 2 (546673) 69.0 kV to GW TAP 1 (546675) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_335 | 3 Phase fault on SPEAKER2 (546674) 69 kV Bus a. Apply fault at the SPEAKER2 (546674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_335 | 3 Phase fault on SPEAKER2 (546674) 69 kV Bus a. Apply fault at the SPEAKER2 (546674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_336 | 3 Phase fault on GW TAP 1 (546675) 69 kV Bus a. Apply fault at the GW TAP 1 (546675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GW TAP 1 (546675) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_336 | 3 Phase fault on GW TAP 1 (546675) 69 kV Bus a. Apply fault at the GW TAP 1 (546675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GW TAP 1 (546675) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_337 | 3 Phase fault on MAYWOOD2 (546677) 69 kV Bus a. Apply fault at the MAYWOOD2 (546677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD2 (546677) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_337 | 3 Phase fault on MAYWOOD2 (546677) 69 kV Bus a. Apply fault at the MAYWOOD2 (546677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD2 (546677) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_338 | 3 Phase fault on EVERETT2 (546682) 69 kV Bus a. Apply fault at the EVERETT2 (546682) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVERETT2 (546682) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_338 | 3 Phase fault on EVERETT2 (546682) 69 kV Bus a. Apply fault at the EVERETT2 (546682) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVERETT2 (546682) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_339 | 3 Phase fault on QUINDA 2 (546692) 69 kV Bus a. Apply fault at the QUINDA 2 (546692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_339 | 3 Phase fault on QUINDA 2 (546692) 69 kV Bus a. Apply fault at the QUINDA 2 (546692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_34 | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_34 | 3 Phase fault on MORRIS 6 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_340 | 3 Phase fault on QUINDA 2 (546692) 69 kV Bus a. Apply fault at the QUINDA 2 (546692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_340 | 3 Phase fault on QUINDA 2 (546692) 69 kV Bus a. Apply fault at the QUINDA 2 (546692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_341 | 3 Phase fault on MAYSOTH5 (546722) 161 kV Bus a. Apply fault at the MAYSOTH5 (546722) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_341 | 3 Phase fault on MAYSOTH5 (546722) 161 kV Bus a. Apply fault at the MAYSOTH5 (546722) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_342 | 3 Phase fault on KAW 5 (546214) 161 kV Bus a. Apply fault at the KAW 5 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_342 | 3 Phase fault on KAW 5 (546214) 161 kV Bus a. Apply fault at the KAW 5 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_343 | 3 Phase fault on KAW 5 (546214) 161 kV Bus a. Apply fault at the KAW 5 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_343 | 3 Phase fault on KAW 5 (546214) 161 kV Bus a. Apply fault at the KAW 5 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_344 | 3 Phase fault on QUIND 5 (546652) 161 kV Bus a. Apply fault at the QUIND 5 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_344 | 3 Phase fault on QUIND 5 (546652) 161 kV Bus a. Apply fault at the QUIND 5 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_345 | 3 Phase fault on KAW W 5 (546655) 161 kV Bus a. Apply fault at the KAW W 5 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_345 | 3 Phase fault on KAW W 5 (546655) 161 kV Bus a. Apply fault at the KAW W 5 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_346 | 3 Phase fault on MAYWOOD5 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_346 | 3 Phase fault on MAYWOOD5 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_347 | 3 Phase fault on OCHILTREE 6 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.3. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_347 | 3 Phase fault on OCHILTREE 6 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.3. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_348 | 3 Phase fault on TC-MCMURRY 3 (523113) 115 kV Bus a. Apply fault at the TC-MCMURRY 3 (523113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to TC-MCMURRY 3 (523113) 115.0 kV Transmission Circuit #1 b.2. TC-MCMURRY 3 (523113) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.3. COLE 3 (523120) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_348 | 3 Phase fault on TC-MCMURRY 3 (523113) 115 kV Bus a. Apply fault at the TC-MCMURRY 3 (523113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to TC-MCMURRY 3 (523113) 115.0 kV Transmission Circuit #1 b.2. TC-MCMURRY 3 (523113) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.3. COLE 3 (523120) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_349 | 3 Phase fault on TXPHSF 3 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_349 | 3 Phase fault on TXPHSF 3 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_35 | 3 Phase fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_35 | 3 Phase fault on SMOKYHL6 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_350 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_350 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_351 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_351 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_352 | 3 Phase fault on BRMALL 2 (541283) 69 kV Bus a. Apply fault at the BRMALL 2 (541283) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_352 | 3 Phase fault on BRMALL 2 (541283) 69 kV Bus a. Apply fault at the BRMALL 2 (541283) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_353 | 3 Phase fault on SUB I (548800) 69 kV Bus a. Apply fault at the SUB I (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_353 | 3 Phase fault on SUB I (548800) 69 kV Bus a. Apply fault at the SUB I (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_354 | 3 Phase fault on SUB I (548800) 69 kV Bus a. Apply fault at the SUB I (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_354 | 3 Phase fault on SUB I (548800) 69 kV Bus a. Apply fault at the SUB I (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_355 | 3 Phase fault on SUB K (548801) 69 kV Bus a. Apply fault at the SUB K (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_355 | 3 Phase fault on SUB K (548801) 69 kV Bus a. Apply fault at the SUB K (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_356 | 3 Phase fault on SUB K (548801) 69 kV Bus a. Apply fault at the SUB K (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_356 | 3 Phase fault on SUB K (548801) 69 kV Bus a. Apply fault at the SUB K (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_357 | 3 Phase fault on SUB H (548802) 69 kV Bus a. Apply fault at the SUB H (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_357 | 3 Phase fault on SUB H (548802) 69 kV Bus a. Apply fault at the SUB H (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_358 | 3 Phase fault on SUB H (548802) 69 kV Bus a. Apply fault at the SUB H (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_358 | 3 Phase fault on SUB H (548802) 69 kV Bus a. Apply fault at the SUB H (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_359 | 3 Phase fault on SUB E (548804) 69 kV Bus a. Apply fault at the SUB E (548804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_359 | 3 Phase fault on SUB E (548804) 69 kV Bus a. Apply fault at the SUB E (548804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_36 | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_36 | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_360 | 3 Phase fault on BLUVLY (548806) 69 kV Bus a. Apply fault at the BLUVLY (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_360 | 3 Phase fault on BLUVLY (548806) 69 kV Bus a. Apply fault at the BLUVLY (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_361 | 3 Phase fault on BLUVLY (548806) 69 kV Bus a. Apply fault at the BLUVLY (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_361 | 3 Phase fault on BLUVLY (548806) 69 kV Bus a. Apply fault at the BLUVLY (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_362 | 3 Phase fault on BLUVLY (548806) 69 kV Bus a. Apply fault at the BLUVLY (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_362 | 3 Phase fault on BLUVLY (548806) 69 kV Bus a. Apply fault at the BLUVLY (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_363 | 3 Phase fault on SUB B (548810) 69 kV Bus a. Apply fault at the SUB B (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_363 | 3 Phase fault on SUB B (548810) 69 kV Bus a. Apply fault at the SUB B (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_364 | 3 Phase fault on SUB J (548811) 69 kV Bus a. Apply fault at the SUB J (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_364 | 3 Phase fault on SUB J (548811) 69 kV Bus a. Apply fault at the SUB J (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_365 | 3 Phase fault on BLUVLY-161 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_365 | 3 Phase fault on BLUVLY-161 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_366 | 3 Phase fault on SHRNKRD (548809) 69 kV Bus a. Apply fault at the SHRNKRD (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_366 | 3 Phase fault on SHRNKRD (548809) 69 kV Bus a. Apply fault at the SHRNKRD (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_367 | 3 Phase fault on STRLNGRD (548826) 69 kV Bus a. Apply fault at the STRLNGRD (548826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.3. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_367 | 3 Phase fault on STRLNGRD (548826) 69 kV Bus a. Apply fault at the STRLNGRD (548826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.3. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_368 | 3 Phase fault on KCPL JCT (548832) 69 kV Bus a. Apply fault at the KCPL JCT (548832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB F (548803) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 b.2. SUB E (548804) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_368 | 3 Phase fault on KCPL JCT (548832) 69 kV Bus a. Apply fault at the KCPL JCT (548832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB F (548803) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 b.2. SUB E (548804) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_369 | 3 Phase fault on BLUMILS5 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_369 | 3 Phase fault on BLUMILS5 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_37 | 3 Phase fault on EDWRDVL5 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_37 | 3 Phase fault on EDWRDVL5 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_370 | 3 Phase fault on 5MOCITYB1 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_370 | 3 Phase fault on 5MOCITYB1 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_371 | 3 Phase fault on 5LEVASY (300320) 161 kV Bus a. Apply fault at the 5LEVASY (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_371 | 3 Phase fault on 5LEVASY (300320) 161 kV Bus a. Apply fault at the 5LEVASY (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_372 | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_372 | 3 Phase fault on SIBLEYPL (541250) 161 kV Bus a. Apply fault at the SIBLEYPL (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_373 | 3 Phase fault on HAWTH 2 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_373 | 3 Phase fault on HAWTH 2 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_374 | 3 Phase fault on LAKCTYJ2 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_374 | 3 Phase fault on LAKCTYJ2 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_375 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_375 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_376 | 3 Phase fault on BLUEVLY5 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_376 | 3 Phase fault on BLUEVLY5 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_377 | 3 Phase fault on CRAIG_CAP 5 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_377 | 3 Phase fault on CRAIG_CAP 5 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_378 | 3 Phase fault on GLADSTN_CAP5 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_378 | 3 Phase fault on GLADSTN_CAP5 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_379 | 3 Phase fault on NORTON 5 (543064) 161 kV Bus a. Apply fault at the NORTON 5 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (543064) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_379 | 3 Phase fault on NORTON 5 (543064) 161 kV Bus a. Apply fault at the NORTON 5 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (543064) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_38 | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_38 | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_380 | 3 Phase fault on SWAVCAP5 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_380 | 3 Phase fault on SWAVCAP5 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_381 | 3 Phase fault on SUGRCK_TP_E2 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E2 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCRK_S2 (543163) 69.0 kV Transmission Circuit #z1 b.2. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.3. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.4. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.5. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_381 | 3 Phase fault on SUGRCK_TP_E2 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E2 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCRK_S2 (543163) 69.0 kV Transmission Circuit #z1 b.2. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.3. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.4. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.5. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_382 | 3 Phase fault on KCSOUTH5 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_382 | 3 Phase fault on KCSOUTH5 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_383 | 3 Phase fault on NEVADA 2 (541308) 69 kV Bus a. Apply fault at the NEVADA 2 (541308) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_383 | 3 Phase fault on NEVADA 2 (541308) 69 kV Bus a. Apply fault at the NEVADA 2 (541308) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_384 | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_384 | 3 Phase fault on COWSKIN4 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_385 | 3 Phase fault on HOOVERS4 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_385 | 3 Phase fault on HOOVERS4 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_386 | 3 Phase fault on HOOVERN4 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_386 | 3 Phase fault on HOOVERN4 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_387 | 3 Phase fault on NOEASTW4 (533061) 138 kV Bus a. Apply fault at the NOEASTW4 (533061) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_387 | 3 Phase fault on NOEASTW4 (533061) 138 kV Bus a. Apply fault at the NOEASTW4 (533061) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_388 | 3 Phase fault on NOEASTE4 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_388 | 3 Phase fault on NOEASTE4 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_389 | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_389 | 3 Phase fault on WEAVER 4 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_39 | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_39 | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_390 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_390 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_391 | 3 Phase fault on CHAPMAN3 (533362) 115 kV Bus a. Apply fault at the CHAPMAN3 (533362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPMAN3 (533362) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_391 | 3 Phase fault on CHAPMAN3 (533362) 115 kV Bus a. Apply fault at the CHAPMAN3 (533362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPMAN3 (533362) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_392 | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_392 | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_393 | 3 Phase fault on FT JCT 3 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_393 | 3 Phase fault on FT JCT 3 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_394 | 3 Phase fault on JARBALO3 (533244) 115 kV Bus a. Apply fault at the JARBALO3 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_394 | 3 Phase fault on JARBALO3 (533244) 115 kV Bus a. Apply fault at the JARBALO3 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_395 | 3 Phase fault on NORTHVW3 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_395 | 3 Phase fault on NORTHVW3 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_396 | 3 Phase fault on NW LEAV3 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_396 | 3 Phase fault on NW LEAV3 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_397 | 3 Phase fault on SENECA 3 (533337) 115 kV Bus a. Apply fault at the SENECA 3 (533337) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SENECA 3 (533337) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_397 | 3 Phase fault on SENECA 3 (533337) 115 kV Bus a. Apply fault at the SENECA 3 (533337) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SENECA 3 (533337) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_398 | 3 Phase fault on TCSENCA3 (533348) 115 kV Bus a. Apply fault at the TCSENCA3 (533348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCSENCA3 (533348) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_398 | 3 Phase fault on TCSENCA3 (533348) 115 kV Bus a. Apply fault at the TCSENCA3 (533348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCSENCA3 (533348) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_399 | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_399 | 3 Phase fault on WMCPHER3 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_4 | 3 Phase fault on JAGGER 3 (531360) 115 kV Bus a. Apply fault at the JAGGER 3 (531360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELER 3 (531359) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.2. BEELER 3 (531359) 115.0 kV to LIBERTYT (531495) 115.0 kV Transmission Circuit #1 b.3. JAGGER 3 (531360) 115.0 kV to DIGHTON3 (531361) 115.0 kV Transmission Circuit #1 b.4. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.5. JAGGER 3 (531360) 115.0 kV to LIBERTYT (531495) 115.0 kV Transmission Circuit #1 b.6. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.7. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_4 | 3 Phase fault on JAGGER 3 (531360) 115 kV Bus a. Apply fault at the JAGGER 3 (531360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELER 3 (531359) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.2. BEELER 3 (531359) 115.0 kV to LIBERTYT (531495) 115.0 kV Transmission Circuit #1 b.3. JAGGER 3 (531360) 115.0 kV to DIGHTON3 (531361) 115.0 kV Transmission Circuit #1 b.4. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.5. JAGGER 3 (531360) 115.0 kV to LIBERTYT (531495) 115.0 kV Transmission Circuit #1 b.6. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.7. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_40 | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_40 | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_400 | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_400 | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_401 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_401 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_402 | 3 Phase fault on NEPARSN4 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_402 | 3 Phase fault on NEPARSN4 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_403 | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_403 | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_404 | 3 Phase fault on HOOVERN2 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_404 | 3 Phase fault on HOOVERN2 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_405 | 3 Phase fault on PARSONS2 (533704) 69 kV Bus a. Apply fault at the PARSONS2 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_405 | 3 Phase fault on PARSONS2 (533704) 69 kV Bus a. Apply fault at the PARSONS2 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_406 | 3 Phase fault on WOLFCRK2 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_406 | 3 Phase fault on WOLFCRK2 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_407 | 3 Phase fault on WAVERLY3 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_407 | 3 Phase fault on WAVERLY3 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_408 | 3 Phase fault on SHAWNEE3 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_408 | 3 Phase fault on SHAWNEE3 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_409 | 3 Phase fault on CRAWFRD3 (533364) 115 kV Bus a. Apply fault at the CRAWFRD3 (533364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD3 (533364) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 b.3. MENTOR 3 (533374) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_409 | 3 Phase fault on CRAWFRD3 (533364) 115 kV Bus a. Apply fault at the CRAWFRD3 (533364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD3 (533364) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 b.3. MENTOR 3 (533374) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_41 | 3 Phase fault on TIOGA 4 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_41 | 3 Phase fault on TIOGA 4 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_410 | 3 Phase fault on MENTOR 3 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_410 | 3 Phase fault on MENTOR 3 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_411 | 3 Phase fault on TECHILW3 (533181) 115 kV Bus a. Apply fault at the TECHILW3 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_411 | 3 Phase fault on TECHILW3 (533181) 115 kV Bus a. Apply fault at the TECHILW3 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_412 | 3 Phase fault on SO GATE3 (533379) 115 kV Bus a. Apply fault at the SO GATE3 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_412 | 3 Phase fault on SO GATE3 (533379) 115 kV Bus a. Apply fault at the SO GATE3 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_413 | 3 Phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_413 | 3 Phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_414 | 3 Phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_414 | 3 Phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_415 | 3 Phase fault on BAKER 2 (532926) 69 kV Bus a. Apply fault at the BAKER 2 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_415 | 3 Phase fault on BAKER 2 (532926) 69 kV Bus a. Apply fault at the BAKER 2 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_416 | 3 Phase fault on EDWARVL3 (533238) 115 kV Bus a. Apply fault at the EDWARVL3 (533238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_416 | 3 Phase fault on EDWARVL3 (533238) 115 kV Bus a. Apply fault at the EDWARVL3 (533238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_417 | 3 Phase fault on MENTOR 3 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_417 | 3 Phase fault on MENTOR 3 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_418 | 3 Phase fault on QUINTON3 (533172) 115 kV Bus a. Apply fault at the QUINTON3 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_418 | 3 Phase fault on QUINTON3 (533172) 115 kV Bus a. Apply fault at the QUINTON3 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_419 | 3 Phase fault on STEINER7 (640361) 115 kV Bus a. Apply fault at the STEINER7 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_419 | 3 Phase fault on STEINER7 (640361) 115 kV Bus a. Apply fault at the STEINER7 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_42 | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_42 | 3 Phase fault on BENTON 4 (532986) 138 kV Bus a. Apply fault at the BENTON 4 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_420 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_420 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_421 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_421 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_422 | 3 Phase fault on HUMBOLT5 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_422 | 3 Phase fault on HUMBOLT5 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_423 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_423 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_424 | 3 Phase fault on MONOLITH 3 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_424 | 3 Phase fault on MONOLITH 3 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_425 | 3 Phase fault on MONOLITH 3 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_425 | 3 Phase fault on MONOLITH 3 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_426 | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_426 | 3 Phase fault on 7FAIRPT (300039) 345 kV Bus a. Apply fault at the 7FAIRPT (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_427 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_427 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_428 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_428 | 3 Phase fault on S3451 3 (645451) 345 kV Bus a. Apply fault at the S3451 3 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_429 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_429 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_43 | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_43 | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_430 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_430 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_431 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_431 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_432 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_432 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_433 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_433 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_434 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_434 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_435 | 3 Phase fault on S3458 3 (645458) 345 kV Bus a. Apply fault at the S3458 3 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_435 | 3 Phase fault on S3458 3 (645458) 345 kV Bus a. Apply fault at the S3458 3 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_436 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_436 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_437 | 3 Phase fault on HUMBOLT5 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_437 | 3 Phase fault on HUMBOLT5 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_438 | 3 Phase fault on S1263 5 (646263) 161 kV Bus a. Apply fault at the S1263 5 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_438 | 3 Phase fault on S1263 5 (646263) 161 kV Bus a. Apply fault at the S1263 5 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_439 | 3 Phase fault on COOPER 5 (640140) 161 kV Bus a. Apply fault at the COOPER 5 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_439 | 3 Phase fault on COOPER 5 (640140) 161 kV Bus a. Apply fault at the COOPER 5 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_44 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_44 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_440 | 3 Phase fault on S1398 5 (646398) 161 kV Bus a. Apply fault at the S1398 5 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_440 | 3 Phase fault on S1398 5 (646398) 161 kV Bus a. Apply fault at the S1398 5 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_441 | 3 Phase fault on S965 8 (647965) 69 kV Bus a. Apply fault at the S965 8 (647965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_441 | 3 Phase fault on S965 8 (647965) 69 kV Bus a. Apply fault at the S965 8 (647965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_442 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_442 | 3 Phase fault on S3454 3 (645454) 345 kV Bus a. Apply fault at the S3454 3 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_443 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_443 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_444 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_444 | 3 Phase fault on S3455 3 (645455) 345 kV Bus a. Apply fault at the S3455 3 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_445 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_445 | 3 Phase fault on S3456 3 (645456) 345 kV Bus a. Apply fault at the S3456 3 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_446 | 3 Phase fault on S3459 3 (645459) 345 kV Bus a. Apply fault at the S3459 3 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_446 | 3 Phase fault on S3459 3 (645459) 345 kV Bus a. Apply fault at the S3459 3 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_447 | 3 Phase fault on S3459 3 (645459) 345 kV Bus a. Apply fault at the S3459 3 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_447 | 3 Phase fault on S3459 3 (645459) 345 kV Bus a. Apply fault at the S3459 3 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_448 | 3 Phase fault on S3761 3 (645761) 345 kV Bus a. Apply fault at the S3761 3 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_448 | 3 Phase fault on S3761 3 (645761) 345 kV Bus a. Apply fault at the S3761 3 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_449 | 3 Phase fault on HUMBOLT5 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_449 | 3 Phase fault on HUMBOLT5 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_45 | 3 Phase fault on ELPASO 4 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_45 | 3 Phase fault on ELPASO 4 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_450 | 3 Phase fault on ELMCREEK7 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_450 | 3 Phase fault on ELMCREEK7 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_451 | 3 Phase fault on RAGO 4 (539000) 138 kV Bus a. Apply fault at the RAGO 4 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_451 | 3 Phase fault on RAGO 4 (539000) 138 kV Bus a. Apply fault at the RAGO 4 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_452 | 3 Phase fault on IODINE 4 (520957) 138 kV Bus a. Apply fault at the IODINE 4 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_452 | 3 Phase fault on IODINE 4 (520957) 138 kV Bus a. Apply fault at the IODINE 4 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_453 | 3 Phase fault on GLASMTN4 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_453 | 3 Phase fault on GLASMTN4 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_454 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_454 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_455 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_455 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_456 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_456 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_457 | 3 Phase fault on WFEC_RNFRO4 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_457 | 3 Phase fault on WFEC_RNFRO4 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_458 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_458 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_459 | 3 Phase fault on Y ROAD 3 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to TEXAS_CNTY 3 (523090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_459 | 3 Phase fault on Y ROAD 3 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to TEXAS_CNTY 3 (523090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_46 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_46 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_460 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR11 (523085) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_460 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR11 (523085) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_461 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_461 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR11 (523085) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_462 | 3 Phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_462 | 3 Phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_463 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_463 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_464 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_464 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_465 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_465 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_466 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_466 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_467 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_467 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_468 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_468 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_469 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_469 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_47 | 3 Phase fault on HALSTD 4 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_47 | 3 Phase fault on HALSTD 4 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_470 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_470 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_471 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_471 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_472 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_472 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_473 | 3 Phase fault on MDFRDTP4 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_473 | 3 Phase fault on MDFRDTP4 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_474 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_474 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_475 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_475 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_476 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_476 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_477 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_477 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_478 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_478 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_479 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_479 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_48 | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_48 | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_480 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_480 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_481 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_481 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_482 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_482 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_483 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_483 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_484 | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_484 | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_485 | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_485 | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_486 | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_486 | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_487 | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_487 | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_488 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_488 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_489 | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_489 | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_49 | 3 Phase fault on GILL W 4 (533045) 138 kV Bus a. Apply fault at the GILL W 4 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_49 | 3 Phase fault on GILL W 4 (533045) 138 kV Bus a. Apply fault at the GILL W 4 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_490 | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_490 | 3 Phase fault on GRTBEND6 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_491 | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_491 | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_492 | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_492 | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_493 | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_493 | 3 Phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_494 | 3 Phase fault on MILAN_GOAB (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_494 | 3 Phase fault on MILAN_GOAB (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_495 | 3 Phase fault on SETAB 3 (531464) 115 kV Bus a. Apply fault at the SETAB 3 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_495 | 3 Phase fault on SETAB 3 (531464) 115 kV Bus a. Apply fault at the SETAB 3 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_496 | 3 Phase fault on SCOTCTY3 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_496 | 3 Phase fault on SCOTCTY3 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_497 | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_497 | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_498 | 3 Phase fault on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_498 | 3 Phase fault on PLYMELL3 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_499 | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_499 | 3 Phase fault on FLETCHR3 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_5 | 3 Phase fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_5 | 3 Phase fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_50 | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_50 | 3 Phase fault on ROSEHIL4 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_500 | 3 Phase fault on GRANTTP3 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_500 | 3 Phase fault on GRANTTP3 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_501 | 3 Phase fault on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_501 | 3 Phase fault on PK_GOAB3 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_502 | 3 Phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_502 | 3 Phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_503 | 3 Phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_503 | 3 Phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_504 | 3 Phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_504 | 3 Phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_505 | 3 Phase fault on SATATAP3 (531396) 115 kV Bus a. Apply fault at the SATATAP3 (531396) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUBART 3 (531200) 115.0 kV to SATATAP3 (531396) 115.0 kV Transmission Circuit #1 b.2. PNTPR-GOAB3 (531203) 115.0 kV to PLSNTPR3 (531204) 115.0 kV Transmission Circuit #1 b.3. PNTPR-GOAB3 (531203) 115.0 kV to PIONTAP3 (531392) 115.0 kV Transmission Circuit #1 b.4. PNTPR-GOAB3 (531203) 115.0 kV to SATATAP3 (531396) 115.0 kV Transmission Circuit #1 b.5. SATATAP3 (531396) 115.0 kV to SATANTA3 (531397) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_505 | 3 Phase fault on SATATAP3 (531396) 115 kV Bus a. Apply fault at the SATATAP3 (531396) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUBART 3 (531200) 115.0 kV to SATATAP3 (531396) 115.0 kV Transmission Circuit #1 b.2. PNTPR-GOAB3 (531203) 115.0 kV to PLSNTPR3 (531204) 115.0 kV Transmission Circuit #1 b.3. PNTPR-GOAB3 (531203) 115.0 kV to PIONTAP3 (531392) 115.0 kV Transmission Circuit #1 b.4. PNTPR-GOAB3 (531203) 115.0 kV to SATATAP3 (531396) 115.0 kV Transmission Circuit #1 b.5. SATATAP3 (531396) 115.0 kV to SATANTA3 (531397) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_506 | 3 Phase fault on SAT-TAP3 (531442) 115 kV Bus a. Apply fault at the SAT-TAP3 (531442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 b.3. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.4. SAT-TAP3 (531442) 115.0 kV to SATMKEC3 (539691) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_506 | 3 Phase fault on SAT-TAP3 (531442) 115 kV Bus a. Apply fault at the SAT-TAP3 (531442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 b.3. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.4. SAT-TAP3 (531442) 115.0 kV to SATMKEC3 (539691) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_507 | 3 Phase fault on N-CIMRN3 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_507 | 3 Phase fault on N-CIMRN3 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_508 | 3 Phase fault on WILLIAM3 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_508 | 3 Phase fault on WILLIAM3 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_509 | 3 Phase fault on GANO 3 (531493) 115 kV Bus a. Apply fault at the GANO 3 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_509 | 3 Phase fault on GANO 3 (531493) 115 kV Bus a. Apply fault at the GANO 3 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_51 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_51 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_510 | 3 Phase fault on KSAVWTP3 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_510 | 3 Phase fault on KSAVWTP3 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_511 | 3 Phase fault on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_511 | 3 Phase fault on SWNDTAP3 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_512 | 3 Phase fault on MORRIS-3 (531430) 115 kV Bus a. Apply fault at the MORRIS-3 (531430) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.3. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_512 | 3 Phase fault on MORRIS-3 (531430) 115 kV Bus a. Apply fault at the MORRIS-3 (531430) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.3. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_513 | 3 Phase fault on LOWETAP3 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_513 | 3 Phase fault on LOWETAP3 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_514 | 3 Phase fault on SAWYER 3 (539649) 115 kV Bus a. Apply fault at the SAWYER 3 (539649) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER 3 (539649) 115.0 kV to RVROAD (539651) 115.0 kV Transmission Circuit #1 b.2. SAWYER 3 (539649) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_514 | 3 Phase fault on SAWYER 3 (539649) 115 kV Bus a. Apply fault at the SAWYER 3 (539649) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER 3 (539649) 115.0 kV to RVROAD (539651) 115.0 kV Transmission Circuit #1 b.2. SAWYER 3 (539649) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_515 | 3 Phase fault on MED-LDG3 (539673) 115 kV Bus a. Apply fault at the MED-LDG3 (539673) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MED-LDG3 (539673) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_515 | 3 Phase fault on MED-LDG3 (539673) 115 kV Bus a. Apply fault at the MED-LDG3 (539673) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MED-LDG3 (539673) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_516 | 3 Phase fault on SUNCITY3 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_516 | 3 Phase fault on SUNCITY3 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_517 | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_517 | 3 Phase fault on FORD 3 (539758) 115 kV Bus a. Apply fault at the FORD 3 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_518 | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_518 | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_519 | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_519 | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_52 | 3 Phase fault on QUINTON3 (533172) 115 kV Bus a. Apply fault at the QUINTON3 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_52 | 3 Phase fault on QUINTON3 (533172) 115 kV Bus a. Apply fault at the QUINTON3 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_520 | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_520 | 3 Phase fault on FTDODGE3 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_521 | 3 Phase fault on CUDAHY 3 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_521 | 3 Phase fault on CUDAHY 3 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_522 | 3 Phase fault on DCBEEF3 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_522 | 3 Phase fault on DCBEEF3 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_523 | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_523 | 3 Phase fault on SPEARVL3 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_524 | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_524 | 3 Phase fault on SPRVL 3 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_525 | 3 Phase fault on HAYNE3 (539640) 115 kV Bus a. Apply fault at the HAYNE3 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_525 | 3 Phase fault on HAYNE3 (539640) 115 kV Bus a. Apply fault at the HAYNE3 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_526 | 3 Phase fault on N-DODGE3 (539680) 115 kV Bus a. Apply fault at the N-DODGE3 (539680) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DODG3 (539641) 115.0 kV to N-DODGE3 (539680) 115.0 kV Transmission Circuit #1 b.2. N-DODGE3 (539680) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. N-DODGE3 (539680) 115.0 kV to N-DODGE1 (539720) 34.5 kV to N-DODG-T (539922) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_526 | 3 Phase fault on N-DODGE3 (539680) 115 kV Bus a. Apply fault at the N-DODGE3 (539680) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DODG3 (539641) 115.0 kV to N-DODGE3 (539680) 115.0 kV Transmission Circuit #1 b.2. N-DODGE3 (539680) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. N-DODGE3 (539680) 115.0 kV to N-DODGE1 (539720) 34.5 kV to N-DODG-T (539922) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_527 | 3 Phase fault on HAYNE3 (539640) 115 kV Bus a. Apply fault at the HAYNE3 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_527 | 3 Phase fault on HAYNE3 (539640) 115 kV Bus a. Apply fault at the HAYNE3 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_528 | 3 Phase fault on NATBEEF3 (539751) 115 kV Bus a. Apply fault at the NATBEEF3 (539751) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_528 | 3 Phase fault on NATBEEF3 (539751) 115 kV Bus a. Apply fault at the NATBEEF3 (539751) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_529 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_529 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_53 | 3 Phase fault on 6 GOLDN3 (533177) 115 kV Bus a. Apply fault at the 6 GOLDN3 (533177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_53 | 3 Phase fault on 6 GOLDN3 (533177) 115 kV Bus a. Apply fault at the 6 GOLDN3 (533177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_530 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_530 | 3 Phase fault on MINGO 7 (531451) 345 kV Bus a. Apply fault at the MINGO 7 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_531 | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_531 | 3 Phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_532 | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_532 | 3 Phase fault on SETAB 7 (531465) 345 kV Bus a. Apply fault at the SETAB 7 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_533 | 3 Phase fault on BARBER 4 (539674) 138 kV Bus a. Apply fault at the BARBER 4 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_533 | 3 Phase fault on BARBER 4 (539674) 138 kV Bus a. Apply fault at the BARBER 4 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_534 | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_534 | 3 Phase fault on SPEARVL6 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_535 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_535 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_536 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_536 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_537 | 3 Phase fault on WALKMYR2 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_537 | 3 Phase fault on WALKMYR2 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_538 | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_538 | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_539 | 3 Phase fault on E-LIBER3 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_539 | 3 Phase fault on E-LIBER3 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_54 | 3 Phase fault on QUINTON3 (533172) 115 kV Bus a. Apply fault at the QUINTON3 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 12&CLAY3 (533184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_54 | 3 Phase fault on QUINTON3 (533172) 115 kV Bus a. Apply fault at the QUINTON3 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 12&CLAY3 (533184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_540 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_540 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_541 | 3 Phase fault on J1026 POI (40264) 345 kV Bus a. Apply fault at the J1026 POI (40264) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1026 POI (40264) 345.0 kV to 7MAYWOOD (345435) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_541 | 3 Phase fault on J1026 POI (40264) 345 kV Bus a. Apply fault at the J1026 POI (40264) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1026 POI (40264) 345.0 kV to 7MAYWOOD (345435) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_542 | 3 Phase fault on J1026 POI (40264) 345 kV Bus a. Apply fault at the J1026 POI (40264) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1026 POI (40264) 345.0 kV to 7SPENCER (345992) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_542 | 3 Phase fault on J1026 POI (40264) 345 kV Bus a. Apply fault at the J1026 POI (40264) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1026 POI (40264) 345.0 kV to 7SPENCER (345992) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_543 | 3 Phase fault on J1352 POI (43524) 345 kV Bus a. Apply fault at the J1352 POI (43524) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1352 POI (43524) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_543 | 3 Phase fault on J1352 POI (43524) 345 kV Bus a. Apply fault at the J1352 POI (43524) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1352 POI (43524) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_544 | 3 Phase fault on J1352 POI (43524) 345 kV Bus a. Apply fault at the J1352 POI (43524) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1352 POI (43524) 345.0 kV to 7SPENCER (345992) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_544 | 3 Phase fault on J1352 POI (43524) 345 kV Bus a. Apply fault at the J1352 POI (43524) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1352 POI (43524) 345.0 kV to 7SPENCER (345992) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_545 | 3 Phase fault on J1490_POI (44888) 345 kV Bus a. Apply fault at the J1490_POI (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_545 | 3 Phase fault on J1490_POI (44888) 345 kV Bus a. Apply fault at the J1490_POI (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_546 | 3 Phase fault on J1490_POI (44888) 345 kV Bus a. Apply fault at the J1490_POI (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_546 | 3 Phase fault on J1490_POI (44888) 345 kV Bus a. Apply fault at the J1490_POI (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_547 | 3 Phase fault on 7KINGDM (300043) 345 kV Bus a. Apply fault at the 7KINGDM (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_547 | 3 Phase fault on 7KINGDM (300043) 345 kV Bus a. Apply fault at the 7KINGDM (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_548 | 3 Phase fault on 7MCCRED (300044) 345 kV Bus a. Apply fault at the 7MCCRED (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_548 | 3 Phase fault on 7MCCRED (300044) 345 kV Bus a. Apply fault at the 7MCCRED (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_549 | 3 Phase fault on 7MCCRED (300044) 345 kV Bus a. Apply fault at the 7MCCRED (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_549 | 3 Phase fault on 7MCCRED (300044) 345 kV Bus a. Apply fault at the 7MCCRED (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_55 | 3 Phase fault on TIMBRLN3 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_55 | 3 Phase fault on TIMBRLN3 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_550 | 3 Phase fault on 7MCCRED (300044) 345 kV Bus a. Apply fault at the 7MCCRED (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_550 | 3 Phase fault on 7MCCRED (300044) 345 kV Bus a. Apply fault at the 7MCCRED (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_551 | 3 Phase fault on 7PALMYR_AI (300050) 345 kV Bus a. Apply fault at the 7PALMYR_AI (300050) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7PALMYR_AI (300050) 345.0 kV to 7MAYWOOD (345435) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_551 | 3 Phase fault on 7PALMYR_AI (300050) 345 kV Bus a. Apply fault at the 7PALMYR_AI (300050) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7PALMYR_AI (300050) 345.0 kV to 7MAYWOOD (345435) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_552 | 3 Phase fault on 7ENON (300052) 345 kV Bus a. Apply fault at the 7ENON (300052) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ENON (300052) 345.0 kV to 7ENON_TP (344536) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_552 | 3 Phase fault on 7ENON (300052) 345 kV Bus a. Apply fault at the 7ENON (300052) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ENON (300052) 345.0 kV to 7ENON_TP (344536) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_553 | 3 Phase fault on 5HIGBEEB1 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_553 | 3 Phase fault on 5HIGBEEB1 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_554 | 3 Phase fault on 5HIGBEEB1 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_554 | 3 Phase fault on 5HIGBEEB1 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_555 | 3 Phase fault on 5HIGBEEB1 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to GI92_POI (709200) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_555 | 3 Phase fault on 5HIGBEEB1 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to GI92_POI (709200) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_556 | 3 Phase fault on 5CHILLIN (300068) 161 kV Bus a. Apply fault at the 5CHILLIN (300068) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHILLIN (300068) 161.0 kV to 5CHILLIS (300218) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_556 | 3 Phase fault on 5CHILLIN (300068) 161 kV Bus a. Apply fault at the 5CHILLIN (300068) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHILLIN (300068) 161.0 kV to 5CHILLIS (300218) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_557 | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_557 | 3 Phase fault on 5CHOTEAU1 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_558 | 3 Phase fault on 5CLARK (300070) 161 kV Bus a. Apply fault at the 5CLARK (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_558 | 3 Phase fault on 5CLARK (300070) 161 kV Bus a. Apply fault at the 5CLARK (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_559 | 3 Phase fault on 5CLARK (300070) 161 kV Bus a. Apply fault at the 5CLARK (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_559 | 3 Phase fault on 5CLARK (300070) 161 kV Bus a. Apply fault at the 5CLARK (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_56 | 3 Phase fault on ANZIO 3 (533321) 115 kV Bus a. Apply fault at the ANZIO 3 (533321) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_56 | 3 Phase fault on ANZIO 3 (533321) 115 kV Bus a. Apply fault at the ANZIO 3 (533321) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_560 | 3 Phase fault on 5GEORGE (300082) 161 kV Bus a. Apply fault at the 5GEORGE (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_560 | 3 Phase fault on 5GEORGE (300082) 161 kV Bus a. Apply fault at the 5GEORGE (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_561 | 3 Phase fault on 5GEORGE (300082) 161 kV Bus a. Apply fault at the 5GEORGE (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_561 | 3 Phase fault on 5GEORGE (300082) 161 kV Bus a. Apply fault at the 5GEORGE (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_562 | 3 Phase fault on 5KINGDMB1 (300090) 161 kV Bus a. Apply fault at the 5KINGDMB1 (300090) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KINGDMB1 (300090) 161.0 kV to 5KINGDMB2 (301497) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_562 | 3 Phase fault on 5KINGDMB1 (300090) 161 kV Bus a. Apply fault at the 5KINGDMB1 (300090) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KINGDMB1 (300090) 161.0 kV to 5KINGDMB2 (301497) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_563 | 3 Phase fault on 5NORTON (300105) 161 kV Bus a. Apply fault at the 5NORTON (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_563 | 3 Phase fault on 5NORTON (300105) 161 kV Bus a. Apply fault at the 5NORTON (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_564 | 3 Phase fault on 5THMHILB1 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_564 | 3 Phase fault on 5THMHILB1 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_565 | 3 Phase fault on 5THMHILB1 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_565 | 3 Phase fault on 5THMHILB1 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_566 | 3 Phase fault on 5THMHILB1 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHILTFERB (301511) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_566 | 3 Phase fault on 5THMHILB1 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHILTFERB (301511) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_567 | 3 Phase fault on 5MOBTAP (300126) 161 kV Bus a. Apply fault at the 5MOBTAP (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_567 | 3 Phase fault on 5MOBTAP (300126) 161 kV Bus a. Apply fault at the 5MOBTAP (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_568 | 3 Phase fault on 5MOBTAP (300126) 161 kV Bus a. Apply fault at the 5MOBTAP (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_568 | 3 Phase fault on 5MOBTAP (300126) 161 kV Bus a. Apply fault at the 5MOBTAP (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_569 | 3 Phase fault on 5THMHLB2 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB3 (300133) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_569 | 3 Phase fault on 5THMHLB2 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB3 (300133) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_57 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_57 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_570 | 3 Phase fault on 5THMHLB2 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5BEVIER (300381) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_570 | 3 Phase fault on 5THMHLB2 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5BEVIER (300381) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_571 | 3 Phase fault on 5THMHLB2 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_571 | 3 Phase fault on 5THMHLB2 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_572 | 3 Phase fault on 5THMHLB2 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THOMHLXF1 (301508) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_572 | 3 Phase fault on 5THMHLB2 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THOMHLXF1 (301508) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_573 | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5MEADVLB1 (300207) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_573 | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5MEADVLB1 (300207) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_574 | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLXF3 (301506) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_574 | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLXF3 (301506) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_575 | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLU3SU (301507) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_575 | 3 Phase fault on 5THMHLB3 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLU3SU (301507) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_576 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2INGROV (300201) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_576 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2INGROV (300201) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_577 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2BYNUMV (300389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_577 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2BYNUMV (300389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_578 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2YATES (300615) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_578 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2YATES (300615) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_579 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2THMINTP (301318) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_579 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2THMINTP (301318) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_58 | 3 Phase fault on GEARY 3 (533336) 115 kV Bus a. Apply fault at the GEARY 3 (533336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_58 | 3 Phase fault on GEARY 3 (533336) 115 kV Bus a. Apply fault at the GEARY 3 (533336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_580 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2THOMHLXF1 (301509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_580 | 3 Phase fault on 2TMHILL (300172) 69 kV Bus a. Apply fault at the 2TMHILL (300172) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 2THOMHLXF1 (301509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_581 | 3 Phase fault on 5MEADVLB1 (300207) 161 kV Bus a. Apply fault at the 5MEADVLB1 (300207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MEADVLB1 (300207) 161.0 kV to 5MEADVLB2 (301562) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_581 | 3 Phase fault on 5MEADVLB1 (300207) 161 kV Bus a. Apply fault at the 5MEADVLB1 (300207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MEADVLB1 (300207) 161.0 kV to 5MEADVLB2 (301562) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_582 | 3 Phase fault on 5CHILLIS (300218) 161 kV Bus a. Apply fault at the 5CHILLIS (300218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHILLIS (300218) 161.0 kV to 5MEADVLB2 (301562) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_582 | 3 Phase fault on 5CHILLIS (300218) 161 kV Bus a. Apply fault at the 5CHILLIS (300218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHILLIS (300218) 161.0 kV to 5MEADVLB2 (301562) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_583 | 3 Phase fault on 2BEVIER (300387) 69 kV Bus a. Apply fault at the 2BEVIER (300387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEVIER (300387) 69.0 kV to 2BEVIERTP (301623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_583 | 3 Phase fault on 2BEVIER (300387) 69 kV Bus a. Apply fault at the 2BEVIER (300387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEVIER (300387) 69.0 kV to 2BEVIERTP (301623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_584 | 3 Phase fault on 2BYNUMV (300389) 69 kV Bus a. Apply fault at the 2BYNUMV (300389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BYNUMV (300389) 69.0 kV to 2MARCTP (300404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_584 | 3 Phase fault on 2BYNUMV (300389) 69 kV Bus a. Apply fault at the 2BYNUMV (300389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BYNUMV (300389) 69.0 kV to 2MARCTP (300404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_585 | 3 Phase fault on 2HUNTSV (300394) 69 kV Bus a. Apply fault at the 2HUNTSV (300394) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HUNTSV (300394) 69.0 kV to 2THMINTP (301318) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_585 | 3 Phase fault on 2HUNTSV (300394) 69 kV Bus a. Apply fault at the 2HUNTSV (300394) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HUNTSV (300394) 69.0 kV to 2THMINTP (301318) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_586 | 3 Phase fault on 2MACNLK (300400) 69 kV Bus a. Apply fault at the 2MACNLK (300400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MACNLK (300400) 69.0 kV to 2BEVIERTP (301623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_586 | 3 Phase fault on 2MACNLK (300400) 69 kV Bus a. Apply fault at the 2MACNLK (300400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MACNLK (300400) 69.0 kV to 2BEVIERTP (301623) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_587 | 3 Phase fault on 5MCBAINB1 (300501) 161 kV Bus a. Apply fault at the 5MCBAINB1 (300501) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_587 | 3 Phase fault on 5MCBAINB1 (300501) 161 kV Bus a. Apply fault at the 5MCBAINB1 (300501) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_588 | 3 Phase fault on 5STURGN (300508) 161 kV Bus a. Apply fault at the 5STURGN (300508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STURGN (300508) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) High End of Sim Voltage (Near Faulted Bus) - VOLT 300508 [5STURGN 161.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_588 | 3 Phase fault on 5STURGN (300508) 161 kV Bus a. Apply fault at the 5STURGN (300508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STURGN (300508) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_589 | 3 Phase fault on 2MALTAB (300535) 69 kV Bus a. Apply fault at the 2MALTAB (300535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAB (300535) 69.0 kV to 2MALTAJ (300536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_589 | 3 Phase fault on 2MALTAB (300535) 69 kV Bus a. Apply fault at the 2MALTAB (300535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAB (300535) 69.0 kV to 2MALTAJ (300536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_59 | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_59 | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_590 | 3 Phase fault on 2MALTAJ (300536) 69 kV Bus a. Apply fault at the 2MALTAJ (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2MARSHL (300537) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_590 | 3 Phase fault on 2MALTAJ (300536) 69 kV Bus a. Apply fault at the 2MALTAJ (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2MARSHL (300537) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_591 | 3 Phase fault on 2MALTAJ (300536) 69 kV Bus a. Apply fault at the 2MALTAJ (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_591 | 3 Phase fault on 2MALTAJ (300536) 69 kV Bus a. Apply fault at the 2MALTAJ (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_592 | 3 Phase fault on 2NAPTON (300538) 69 kV Bus a. Apply fault at the 2NAPTON (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Low Voltage + Oscillations - VOLT 533324 [TCRILEY 3 115.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) 2017-120 Units require Drive Train to have Machine Damping (WTDTA1)
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_592 | 3 Phase fault on 2NAPTON (300538) 69 kV Bus a. Apply fault at the 2NAPTON (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_593 | 3 Phase fault on 2BLLMYTP (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_593 | 3 Phase fault on 2BLLMYTP (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_594 | 3 Phase fault on 2BLLMYTP (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2MILO (300654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_594 | 3 Phase fault on 2BLLMYTP (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2MILO (300654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_595 | 3 Phase fault on 2LAMRRLS (300648) 69 kV Bus a. Apply fault at the 2LAMRRLS (300648) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRRLS (300648) 69.0 kV to 2LAMRCTN (300655) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_595 | 3 Phase fault on 2LAMRRLS (300648) 69 kV Bus a. Apply fault at the 2LAMRRLS (300648) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRRLS (300648) 69.0 kV to 2LAMRCTN (300655) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_596 | 3 Phase fault on 2JASPER (300649) 69 kV Bus a. Apply fault at the 2JASPER (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_596 | 3 Phase fault on 2JASPER (300649) 69 kV Bus a. Apply fault at the 2JASPER (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_597 | 3 Phase fault on 2KENOMA (300650) 69 kV Bus a. Apply fault at the 2KENOMA (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_597 | 3 Phase fault on 2KENOMA (300650) 69 kV Bus a. Apply fault at the 2KENOMA (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_598 | 3 Phase fault on 2KENOMA (300650) 69 kV Bus a. Apply fault at the 2KENOMA (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV to 2LOCKWD (300676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_598 | 3 Phase fault on 2KENOMA (300650) 69 kV Bus a. Apply fault at the 2KENOMA (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV to 2LOCKWD (300676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_599 | 3 Phase fault on 2LAMR (300651) 69 kV Bus a. Apply fault at the 2LAMR (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_599 | 3 Phase fault on 2LAMR (300651) 69 kV Bus a. Apply fault at the 2LAMR (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_6 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_6 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_60 | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_60 | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_600 | 3 Phase fault on 2LAMR (300651) 69 kV Bus a. Apply fault at the 2LAMR (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_600 | 3 Phase fault on 2LAMR (300651) 69 kV Bus a. Apply fault at the 2LAMR (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_601 | 3 Phase fault on 2LAMRCTS (300652) 69 kV Bus a. Apply fault at the 2LAMRCTS (300652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRCTS (300652) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_601 | 3 Phase fault on 2LAMRCTS (300652) 69 kV Bus a. Apply fault at the 2LAMRCTS (300652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRCTS (300652) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_602 | 3 Phase fault on 2LAMRCTN (300655) 69 kV Bus a. Apply fault at the 2LAMRCTN (300655) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRCTN (300655) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_602 | 3 Phase fault on 2LAMRCTN (300655) 69 kV Bus a. Apply fault at the 2LAMRCTN (300655) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRCTN (300655) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_603 | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_603 | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_604 | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2CRESTH (300697) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_604 | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2CRESTH (300697) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_605 | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2PL GAP (300707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_605 | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 2PL GAP (300707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_606 | 3 Phase fault on 2BUTLERE (300690) 69 kV Bus a. Apply fault at the 2BUTLERE (300690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLERE (300690) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_606 | 3 Phase fault on 2BUTLERE (300690) 69 kV Bus a. Apply fault at the 2BUTLERE (300690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLERE (300690) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_607 | 3 Phase fault on 2METZ (300704) 69 kV Bus a. Apply fault at the 2METZ (300704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2METZ (300704) 69.0 kV to 2RICHHIL (300708) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_607 | 3 Phase fault on 2METZ (300704) 69 kV Bus a. Apply fault at the 2METZ (300704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2METZ (300704) 69.0 kV to 2RICHHIL (300708) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_608 | 3 Phase fault on 2PL GAP (300707) 69 kV Bus a. Apply fault at the 2PL GAP (300707) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PL GAP (300707) 69.0 kV to 2RICHHIL (300708) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_608 | 3 Phase fault on 2PL GAP (300707) 69 kV Bus a. Apply fault at the 2PL GAP (300707) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PL GAP (300707) 69.0 kV to 2RICHHIL (300708) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_609 | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_609 | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_61 | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_61 | 3 Phase fault on CIRCLE 3 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_610 | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_610 | 3 Phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_611 | 3 Phase fault on 5LAMAR (300794) 161 kV Bus a. Apply fault at the 5LAMAR (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_611 | 3 Phase fault on 5LAMAR (300794) 161 kV Bus a. Apply fault at the 5LAMAR (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_612 | 3 Phase fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_612 | 3 Phase fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_613 | 3 Phase fault on 5HARRSBRG (300953) 161 kV Bus a. Apply fault at the 5HARRSBRG (300953) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HARRSBRG (300953) 161.0 kV to GI92_POI (709200) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_613 | 3 Phase fault on 5HARRSBRG (300953) 161 kV Bus a. Apply fault at the 5HARRSBRG (300953) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HARRSBRG (300953) 161.0 kV to GI92_POI (709200) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_614 | 3 Phase fault on 5THMHLB4 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_614 | 3 Phase fault on 5THMHLB4 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_615 | 3 Phase fault on 5THMHLB4 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_615 | 3 Phase fault on 5THMHLB4 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_616 | 3 Phase fault on 5MCBAINB2 (301489) 161 kV Bus a. Apply fault at the 5MCBAINB2 (301489) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_616 | 3 Phase fault on 5MCBAINB2 (301489) 161 kV Bus a. Apply fault at the 5MCBAINB2 (301489) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_617 | 3 Phase fault on 5SHARSNV (301515) 161 kV Bus a. Apply fault at the 5SHARSNV (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_617 | 3 Phase fault on 5SHARSNV (301515) 161 kV Bus a. Apply fault at the 5SHARSNV (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_618 | 3 Phase fault on 2BEVIERTP (301623) 69 kV Bus a. Apply fault at the 2BEVIERTP (301623) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEVIERTP (301623) 69.0 kV to 2BEVIERLD (301624) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_618 | 3 Phase fault on 2BEVIERTP (301623) 69 kV Bus a. Apply fault at the 2BEVIERTP (301623) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEVIERTP (301623) 69.0 kV to 2BEVIERLD (301624) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_619 | 3 Phase fault on 7ZACHARY (344000) 345 kV Bus a. Apply fault at the 7ZACHARY (344000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ZACHARY (344000) 345.0 kV to 7HUGHES (344011) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_619 | 3 Phase fault on 7ZACHARY (344000) 345 kV Bus a. Apply fault at the 7ZACHARY (344000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ZACHARY (344000) 345.0 kV to 7HUGHES (344011) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_62 | 3 Phase fault on CITIES 3 (533414) 115 kV Bus a. Apply fault at the CITIES 3 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_62 | 3 Phase fault on CITIES 3 (533414) 115 kV Bus a. Apply fault at the CITIES 3 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_620 | 3 Phase fault on 7ZACHARY (344000) 345 kV Bus a. Apply fault at the 7ZACHARY (344000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ZACHARY (344000) 345.0 kV to J1025POI (345438) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_620 | 3 Phase fault on 7ZACHARY (344000) 345 kV Bus a. Apply fault at the 7ZACHARY (344000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ZACHARY (344000) 345.0 kV to J1025POI (345438) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_621 | 3 Phase fault on 7BELLEAU (344102) 345 kV Bus a. Apply fault at the 7BELLEAU (344102) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BELLEAU (344102) 345.0 kV to 7ENON_TP (344536) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_621 | 3 Phase fault on 7BELLEAU (344102) 345 kV Bus a. Apply fault at the 7BELLEAU (344102) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BELLEAU (344102) 345.0 kV to 7ENON_TP (344536) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_622 | 3 Phase fault on 5CALIF UE 1 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_622 | 3 Phase fault on 5CALIF UE 1 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_623 | 3 Phase fault on 7ENON_TP (344536) 345 kV Bus a. Apply fault at the 7ENON_TP (344536) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ENON_TP (344536) 345.0 kV to 7ROOTBEER (345217) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_623 | 3 Phase fault on 7ENON_TP (344536) 345 kV Bus a. Apply fault at the 7ENON_TP (344536) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ENON_TP (344536) 345.0 kV to 7ROOTBEER (345217) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_624 | 3 Phase fault on 5MAURER 1 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_624 | 3 Phase fault on 5MAURER 1 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_625 | 3 Phase fault on 5MCBAIN T (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_625 | 3 Phase fault on 5MCBAIN T (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_626 | 3 Phase fault on 7ROOTBEER (345217) 345 kV Bus a. Apply fault at the 7ROOTBEER (345217) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ROOTBEER (345217) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_626 | 3 Phase fault on 7ROOTBEER (345217) 345 kV Bus a. Apply fault at the 7ROOTBEER (345217) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ROOTBEER (345217) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_627 | 3 Phase fault on 5OVERTON (345409) 161 kV Bus a. Apply fault at the 5OVERTON (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_627 | 3 Phase fault on 5OVERTON (345409) 161 kV Bus a. Apply fault at the 5OVERTON (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_628 | 3 Phase fault on 7MAYWOOD (345435) 345 kV Bus a. Apply fault at the 7MAYWOOD (345435) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MAYWOOD (345435) 345.0 kV to J1025POI (345438) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_628 | 3 Phase fault on 7MAYWOOD (345435) 345 kV Bus a. Apply fault at the 7MAYWOOD (345435) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MAYWOOD (345435) 345.0 kV to J1025POI (345438) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_629 | 3 Phase fault on 2ADAIR 1 (346005) 69 kV Bus a. Apply fault at the 2ADAIR 1 (346005) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ADAIR 1 (346005) 69.0 kV to 2ADAIR 2 (346006) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_629 | 3 Phase fault on 2ADAIR 1 (346005) 69 kV Bus a. Apply fault at the 2ADAIR 1 (346005) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ADAIR 1 (346005) 69.0 kV to 2ADAIR 2 (346006) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_63 | 3 Phase fault on COLINE 3 (533153) 115 kV Bus a. Apply fault at the COLINE 3 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_63 | 3 Phase fault on COLINE 3 (533153) 115 kV Bus a. Apply fault at the COLINE 3 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_630 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_630 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_631 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_631 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_632 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_632 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_633 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_633 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_634 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_634 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_635 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_635 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_636 | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_636 | 3 Phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_637 | 3 Phase fault on MOSCOW 2 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_637 | 3 Phase fault on MOSCOW 2 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_638 | 3 Phase fault on MOSCOWT2 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_638 | 3 Phase fault on MOSCOWT2 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_639 | 3 Phase fault on NORTH6 2 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_639 | 3 Phase fault on NORTH6 2 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_64 | 3 Phase fault on COLINE 3 (533153) 115 kV Bus a. Apply fault at the COLINE 3 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_64 | 3 Phase fault on COLINE 3 (533153) 115 kV Bus a. Apply fault at the COLINE 3 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_640 | 3 Phase fault on NORTH6T2 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_640 | 3 Phase fault on NORTH6T2 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_641 | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to SUBLETE3 (531398) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_641 | 3 Phase fault on PIONTAP3 (531392) 115 kV Bus a. Apply fault at the PIONTAP3 (531392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to SUBLETE3 (531398) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_642 | 3 Phase fault on ROLLA 2 (531395) 115 kV Bus a. Apply fault at the ROLLA 2 (531395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLA 2 (531395) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_642 | 3 Phase fault on ROLLA 2 (531395) 115 kV Bus a. Apply fault at the ROLLA 2 (531395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLA 2 (531395) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_643 | 3 Phase fault on WALKMYR2 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_643 | 3 Phase fault on WALKMYR2 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_644 | 3 Phase fault on MOSCCMS2 (531454) 69 kV Bus a. Apply fault at the MOSCCMS2 (531454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCCMS2 (531454) 69.0 kV to CMSSWRD2 (531466) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_644 | 3 Phase fault on MOSCCMS2 (531454) 69 kV Bus a. Apply fault at the MOSCCMS2 (531454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCCMS2 (531454) 69.0 kV to CMSSWRD2 (531466) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_645 | 3 Phase fault on SANTCMS2 (531463) 69 kV Bus a. Apply fault at the SANTCMS2 (531463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANTCMS2 (531463) 69.0 kV to CMSSWRD2 (531466) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_645 | 3 Phase fault on SANTCMS2 (531463) 69 kV Bus a. Apply fault at the SANTCMS2 (531463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANTCMS2 (531463) 69.0 kV to CMSSWRD2 (531466) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_646 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_646 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_647 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_647 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_648 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_648 | 3 Phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_649 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_649 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_65 | 3 Phase fault on DAVIS 3 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_65 | 3 Phase fault on DAVIS 3 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_650 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_650 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_651 | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_651 | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_652 | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_652 | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_653 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_653 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_654 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_654 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_655 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_655 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_656 | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_656 | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_657 | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_657 | 3 Phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_658 | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_658 | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_659 | 3 Phase fault on NEPARSN4 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_659 | 3 Phase fault on NEPARSN4 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_66 | 3 Phase fault on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_66 | 3 Phase fault on EMCPHER3 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_660 | 3 Phase fault on NEOSHOS4 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_660 | 3 Phase fault on NEOSHOS4 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_661 | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_661 | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_662 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_662 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_663 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_663 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_664 | 3 Phase fault on GILL E 4 (533044) 138 kV Bus a. Apply fault at the GILL E 4 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_664 | 3 Phase fault on GILL E 4 (533044) 138 kV Bus a. Apply fault at the GILL E 4 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_665 | 3 Phase fault on GILL W 4 (533045) 138 kV Bus a. Apply fault at the GILL W 4 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_665 | 3 Phase fault on GILL W 4 (533045) 138 kV Bus a. Apply fault at the GILL W 4 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_666 | 3 Phase fault on GILL W 4 (533045) 138 kV Bus a. Apply fault at the GILL W 4 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_666 | 3 Phase fault on GILL W 4 (533045) 138 kV Bus a. Apply fault at the GILL W 4 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_667 | 3 Phase fault on GILL S 4 (533046) 138 kV Bus a. Apply fault at the GILL S 4 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_667 | 3 Phase fault on GILL S 4 (533046) 138 kV Bus a. Apply fault at the GILL S 4 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_668 | 3 Phase fault on WACO S 4 (533071) 138 kV Bus a. Apply fault at the WACO S 4 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_668 | 3 Phase fault on WACO S 4 (533071) 138 kV Bus a. Apply fault at the WACO S 4 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_669 | 3 Phase fault on WACO 4 (533072) 138 kV Bus a. Apply fault at the WACO 4 (533072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_669 | 3 Phase fault on WACO 4 (533072) 138 kV Bus a. Apply fault at the WACO 4 (533072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_67 | 3 Phase fault on FT JCT 3 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_67 | 3 Phase fault on FT JCT 3 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_670 | 3 Phase fault on TECHILW3 (533181) 115 kV Bus a. Apply fault at the TECHILW3 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_670 | 3 Phase fault on TECHILW3 (533181) 115 kV Bus a. Apply fault at the TECHILW3 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_671 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_671 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_672 | 3 Phase fault on AEC 3 (533361) 115 kV Bus a. Apply fault at the AEC 3 (533361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_672 | 3 Phase fault on AEC 3 (533361) 115 kV Bus a. Apply fault at the AEC 3 (533361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_673 | 3 Phase fault on BERG 3 (533367) 115 kV Bus a. Apply fault at the BERG 3 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_673 | 3 Phase fault on BERG 3 (533367) 115 kV Bus a. Apply fault at the BERG 3 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_674 | 3 Phase fault on BERG 3 (533367) 115 kV Bus a. Apply fault at the BERG 3 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_674 | 3 Phase fault on BERG 3 (533367) 115 kV Bus a. Apply fault at the BERG 3 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_675 | 3 Phase fault on NORTHVW3 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_675 | 3 Phase fault on NORTHVW3 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_676 | 3 Phase fault on MOUNDRG3 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_676 | 3 Phase fault on MOUNDRG3 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_677 | 3 Phase fault on LABETTE2 (533695) 69 kV Bus a. Apply fault at the LABETTE2 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_677 | 3 Phase fault on LABETTE2 (533695) 69 kV Bus a. Apply fault at the LABETTE2 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_678 | 3 Phase fault on ORDNCE 2 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_678 | 3 Phase fault on ORDNCE 2 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_679 | 3 Phase fault on NEOSHON2 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_679 | 3 Phase fault on NEOSHON2 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_68 | 3 Phase fault on FT JCT 3 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_68 | 3 Phase fault on FT JCT 3 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_680 | 3 Phase fault on HOOVERN2 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_680 | 3 Phase fault on HOOVERN2 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_681 | 3 Phase fault on HOOVERS2 (533806) 69 kV Bus a. Apply fault at the HOOVERS2 (533806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_681 | 3 Phase fault on HOOVERS2 (533806) 69 kV Bus a. Apply fault at the HOOVERS2 (533806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_682 | 3 Phase fault on PLAZA E2 (533829) 69 kV Bus a. Apply fault at the PLAZA E2 (533829) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_682 | 3 Phase fault on PLAZA E2 (533829) 69 kV Bus a. Apply fault at the PLAZA E2 (533829) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_683 | 3 Phase fault on PLAZA M2 (533857) 69 kV Bus a. Apply fault at the PLAZA M2 (533857) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_683 | 3 Phase fault on PLAZA M2 (533857) 69 kV Bus a. Apply fault at the PLAZA M2 (533857) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_684 | 3 Phase fault on E-LIBER3 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to E-PINE 3 (539690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_684 | 3 Phase fault on E-LIBER3 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to E-PINE 3 (539690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_685 | 3 Phase fault on W-LIBER3 (539700) 115 kV Bus a. Apply fault at the W-LIBER3 (539700) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-LIBER3 (539700) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_685 | 3 Phase fault on W-LIBER3 (539700) 115 kV Bus a. Apply fault at the W-LIBER3 (539700) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-LIBER3 (539700) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_686 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_686 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_687 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_687 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_688 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_688 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_689 | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_689 | 3 Phase fault on IRONWOOD7 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_69 | 3 Phase fault on FT JCT 3 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_69 | 3 Phase fault on FT JCT 3 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_690 | 3 Phase fault on ELMCREEK7 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_690 | 3 Phase fault on ELMCREEK7 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_691 | 3 Phase fault on CLNTPLT_CAP2 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP2 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_691 | 3 Phase fault on CLNTPLT_CAP2 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP2 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_692 | 3 Phase fault on FROSTRD_CAP5 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_692 | 3 Phase fault on FROSTRD_CAP5 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_693 | 3 Phase fault on NASHUA_CAP5 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_693 | 3 Phase fault on NASHUA_CAP5 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_694 | 3 Phase fault on RNRIDGE_CAP5 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_694 | 3 Phase fault on RNRIDGE_CAP5 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_695 | 3 Phase fault on SEDLIAW_CAP5 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_695 | 3 Phase fault on SEDLIAW_CAP5 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_696 | 3 Phase fault on WSTELEC_CAP5 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_696 | 3 Phase fault on WSTELEC_CAP5 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_697 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_697 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_698 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_698 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_699 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_699 | 3 Phase fault on MULLNCR7 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_7 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_7 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_70 | 3 Phase fault on MCDOWEL3 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_70 | 3 Phase fault on MCDOWEL3 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_700 | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_700 | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_701 | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_701 | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_702 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_702 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_703 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_703 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_704 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_704 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_705 | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_705 | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_706 | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_706 | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_707 | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_707 | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_708 | 3 Phase fault on SIBLEY 5 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_708 | 3 Phase fault on SIBLEY 5 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_709 | 3 Phase fault on NASHUA 5 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_709 | 3 Phase fault on NASHUA 5 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_71 | 3 Phase fault on JARBALO3 (533244) 115 kV Bus a. Apply fault at the JARBALO3 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_71 | 3 Phase fault on JARBALO3 (533244) 115 kV Bus a. Apply fault at the JARBALO3 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_710 | 3 Phase fault on NASHUA 5 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_710 | 3 Phase fault on NASHUA 5 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_711 | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_711 | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_712 | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_712 | 3 Phase fault on ARCHIE 5 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_713 | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_713 | 3 Phase fault on SEDALIA5 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_714 | 3 Phase fault on MARTCTY5 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_714 | 3 Phase fault on MARTCTY5 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_715 | 3 Phase fault on MARTCTY5 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_715 | 3 Phase fault on MARTCTY5 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_716 | 3 Phase fault on MARTCTY5 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_716 | 3 Phase fault on MARTCTY5 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_717 | 3 Phase fault on RAYTOWN5 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_717 | 3 Phase fault on RAYTOWN5 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_718 | 3 Phase fault on FROSTRD5 (541220) 161 kV Bus a. Apply fault at the FROSTRD5 (541220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_718 | 3 Phase fault on FROSTRD5 (541220) 161 kV Bus a. Apply fault at the FROSTRD5 (541220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_719 | 3 Phase fault on WSTELEC5 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_719 | 3 Phase fault on WSTELEC5 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_72 | 3 Phase fault on JARBALO3 (533244) 115 kV Bus a. Apply fault at the JARBALO3 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_72 | 3 Phase fault on JARBALO3 (533244) 115 kV Bus a. Apply fault at the JARBALO3 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_720 | 3 Phase fault on GRDVWE 5 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_720 | 3 Phase fault on GRDVWE 5 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_721 | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_721 | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_722 | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_722 | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_723 | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_723 | 3 Phase fault on PHILL 5 (541225) 161 kV Bus a. Apply fault at the PHILL 5 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_724 | 3 Phase fault on RNRIDGE5 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_724 | 3 Phase fault on RNRIDGE5 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_725 | 3 Phase fault on RNRIDGE5 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_725 | 3 Phase fault on RNRIDGE5 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_726 | 3 Phase fault on RNRIDGE5 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_726 | 3 Phase fault on RNRIDGE5 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_727 | 3 Phase fault on G17-186-TAP (541231) 161 kV Bus a. Apply fault at the G17-186-TAP (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-TAP (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_727 | 3 Phase fault on G17-186-TAP (541231) 161 kV Bus a. Apply fault at the G17-186-TAP (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-TAP (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_728 | 3 Phase fault on G17-186-TAP (541231) 161 kV Bus a. Apply fault at the G17-186-TAP (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-TAP (541231) 161.0 kV to NRAYMORE (541317) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_728 | 3 Phase fault on G17-186-TAP (541231) 161 kV Bus a. Apply fault at the G17-186-TAP (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-TAP (541231) 161.0 kV to NRAYMORE (541317) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_729 | 3 Phase fault on SEDEAST5 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_729 | 3 Phase fault on SEDEAST5 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_73 | 3 Phase fault on KELLY 3 (533217) 115 kV Bus a. Apply fault at the KELLY 3 (533217) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 3 (533217) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_73 | 3 Phase fault on KELLY 3 (533217) 115 kV Bus a. Apply fault at the KELLY 3 (533217) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 3 (533217) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_730 | 3 Phase fault on LBRTYST5 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_730 | 3 Phase fault on LBRTYST5 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_731 | 3 Phase fault on LNGVW 2 (541282) 69 kV Bus a. Apply fault at the LNGVW 2 (541282) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to BRMALL 2 (541283) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_731 | 3 Phase fault on LNGVW 2 (541282) 69 kV Bus a. Apply fault at the LNGVW 2 (541282) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to BRMALL 2 (541283) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_732 | 3 Phase fault on CLNTPLT2 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_732 | 3 Phase fault on CLNTPLT2 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_733 | 3 Phase fault on NEVPLT 2 (541307) 69 kV Bus a. Apply fault at the NEVPLT 2 (541307) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVPLT 2 (541307) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_733 | 3 Phase fault on NEVPLT 2 (541307) 69 kV Bus a. Apply fault at the NEVPLT 2 (541307) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVPLT 2 (541307) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_734 | 3 Phase fault on NEVPLT 2 (541307) 69 kV Bus a. Apply fault at the NEVPLT 2 (541307) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVPLT 2 (541307) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_734 | 3 Phase fault on NEVPLT 2 (541307) 69 kV Bus a. Apply fault at the NEVPLT 2 (541307) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVPLT 2 (541307) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_735 | 3 Phase fault on NEVPLT 2 (541307) 69 kV Bus a. Apply fault at the NEVPLT 2 (541307) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVPLT 2 (541307) 69.0 kV to NEVJCT 2 (541311) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_735 | 3 Phase fault on NEVPLT 2 (541307) 69 kV Bus a. Apply fault at the NEVPLT 2 (541307) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVPLT 2 (541307) 69.0 kV to NEVJCT 2 (541311) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_736 | 3 Phase fault on METZ 2 (541309) 69 kV Bus a. Apply fault at the METZ 2 (541309) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. METZ 2 (541309) 69.0 kV to 3M 2 (541310) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_736 | 3 Phase fault on METZ 2 (541309) 69 kV Bus a. Apply fault at the METZ 2 (541309) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. METZ 2 (541309) 69.0 kV to 3M 2 (541310) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_737 | 3 Phase fault on NEVJCT 2 (541311) 69 kV Bus a. Apply fault at the NEVJCT 2 (541311) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVJCT 2 (541311) 69.0 kV to SHELDON_69 (541499) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_737 | 3 Phase fault on NEVJCT 2 (541311) 69 kV Bus a. Apply fault at the NEVJCT 2 (541311) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVJCT 2 (541311) 69.0 kV to SHELDON_69 (541499) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_738 | 3 Phase fault on LAMAR 2 (541312) 69 kV Bus a. Apply fault at the LAMAR 2 (541312) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR 2 (541312) 69.0 kV to SHELDON_69 (541499) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_738 | 3 Phase fault on LAMAR 2 (541312) 69 kV Bus a. Apply fault at the LAMAR 2 (541312) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR 2 (541312) 69.0 kV to SHELDON_69 (541499) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_739 | 3 Phase fault on NRAYMORE (541317) 161 kV Bus a. Apply fault at the NRAYMORE (541317) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_739 | 3 Phase fault on NRAYMORE (541317) 161 kV Bus a. Apply fault at the NRAYMORE (541317) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_74 | 3 Phase fault on KERFORD3 (533216) 115 kV Bus a. Apply fault at the KERFORD3 (533216) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_74 | 3 Phase fault on KERFORD3 (533216) 115 kV Bus a. Apply fault at the KERFORD3 (533216) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_740 | 3 Phase fault on IATAN5 (541350) 161 kV Bus a. Apply fault at the IATAN5 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_740 | 3 Phase fault on IATAN5 (541350) 161 kV Bus a. Apply fault at the IATAN5 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_741 | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_741 | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_742 | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_742 | 3 Phase fault on HOLT 7 (541510) 345 kV Bus a. Apply fault at the HOLT 7 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_743 | 3 Phase fault on LAC_LAKE_2 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_743 | 3 Phase fault on LAC_LAKE_2 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_744 | 3 Phase fault on BARRY_CAP 5 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_744 | 3 Phase fault on BARRY_CAP 5 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_745 | 3 Phase fault on CRAIG_CAP 5 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_745 | 3 Phase fault on CRAIG_CAP 5 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_746 | 3 Phase fault on GLADSTN_CAP5 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_746 | 3 Phase fault on GLADSTN_CAP5 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_747 | 3 Phase fault on MERRIAM_CAP5 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM_CAP5 (542947) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_747 | 3 Phase fault on MERRIAM_CAP5 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM_CAP5 (542947) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_748 | 3 Phase fault on NEASTS_CAP5 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_748 | 3 Phase fault on NEASTS_CAP5 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_749 | 3 Phase fault on STHTOWN_CAP5 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN_CAP5 (542950) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_749 | 3 Phase fault on STHTOWN_CAP5 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN_CAP5 (542950) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_75 | 3 Phase fault on MANVILE3 (533426) 115 kV Bus a. Apply fault at the MANVILE3 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_75 | 3 Phase fault on MANVILE3 (533426) 115 kV Bus a. Apply fault at the MANVILE3 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_750 | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_750 | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_751 | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_751 | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_752 | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_752 | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_753 | 3 Phase fault on WGARDNR5 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_753 | 3 Phase fault on WGARDNR5 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_754 | 3 Phase fault on WGARDNR5 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_754 | 3 Phase fault on WGARDNR5 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_755 | 3 Phase fault on WGARDNR5 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_755 | 3 Phase fault on WGARDNR5 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | No | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) High End of Sim Voltage (Near Faulted Bus) - VOLT 543055 [SEOTTWA5 161.00] - VOLT 543077 [PLSTVAL5 161.00] - VOLT 543166 [NEASTOTTW5 161.00] - VOLT 762405 [ASG-2018-010161.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_756 | 3 Phase fault on WGARDNR5 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_756 | 3 Phase fault on WGARDNR5 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_757 | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_757 | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_758 | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_758 | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_759 | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_759 | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_76 | 3 Phase fault on REFINRY3 (533427) 115 kV Bus a. Apply fault at the REFINRY3 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_76 | 3 Phase fault on REFINRY3 (533427) 115 kV Bus a. Apply fault at the REFINRY3 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_760 | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_760 | 3 Phase fault on STILWEL5 (542969) 161 kV Bus a. Apply fault at the STILWEL5 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_761 | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_761 | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_762 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_762 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_763 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_763 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_764 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_764 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_765 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_765 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_766 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_766 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_767 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_767 | 3 Phase fault on HAWTHS5 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_768 | 3 Phase fault on LEVEE 5 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_768 | 3 Phase fault on LEVEE 5 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_769 | 3 Phase fault on LEVEE 5 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_769 | 3 Phase fault on LEVEE 5 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_77 | 3 Phase fault on MCPHER 3 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_77 | 3 Phase fault on MCPHER 3 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_770 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Low End of Sim Voltage (Near Faulted Bus) - VOLT 539640 [HAYNE3 115.00] - VOLT 539672 [E-LIBER3 115.00] - VOLT 539690 [E-PINE 3 115.00] - VOLT 539700 [W-LIBER3 115.00] - VOLT 539737 [NLIB 3 115.00] - VOLT 539751 [NATBEEF3 115.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Steady State issue in load pocket, unrelated to CQ.
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_770 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_771 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_771 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_772 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_772 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_773 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_773 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_774 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_774 | 3 Phase fault on CRAIG 5 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_775 | 3 Phase fault on PFLUMM 5 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_775 | 3 Phase fault on PFLUMM 5 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_776 | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_776 | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_777 | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_777 | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_778 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_778 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_779 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_779 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_78 | 3 Phase fault on MIDLADN3 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_78 | 3 Phase fault on MIDLADN3 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_780 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_780 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_781 | 3 Phase fault on NEASTS5 (542985) 161 kV Bus a. Apply fault at the NEASTS5 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_781 | 3 Phase fault on NEASTS5 (542985) 161 kV Bus a. Apply fault at the NEASTS5 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_782 | 3 Phase fault on NEASTS5 (542985) 161 kV Bus a. Apply fault at the NEASTS5 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_782 | 3 Phase fault on NEASTS5 (542985) 161 kV Bus a. Apply fault at the NEASTS5 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_783 | 3 Phase fault on TROOST 5 (542986) 161 kV Bus a. Apply fault at the TROOST 5 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_783 | 3 Phase fault on TROOST 5 (542986) 161 kV Bus a. Apply fault at the TROOST 5 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_784 | 3 Phase fault on TROOST 5 (542986) 161 kV Bus a. Apply fault at the TROOST 5 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_784 | 3 Phase fault on TROOST 5 (542986) 161 kV Bus a. Apply fault at the TROOST 5 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_785 | 3 Phase fault on GRAND 5 (542987) 161 kV Bus a. Apply fault at the GRAND 5 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_785 | 3 Phase fault on GRAND 5 (542987) 161 kV Bus a. Apply fault at the GRAND 5 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_786 | 3 Phase fault on GRAND 5 (542987) 161 kV Bus a. Apply fault at the GRAND 5 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_786 | 3 Phase fault on GRAND 5 (542987) 161 kV Bus a. Apply fault at the GRAND 5 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_787 | 3 Phase fault on GRAND W5 (542988) 161 kV Bus a. Apply fault at the GRAND W5 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_787 | 3 Phase fault on GRAND W5 (542988) 161 kV Bus a. Apply fault at the GRAND W5 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_788 | 3 Phase fault on GRAND W5 (542988) 161 kV Bus a. Apply fault at the GRAND W5 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_788 | 3 Phase fault on GRAND W5 (542988) 161 kV Bus a. Apply fault at the GRAND W5 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_789 | 3 Phase fault on CROSTWN5 (542990) 161 kV Bus a. Apply fault at the CROSTWN5 (542990) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSTWN5 (542990) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_789 | 3 Phase fault on CROSTWN5 (542990) 161 kV Bus a. Apply fault at the CROSTWN5 (542990) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSTWN5 (542990) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_79 | 3 Phase fault on NORTHVW3 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_79 | 3 Phase fault on NORTHVW3 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_790 | 3 Phase fault on BENDIX 5 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_790 | 3 Phase fault on BENDIX 5 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_791 | 3 Phase fault on BENDIX 5 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_791 | 3 Phase fault on BENDIX 5 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_792 | 3 Phase fault on STHTOWN5 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_792 | 3 Phase fault on STHTOWN5 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_793 | 3 Phase fault on STHTOWN5 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_793 | 3 Phase fault on STHTOWN5 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_794 | 3 Phase fault on STHTOWN5 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_794 | 3 Phase fault on STHTOWN5 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_795 | 3 Phase fault on MIDTOWN5 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_795 | 3 Phase fault on MIDTOWN5 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_796 | 3 Phase fault on MIDTOWN5 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_796 | 3 Phase fault on MIDTOWN5 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_797 | 3 Phase fault on LVISTA 5 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_797 | 3 Phase fault on LVISTA 5 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_798 | 3 Phase fault on BLUEVLY5 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_798 | 3 Phase fault on BLUEVLY5 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_799 | 3 Phase fault on BLUEVLY5 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_799 | 3 Phase fault on BLUEVLY5 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_8 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_8 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_80 | 3 Phase fault on NW LEAV3 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_80 | 3 Phase fault on NW LEAV3 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_800 | 3 Phase fault on CHOUTEU5 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_800 | 3 Phase fault on CHOUTEU5 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_801 | 3 Phase fault on SWAVCAP5 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_801 | 3 Phase fault on SWAVCAP5 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_802 | 3 Phase fault on AVONDAL5 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_802 | 3 Phase fault on AVONDAL5 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_803 | 3 Phase fault on AVONDAL5 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_803 | 3 Phase fault on AVONDAL5 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_804 | 3 Phase fault on GLADSTN5 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_804 | 3 Phase fault on GLADSTN5 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_805 | 3 Phase fault on WETHRBY5 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_805 | 3 Phase fault on WETHRBY5 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_806 | 3 Phase fault on NKANCTY5 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_806 | 3 Phase fault on NKANCTY5 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_807 | 3 Phase fault on BRMGHAM5 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_807 | 3 Phase fault on BRMGHAM5 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_808 | 3 Phase fault on NASHUA-5 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_808 | 3 Phase fault on NASHUA-5 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_809 | 3 Phase fault on SHWNMSN5 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_809 | 3 Phase fault on SHWNMSN5 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_81 | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_81 | 3 Phase fault on RENO 3 (533416) 115 kV Bus a. Apply fault at the RENO 3 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_810 | 3 Phase fault on SHWNMSN5 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_810 | 3 Phase fault on SHWNMSN5 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_811 | 3 Phase fault on MERRIAM5 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_811 | 3 Phase fault on MERRIAM5 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_812 | 3 Phase fault on BRKRIDG5 (543033) 161 kV Bus a. Apply fault at the BRKRIDG5 (543033) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKRIDG5 (543033) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_812 | 3 Phase fault on BRKRIDG5 (543033) 161 kV Bus a. Apply fault at the BRKRIDG5 (543033) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKRIDG5 (543033) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_813 | 3 Phase fault on KNLWRTH5 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_813 | 3 Phase fault on KNLWRTH5 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_814 | 3 Phase fault on OLATHE 5 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_814 | 3 Phase fault on OLATHE 5 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_815 | 3 Phase fault on OLATHE 5 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_815 | 3 Phase fault on OLATHE 5 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_816 | 3 Phase fault on QUARRY 5 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_816 | 3 Phase fault on QUARRY 5 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_817 | 3 Phase fault on QUARRY 5 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_817 | 3 Phase fault on QUARRY 5 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_818 | 3 Phase fault on MOONLT 5 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_818 | 3 Phase fault on MOONLT 5 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_819 | 3 Phase fault on SEOTTWA5 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_819 | 3 Phase fault on SEOTTWA5 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_82 | 3 Phase fault on SENECA 3 (533337) 115 kV Bus a. Apply fault at the SENECA 3 (533337) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SENECA 3 (533337) 115.0 kV to TCSENCA3 (533348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_82 | 3 Phase fault on SENECA 3 (533337) 115 kV Bus a. Apply fault at the SENECA 3 (533337) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SENECA 3 (533337) 115.0 kV to TCSENCA3 (533348) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_820 | 3 Phase fault on SEOTTWA5 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_820 | 3 Phase fault on SEOTTWA5 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_821 | 3 Phase fault on SEOTTWA5 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_821 | 3 Phase fault on SEOTTWA5 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_822 | 3 Phase fault on BUCYRUS5 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_822 | 3 Phase fault on BUCYRUS5 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_823 | 3 Phase fault on MALTABN5 (543059) 161 kV Bus a. Apply fault at the MALTABN5 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_823 | 3 Phase fault on MALTABN5 (543059) 161 kV Bus a. Apply fault at the MALTABN5 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_824 | 3 Phase fault on MALTABN5 (543059) 161 kV Bus a. Apply fault at the MALTABN5 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_824 | 3 Phase fault on MALTABN5 (543059) 161 kV Bus a. Apply fault at the MALTABN5 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_825 | 3 Phase fault on SALSBRY5 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_825 | 3 Phase fault on SALSBRY5 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_826 | 3 Phase fault on CNTRVIL5 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_826 | 3 Phase fault on CNTRVIL5 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_827 | 3 Phase fault on CNTRVIL5 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_827 | 3 Phase fault on CNTRVIL5 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_828 | 3 Phase fault on S.OTTWA5 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_828 | 3 Phase fault on S.OTTWA5 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_829 | 3 Phase fault on CENTENL5 (543067) 161 kV Bus a. Apply fault at the CENTENL5 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_829 | 3 Phase fault on CENTENL5 (543067) 161 kV Bus a. Apply fault at the CENTENL5 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_83 | 3 Phase fault on STRANGR3 (533268) 115 kV Bus a. Apply fault at the STRANGR3 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_83 | 3 Phase fault on STRANGR3 (533268) 115 kV Bus a. Apply fault at the STRANGR3 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_830 | 3 Phase fault on CENTENL5 (543067) 161 kV Bus a. Apply fault at the CENTENL5 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_830 | 3 Phase fault on CENTENL5 (543067) 161 kV Bus a. Apply fault at the CENTENL5 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_831 | 3 Phase fault on WEST---5 (543070) 161 kV Bus a. Apply fault at the WEST---5 (543070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST---5 (543070) 161.0 kV to S EAST 5 (543071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_831 | 3 Phase fault on WEST---5 (543070) 161 kV Bus a. Apply fault at the WEST---5 (543070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST---5 (543070) 161.0 kV to S EAST 5 (543071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_832 | 3 Phase fault on WEST---5 (543070) 161 kV Bus a. Apply fault at the WEST---5 (543070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST---5 (543070) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_832 | 3 Phase fault on WEST---5 (543070) 161 kV Bus a. Apply fault at the WEST---5 (543070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST---5 (543070) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_833 | 3 Phase fault on S EAST 5 (543071) 161 kV Bus a. Apply fault at the S EAST 5 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_833 | 3 Phase fault on S EAST 5 (543071) 161 kV Bus a. Apply fault at the S EAST 5 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_834 | 3 Phase fault on MRSHLJT5 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_834 | 3 Phase fault on MRSHLJT5 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_835 | 3 Phase fault on OSAWAT 5 (543112) 161 kV Bus a. Apply fault at the OSAWAT 5 (543112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWAT 5 (543112) 161.0 kV to OSAWTM_CAP5 (543135) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_835 | 3 Phase fault on OSAWAT 5 (543112) 161 kV Bus a. Apply fault at the OSAWAT 5 (543112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWAT 5 (543112) 161.0 kV to OSAWTM_CAP5 (543135) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_836 | 3 Phase fault on SUGRCRK_S2 (543163) 69 kV Bus a. Apply fault at the SUGRCRK_S2 (543163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_S2 (543163) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_836 | 3 Phase fault on SUGRCRK_S2 (543163) 69 kV Bus a. Apply fault at the SUGRCRK_S2 (543163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_S2 (543163) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_837 | 3 Phase fault on ROSEDALE 5 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_837 | 3 Phase fault on ROSEDALE 5 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_838 | 3 Phase fault on ROSEDALE 5 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_838 | 3 Phase fault on ROSEDALE 5 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_839 | 3 Phase fault on MILLST 5 (546224) 161 kV Bus a. Apply fault at the MILLST 5 (546224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_839 | 3 Phase fault on MILLST 5 (546224) 161 kV Bus a. Apply fault at the MILLST 5 (546224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_84 | 3 Phase fault on TECHILW3 (533181) 115 kV Bus a. Apply fault at the TECHILW3 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_84 | 3 Phase fault on TECHILW3 (533181) 115 kV Bus a. Apply fault at the TECHILW3 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_840 | 3 Phase fault on SPEAKER2 (546674) 69 kV Bus a. Apply fault at the SPEAKER2 (546674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_840 | 3 Phase fault on SPEAKER2 (546674) 69 kV Bus a. Apply fault at the SPEAKER2 (546674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_841 | 3 Phase fault on KAW 2 (546678) 69 kV Bus a. Apply fault at the KAW 2 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to EVERETT2 (546682) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_841 | 3 Phase fault on KAW 2 (546678) 69 kV Bus a. Apply fault at the KAW 2 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to EVERETT2 (546682) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_842 | 3 Phase fault on KAW 2 (546678) 69 kV Bus a. Apply fault at the KAW 2 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_842 | 3 Phase fault on KAW 2 (546678) 69 kV Bus a. Apply fault at the KAW 2 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_843 | 3 Phase fault on KAW 2 (546678) 69 kV Bus a. Apply fault at the KAW 2 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_843 | 3 Phase fault on KAW 2 (546678) 69 kV Bus a. Apply fault at the KAW 2 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_844 | 3 Phase fault on MUNCIE 2 (546681) 69 kV Bus a. Apply fault at the MUNCIE 2 (546681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNCIE 2 (546681) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_844 | 3 Phase fault on MUNCIE 2 (546681) 69 kV Bus a. Apply fault at the MUNCIE 2 (546681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNCIE 2 (546681) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_845 | 3 Phase fault on MUNCIE 2 (546681) 69 kV Bus a. Apply fault at the MUNCIE 2 (546681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNCIE 2 (546681) 69.0 kV to QUINDA 2 (546692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_845 | 3 Phase fault on MUNCIE 2 (546681) 69 kV Bus a. Apply fault at the MUNCIE 2 (546681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNCIE 2 (546681) 69.0 kV to QUINDA 2 (546692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_846 | 3 Phase fault on WWR477 (547459) 161 kV Bus a. Apply fault at the WWR477 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_846 | 3 Phase fault on WWR477 (547459) 161 kV Bus a. Apply fault at the WWR477 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_847 | 3 Phase fault on ORO110 5 (547467) 161 kV Bus a. Apply fault at the ORO110 5 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_847 | 3 Phase fault on ORO110 5 (547467) 161 kV Bus a. Apply fault at the ORO110 5 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_848 | 3 Phase fault on ORO110 5 (547467) 161 kV Bus a. Apply fault at the ORO110 5 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_848 | 3 Phase fault on ORO110 5 (547467) 161 kV Bus a. Apply fault at the ORO110 5 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_849 | 3 Phase fault on RIV4525 (547469) 161 kV Bus a. Apply fault at the RIV4525 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_849 | 3 Phase fault on RIV4525 (547469) 161 kV Bus a. Apply fault at the RIV4525 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_85 | 3 Phase fault on MEAD S 2 (533815) 69 kV Bus a. Apply fault at the MEAD S 2 (533815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_85 | 3 Phase fault on MEAD S 2 (533815) 69 kV Bus a. Apply fault at the MEAD S 2 (533815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_850 | 3 Phase fault on RIV4525 (547469) 161 kV Bus a. Apply fault at the RIV4525 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_850 | 3 Phase fault on RIV4525 (547469) 161 kV Bus a. Apply fault at the RIV4525 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_851 | 3 Phase fault on HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_851 | 3 Phase fault on HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_852 | 3 Phase fault on RIV167 2 (547541) 69 kV Bus a. Apply fault at the RIV167 2 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_852 | 3 Phase fault on RIV167 2 (547541) 69 kV Bus a. Apply fault at the RIV167 2 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_853 | 3 Phase fault on RIV167 2 (547541) 69 kV Bus a. Apply fault at the RIV167 2 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_853 | 3 Phase fault on RIV167 2 (547541) 69 kV Bus a. Apply fault at the RIV167 2 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_854 | 3 Phase fault on LAMAR7 (599950) 345 kV Bus a. Apply fault at the LAMAR7 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G18-030-TAP (762662) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_854 | 3 Phase fault on LAMAR7 (599950) 345 kV Bus a. Apply fault at the LAMAR7 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G18-030-TAP (762662) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_855 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_855 | 3 Phase fault on ATCHSN 3 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_856 | 3 Phase fault on HILLS-DT-RX3 (636399) 345 kV Bus a. Apply fault at the HILLS-DT-RX3 (636399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS-DT-RX3 (636399) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_856 | 3 Phase fault on HILLS-DT-RX3 (636399) 345 kV Bus a. Apply fault at the HILLS-DT-RX3 (636399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HILLS-DT-RX3 (636399) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_857 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_857 | 3 Phase fault on COOPER 3 (640139) 345 kV Bus a. Apply fault at the COOPER 3 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_858 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_858 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_859 | 3 Phase fault on GI94_POI (709400) 345 kV Bus a. Apply fault at the GI94_POI (709400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_859 | 3 Phase fault on GI94_POI (709400) 345 kV Bus a. Apply fault at the GI94_POI (709400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_86 | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_86 | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_860 | 3 Phase fault on HAWTH 2 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_860 | 3 Phase fault on HAWTH 2 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_861 | 3 Phase fault on HAWTH 2 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT12_2 (543664) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_861 | 3 Phase fault on HAWTH 2 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT12_2 (543664) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_862 | 3 Phase fault on 7KINGDM (300043) 345 kV Bus a. Apply fault at the 7KINGDM (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5KINGDMB1 (300090) 161.0 kV to 7KINGDM (300043) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_862 | 3 Phase fault on 7KINGDM (300043) 345 kV Bus a. Apply fault at the 7KINGDM (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5KINGDMB1 (300090) 161.0 kV to 7KINGDM (300043) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_863 | 3 Phase fault on 7THOMHL (300049) 345 kV Bus a. Apply fault at the 7THOMHL (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_863 | 3 Phase fault on 7THOMHL (300049) 345 kV Bus a. Apply fault at the 7THOMHL (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_864 | 3 Phase fault on 7THOMHL (300049) 345 kV Bus a. Apply fault at the 7THOMHL (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_864 | 3 Phase fault on 7THOMHL (300049) 345 kV Bus a. Apply fault at the 7THOMHL (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_865 | 3 Phase fault on 5NORTON (300105) 161 kV Bus a. Apply fault at the 5NORTON (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_865 | 3 Phase fault on 5NORTON (300105) 161 kV Bus a. Apply fault at the 5NORTON (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_866 | 3 Phase fault on 5THMHILB1 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 5THMHILB1 (300120) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_866 | 3 Phase fault on 5THMHILB1 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 5THMHILB1 (300120) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_867 | 3 Phase fault on 5BEVIER (300381) 161 kV Bus a. Apply fault at the 5BEVIER (300381) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BEVIER (300381) 161.0 kV to 2BEVIER (300387) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_867 | 3 Phase fault on 5BEVIER (300381) 161 kV Bus a. Apply fault at the 5BEVIER (300381) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BEVIER (300381) 161.0 kV to 2BEVIER (300387) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_868 | 3 Phase fault on 5LAMAR (300794) 161 kV Bus a. Apply fault at the 5LAMAR (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_868 | 3 Phase fault on 5LAMAR (300794) 161 kV Bus a. Apply fault at the 5LAMAR (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_869 | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_869 | 3 Phase fault on 5BUTLER (301342) 161 kV Bus a. Apply fault at the 5BUTLER (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_87 | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_87 | 3 Phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_870 | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_870 | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_871 | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_871 | 3 Phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_872 | 3 Phase fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_872 | 3 Phase fault on 7JASPER (300949) 345 kV Bus a. Apply fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_873 | 3 Phase fault on 5THOMHLXF1 (301508) 161 kV Bus a. Apply fault at the 5THOMHLXF1 (301508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2THOMHLXF1 (301509) 69.0 kV to 5THOMHLXF1 (301508) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_873 | 3 Phase fault on 5THOMHLXF1 (301508) 161 kV Bus a. Apply fault at the 5THOMHLXF1 (301508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2THOMHLXF1 (301509) 69.0 kV to 5THOMHLXF1 (301508) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_874 | 3 Phase fault on 7ZACHARY (344000) 345 kV Bus a. Apply fault at the 7ZACHARY (344000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ZACHARY (344000) 345.0 kV to 5ZACHARY (344010) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_874 | 3 Phase fault on 7ZACHARY (344000) 345 kV Bus a. Apply fault at the 7ZACHARY (344000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ZACHARY (344000) 345.0 kV to 5ZACHARY (344010) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_875 | 3 Phase fault on 5OVERTON (345409) 161 kV Bus a. Apply fault at the 5OVERTON (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_875 | 3 Phase fault on 5OVERTON (345409) 161 kV Bus a. Apply fault at the 5OVERTON (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_876 | 3 Phase fault on 5OVERTON 2 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_876 | 3 Phase fault on 5OVERTON 2 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_877 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_877 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_878 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 (520999) 138.0 kV to MOORLND2 (520995) 69.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_878 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 (520999) 138.0 kV to MOORLND2 (520995) 69.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_879 | 3 Phase fault on TXPHSF 3 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to TEXAS_CNTY 3 (523090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_879 | 3 Phase fault on TXPHSF 3 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to TEXAS_CNTY 3 (523090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_88 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_88 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_880 | 3 Phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_880 | 3 Phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_881 | 3 Phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_881 | 3 Phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_882 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_882 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_883 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_883 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_884 | 3 Phase fault on NOBLE_WND 7 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_884 | 3 Phase fault on NOBLE_WND 7 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_885 | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_885 | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_886 | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_886 | 3 Phase fault on NOVUS1 7 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_887 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_887 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_888 | 3 Phase fault on HUGOTON3 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_888 | 3 Phase fault on HUGOTON3 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_889 | 3 Phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_889 | 3 Phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_89 | 3 Phase fault on NW68HOLDRG3 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_89 | 3 Phase fault on NW68HOLDRG3 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_890 | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_890 | 3 Phase fault on GRDNCTY3 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_891 | 3 Phase fault on SEWARD-3 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMSSWRD2 (531466) 69.0 kV to SEWARD-3 (531467) 115.0 kV to SEWARD 1 (531260) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_891 | 3 Phase fault on SEWARD-3 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMSSWRD2 (531466) 69.0 kV to SEWARD-3 (531467) 115.0 kV to SEWARD 1 (531260) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_892 | 3 Phase fault on HARBNGR7 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_892 | 3 Phase fault on HARBNGR7 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_893 | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_893 | 3 Phase fault on HOYT 7 (532765) 345 kV Bus a. Apply fault at the HOYT 7 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_894 | 3 Phase fault on JEC N 7 (532766) 345 kV Bus a. Apply fault at the JEC N 7 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_894 | 3 Phase fault on JEC N 7 (532766) 345 kV Bus a. Apply fault at the JEC N 7 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_895 | 3 Phase fault on JEC N 7 (532766) 345 kV Bus a. Apply fault at the JEC N 7 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_895 | 3 Phase fault on JEC N 7 (532766) 345 kV Bus a. Apply fault at the JEC N 7 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_896 | 3 Phase fault on GEARY 7 (532767) 345 kV Bus a. Apply fault at the GEARY 7 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_896 | 3 Phase fault on GEARY 7 (532767) 345 kV Bus a. Apply fault at the GEARY 7 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_897 | 3 Phase fault on MORRIS 7 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_897 | 3 Phase fault on MORRIS 7 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_898 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_898 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_899 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_899 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_9 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_9 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_90 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_90 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_900 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_900 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_901 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_901 | 3 Phase fault on STRANGR7 (532772) 345 kV Bus a. Apply fault at the STRANGR7 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_902 | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_902 | 3 Phase fault on SUMMIT 7 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_903 | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_903 | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_904 | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_904 | 3 Phase fault on SWISVAL7 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_905 | 3 Phase fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_905 | 3 Phase fault on 87TH 7 (532775) 345 kV Bus a. Apply fault at the 87TH 7 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_906 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_906 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_907 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_907 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_908 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_908 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_909 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_909 | 3 Phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_91 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_91 | 3 Phase fault on MOORE 3 (640277) 345 kV Bus a. Apply fault at the MOORE 3 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_910 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_910 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_911 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_911 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_912 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_912 | 3 Phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_913 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_913 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_914 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_914 | 3 Phase fault on WICHITA7 (532796) 345 kV Bus a. Apply fault at the WICHITA7 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_915 | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_915 | 3 Phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_916 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_916 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_917 | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_917 | 3 Phase fault on CIRCLE 6 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_918 | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_918 | 3 Phase fault on EMCPHER6 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_919 | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_919 | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_92 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_92 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_920 | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_920 | 3 Phase fault on SUMMIT 6 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Oscillations out of GEN-2017-120 due to Drive Train model (WTDTA1) | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Update damping parameter in WTDTA1 model for GEN-2017-120
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_921 | 3 Phase fault on UNIONRG6 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_921 | 3 Phase fault on UNIONRG6 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_922 | 3 Phase fault on EDWRDVL5 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_922 | 3 Phase fault on EDWRDVL5 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_923 | 3 Phase fault on KELLY 5 (532913) 161 kV Bus a. Apply fault at the KELLY 5 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_923 | 3 Phase fault on KELLY 5 (532913) 161 kV Bus a. Apply fault at the KELLY 5 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_924 | 3 Phase fault on TECHILL5 (532920) 161 kV Bus a. Apply fault at the TECHILL5 (532920) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_924 | 3 Phase fault on TECHILL5 (532920) 161 kV Bus a. Apply fault at the TECHILL5 (532920) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_925 | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_925 | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_926 | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_926 | 3 Phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_927 | 3 Phase fault on BUTLERS4 (532989) 138 kV Bus a. Apply fault at the BUTLERS4 (532989) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_927 | 3 Phase fault on BUTLERS4 (532989) 138 kV Bus a. Apply fault at the BUTLERS4 (532989) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_928 | 3 Phase fault on MIDIAN 4 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_928 | 3 Phase fault on MIDIAN 4 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_929 | 3 Phase fault on HALSTD 4 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_929 | 3 Phase fault on HALSTD 4 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_93 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_93 | 3 Phase fault on WAGENER 3 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_930 | 3 Phase fault on HALSTD 4 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_930 | 3 Phase fault on HALSTD 4 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_931 | 3 Phase fault on MOUND 4 (533013) 138 kV Bus a. Apply fault at the MOUND 4 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_931 | 3 Phase fault on MOUND 4 (533013) 138 kV Bus a. Apply fault at the MOUND 4 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_932 | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_932 | 3 Phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_933 | 3 Phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_933 | 3 Phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_934 | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_934 | 3 Phase fault on CHISHLM4 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_935 | 3 Phase fault on GILL E 4 (533044) 138 kV Bus a. Apply fault at the GILL E 4 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_935 | 3 Phase fault on GILL E 4 (533044) 138 kV Bus a. Apply fault at the GILL E 4 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_936 | 3 Phase fault on GILL S 4 (533046) 138 kV Bus a. Apply fault at the GILL S 4 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_936 | 3 Phase fault on GILL S 4 (533046) 138 kV Bus a. Apply fault at the GILL S 4 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_937 | 3 Phase fault on GILL S 4 (533046) 138 kV Bus a. Apply fault at the GILL S 4 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_937 | 3 Phase fault on GILL S 4 (533046) 138 kV Bus a. Apply fault at the GILL S 4 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_938 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_938 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_939 | 3 Phase fault on COLINE 3 (533153) 115 kV Bus a. Apply fault at the COLINE 3 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_939 | 3 Phase fault on COLINE 3 (533153) 115 kV Bus a. Apply fault at the COLINE 3 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_94 | 3 Phase fault on DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_94 | 3 Phase fault on DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_940 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to ARNOLD 2 (533471) 69.0 kV to ARNOLD 1 (533449) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_940 | 3 Phase fault on ARNOLD 3 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to ARNOLD 2 (533471) 69.0 kV to ARNOLD 1 (533449) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_941 | 3 Phase fault on DAVIS 3 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_941 | 3 Phase fault on DAVIS 3 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_942 | 3 Phase fault on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_942 | 3 Phase fault on HEC 3 (533419) 115 kV Bus a. Apply fault at the HEC 3 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_943 | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_943 | 3 Phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_944 | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_944 | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_945 | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_945 | 3 Phase fault on ALTOONA4 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_946 | 3 Phase fault on LIBERTY4 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_946 | 3 Phase fault on LIBERTY4 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_947 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_947 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_948 | 3 Phase fault on ELMCREEK7 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_948 | 3 Phase fault on ELMCREEK7 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_949 | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_949 | 3 Phase fault on PECULR 7 (541198) 345 kV Bus a. Apply fault at the PECULR 7 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_95 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_95 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_950 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_950 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_951 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_951 | 3 Phase fault on ST JOE 7 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_952 | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_952 | 3 Phase fault on PHILL 7 (541200) 345 kV Bus a. Apply fault at the PHILL 7 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_953 | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_953 | 3 Phase fault on SIBLEY 7 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_954 | 3 Phase fault on NEVADA 5 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVADA 5 (541208) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_954 | 3 Phase fault on NEVADA 5 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVADA 5 (541208) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_955 | 3 Phase fault on NEVADA 5 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVADA 5 (541208) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_955 | 3 Phase fault on NEVADA 5 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVADA 5 (541208) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_956 | 3 Phase fault on MARTCTY5 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_956 | 3 Phase fault on MARTCTY5 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_957 | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_957 | 3 Phase fault on LNGVW 5 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_958 | 3 Phase fault on CLINTON5 (541242) 161 kV Bus a. Apply fault at the CLINTON5 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_958 | 3 Phase fault on CLINTON5 (541242) 161 kV Bus a. Apply fault at the CLINTON5 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_959 | 3 Phase fault on CLINTON5 (541242) 161 kV Bus a. Apply fault at the CLINTON5 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_959 | 3 Phase fault on CLINTON5 (541242) 161 kV Bus a. Apply fault at the CLINTON5 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_96 | 3 Phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_96 | 3 Phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_960 | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_960 | 3 Phase fault on EASTOWN7 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_961 | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_961 | 3 Phase fault on W.GRDNR7 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_962 | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_962 | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_963 | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_963 | 3 Phase fault on STILWEL7 (542968) 345 kV Bus a. Apply fault at the STILWEL7 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_964 | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_964 | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_965 | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_965 | 3 Phase fault on HAWTH 7 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_966 | 3 Phase fault on CRAIG 7 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_966 | 3 Phase fault on CRAIG 7 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_967 | 3 Phase fault on CRAIG 7 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_967 | 3 Phase fault on CRAIG 7 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_968 | 3 Phase fault on CRAIG 7 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_968 | 3 Phase fault on CRAIG 7 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_969 | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_969 | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_97 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_97 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_970 | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_970 | 3 Phase fault on NASHUA 7 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_971 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_971 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_972 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_972 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_973 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_973 | 3 Phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_974 | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_974 | 3 Phase fault on IATAN 7 (542982) 345 kV Bus a. Apply fault at the IATAN 7 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_975 | 3 Phase fault on HAWTHS_XF5 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_975 | 3 Phase fault on HAWTHS_XF5 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_976 | 3 Phase fault on HAWTHS_XF5 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_976 | 3 Phase fault on HAWTHS_XF5 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_977 | 3 Phase fault on BARBER 5 (546651) 161 kV Bus a. Apply fault at the BARBER 5 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_977 | 3 Phase fault on BARBER 5 (546651) 161 kV Bus a. Apply fault at the BARBER 5 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_978 | 3 Phase fault on ORO110 5 (547467) 161 kV Bus a. Apply fault at the ORO110 5 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_978 | 3 Phase fault on ORO110 5 (547467) 161 kV Bus a. Apply fault at the ORO110 5 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_979 | 3 Phase fault on RIV4525 (547469) 161 kV Bus a. Apply fault at the RIV4525 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_979 | 3 Phase fault on RIV4525 (547469) 161 kV Bus a. Apply fault at the RIV4525 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_98 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_98 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_980 | 3 Phase fault on HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_980 | 3 Phase fault on HOC404 5 (547487) 161 kV Bus a. Apply fault at the HOC404 5 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_981 | 3 Phase fault on BLUVLY-161 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_981 | 3 Phase fault on BLUVLY-161 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_982 | 3 Phase fault on BLUVLY-161 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_982 | 3 Phase fault on BLUVLY-161 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_983 | 3 Phase fault on SUB M-161 (548814) 161 kV Bus a. Apply fault at the SUB M-161 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_983 | 3 Phase fault on SUB M-161 (548814) 161 kV Bus a. Apply fault at the SUB M-161 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_984 | 3 Phase fault on SUB N-161 (548820) 161 kV Bus a. Apply fault at the SUB N-161 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_984 | 3 Phase fault on SUB N-161 (548820) 161 kV Bus a. Apply fault at the SUB N-161 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_985 | 3 Phase fault on COOPER 5 (640140) 161 kV Bus a. Apply fault at the COOPER 5 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_985 | 3 Phase fault on COOPER 5 (640140) 161 kV Bus a. Apply fault at the COOPER 5 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_986 | 3 Phase fault on 2JASPER (300649) 69 kV Bus a. Apply fault at the 2JASPER (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_986 | 3 Phase fault on 2JASPER (300649) 69 kV Bus a. Apply fault at the 2JASPER (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_987 | 3 Phase fault on 2KENOMA (300650) 69 kV Bus a. Apply fault at the 2KENOMA (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_987 | 3 Phase fault on 2KENOMA (300650) 69 kV Bus a. Apply fault at the 2KENOMA (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_988 | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_988 | 3 Phase fault on 2BUTLER (300689) 69 kV Bus a. Apply fault at the 2BUTLER (300689) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUTLER (300689) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_989 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_989 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_99 | 3 Phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_99 | 3 Phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_990 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_990 | 3 Phase fault on TEXAS_CNTY 3 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_991 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_991 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_992 | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_992 | 3 Phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_993 | 3 Phase fault on SC_WF1_7 (532779) 345 kV Bus a. Apply fault at the SC_WF1_7 (532779) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_993 | 3 Phase fault on SC_WF1_7 (532779) 345 kV Bus a. Apply fault at the SC_WF1_7 (532779) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_994 | 3 Phase fault on ENSNGW 3 (539784) 115 kV Bus a. Apply fault at the ENSNGW 3 (539784) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENSNGW 3 (539784) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_994 | 3 Phase fault on ENSNGW 3 (539784) 115 kV Bus a. Apply fault at the ENSNGW 3 (539784) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENSNGW 3 (539784) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_995 | 3 Phase fault on SUB K (548801) 69 kV Bus a. Apply fault at the SUB K (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_995 | 3 Phase fault on SUB K (548801) 69 kV Bus a. Apply fault at the SUB K (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_996 | 3 Phase fault on SUB H (548802) 69 kV Bus a. Apply fault at the SUB H (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_996 | 3 Phase fault on SUB H (548802) 69 kV Bus a. Apply fault at the SUB H (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_997 | 3 Phase fault on SUB M (548815) 69 kV Bus a. Apply fault at the SUB M (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_997 | 3 Phase fault on SUB M (548815) 69 kV Bus a. Apply fault at the SUB M (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_998 | 3 Phase fault on SUB N (548821) 69 kV Bus a. Apply fault at the SUB N (548821) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_998 | 3 Phase fault on SUB N (548821) 69 kV Bus a. Apply fault at the SUB N (548821) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P1_FAULT_999 | 3 Phase fault on SUB C (548825) 69 kV Bus a. Apply fault at the SUB C (548825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB C (548825) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P1_FAULT_999 | 3 Phase fault on SUB C (548825) 69 kV Bus a. Apply fault at the SUB C (548825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB C (548825) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on HILLS 3 (636400) 345 kV Bus a. Apply Fault at the HILLS 3 (636400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNSON3 (631208) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1 | Single Phase Fault with Stuck Breaker on HILLS 3 (636400) 345 kV Bus a. Apply Fault at the HILLS 3 (636400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNSON3 (631208) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_10 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_100 | Single Phase Fault with Stuck Breaker on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1000 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1000 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1001 | Single Phase Fault with Stuck Breaker on ROCKCK7 (541511) 345 kV Bus a. Apply Fault at the ROCKCK7 (541511) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKCK7 (541511) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1001 | Single Phase Fault with Stuck Breaker on ROCKCK7 (541511) 345 kV Bus a. Apply Fault at the ROCKCK7 (541511) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKCK7 (541511) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1002 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1002 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | 1) Low voltage and tripping; GEN-2018-058 and GEN-2018-059 2) Low End of Sim Voltage (Near Faulted Bus) - VOLT 543077 [PLSTVAL5 161.00] - VOLT 762405 [ASG-2018-010161.00] | 1) Build a 50 MVAR SVC at GEN-2018-058 345 kV 2) Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1003 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1003 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1004 | Single Phase Fault with Stuck Breaker on SEOTTWA5 (543055) 161 kV Bus a. Apply Fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEOTTWA5 (543055) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1004 | Single Phase Fault with Stuck Breaker on SEOTTWA5 (543055) 161 kV Bus a. Apply Fault at the SEOTTWA5 (543055) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEOTTWA5 (543055) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1005 | Single Phase Fault with Stuck Breaker on CNTRVIL5 (543065) 161 kV Bus a. Apply Fault at the CNTRVIL5 (543065) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRVIL5 (543065) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1005 | Single Phase Fault with Stuck Breaker on CNTRVIL5 (543065) 161 kV Bus a. Apply Fault at the CNTRVIL5 (543065) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRVIL5 (543065) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1006 | Single Phase Fault with Stuck Breaker on S.OTTWA5 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1006 | Single Phase Fault with Stuck Breaker on S.OTTWA5 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1007 | Single Phase Fault with Stuck Breaker on CENTENL5 (543067) 161 kV Bus a. Apply Fault at the CENTENL5 (543067) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENL5 (543067) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1007 | Single Phase Fault with Stuck Breaker on CENTENL5 (543067) 161 kV Bus a. Apply Fault at the CENTENL5 (543067) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENL5 (543067) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1008 | Single Phase Fault with Stuck Breaker on PAOLA 5 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1008 | Single Phase Fault with Stuck Breaker on PAOLA 5 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1009 | Single Phase Fault with Stuck Breaker on PLSTVAL5 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1009 | Single Phase Fault with Stuck Breaker on PLSTVAL5 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 b.2. KERR GR5 (512635) 161.0 kV to KERR BRK4 5 (512771) 161.0 kV Transmission Circuit #z0 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_101 | Single Phase Fault with Stuck Breaker on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1010 | Single Phase Fault with Stuck Breaker on GEN-2017-209 (760914) 345 kV Bus a. Apply Fault at the GEN-2017-209 (760914) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-209 (760914) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1010 | Single Phase Fault with Stuck Breaker on GEN-2017-209 (760914) 345 kV Bus a. Apply Fault at the GEN-2017-209 (760914) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-209 (760914) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1011 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1011 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1012 | Single Phase Fault with Stuck Breaker on WWRDEHV4 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1012 | Single Phase Fault with Stuck Breaker on WWRDEHV4 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1013 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1013 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1014 | Single Phase Fault with Stuck Breaker on HUGOTON2 (531380) 69 kV Bus a. Apply Fault at the HUGOTON2 (531380) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGOTON2 (531380) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1014 | Single Phase Fault with Stuck Breaker on HUGOTON2 (531380) 69 kV Bus a. Apply Fault at the HUGOTON2 (531380) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGOTON2 (531380) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1015 | Single Phase Fault with Stuck Breaker on WALKMYR2 (531404) 69 kV Bus a. Apply Fault at the WALKMYR2 (531404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR2 (531404) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1015 | Single Phase Fault with Stuck Breaker on WALKMYR2 (531404) 69 kV Bus a. Apply Fault at the WALKMYR2 (531404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR2 (531404) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1016 | Single Phase Fault with Stuck Breaker on CMSSWRD2 (531466) 69 kV Bus a. Apply Fault at the CMSSWRD2 (531466) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CMSSWRD2 (531466) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1016 | Single Phase Fault with Stuck Breaker on CMSSWRD2 (531466) 69 kV Bus a. Apply Fault at the CMSSWRD2 (531466) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CMSSWRD2 (531466) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1017 | Single Phase Fault with Stuck Breaker on HARBNGR3 (531510) 115 kV Bus a. Apply Fault at the HARBNGR3 (531510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1017 | Single Phase Fault with Stuck Breaker on HARBNGR3 (531510) 115 kV Bus a. Apply Fault at the HARBNGR3 (531510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1018 | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1018 | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1019 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1019 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on NWMAID5 (512757) 161 kV Bus a. Apply Fault at the NWMAID5 (512757) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_102 | Single Phase Fault with Stuck Breaker on NWMAID5 (512757) 161 kV Bus a. Apply Fault at the NWMAID5 (512757) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1020 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1020 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1021 | Single Phase Fault with Stuck Breaker on 87TH 7 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1021 | Single Phase Fault with Stuck Breaker on 87TH 7 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1022 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1022 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1023 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1023 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1024 | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1024 | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1025 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1025 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1026 | Single Phase Fault with Stuck Breaker on KELLY 5 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1026 | Single Phase Fault with Stuck Breaker on KELLY 5 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1027 | Single Phase Fault with Stuck Breaker on TECHILL5 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILL5 (532920) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1027 | Single Phase Fault with Stuck Breaker on TECHILL5 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILL5 (532920) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1028 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1028 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1029 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1029 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_103 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1030 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1030 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1031 | Single Phase Fault with Stuck Breaker on CHISHLM4 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1031 | Single Phase Fault with Stuck Breaker on CHISHLM4 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1032 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1032 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1033 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1033 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1034 | Single Phase Fault with Stuck Breaker on MARMATN2 (533639) 69 kV Bus a. Apply Fault at the MARMATN2 (533639) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1034 | Single Phase Fault with Stuck Breaker on MARMATN2 (533639) 69 kV Bus a. Apply Fault at the MARMATN2 (533639) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1035 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1035 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1036 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1036 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1037 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1037 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1038 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1038 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1039 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1039 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_104 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1040 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1040 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1041 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1041 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1042 | Single Phase Fault with Stuck Breaker on IATAN 7 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1042 | Single Phase Fault with Stuck Breaker on IATAN 7 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1043 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1043 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1044 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1044 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1045 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1045 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1046 | Single Phase Fault with Stuck Breaker on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1046 | Single Phase Fault with Stuck Breaker on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1047 | Single Phase Fault with Stuck Breaker on 5THOMHLXF4 (301510) 161 kV Bus a. Apply Fault at the 5THOMHLXF4 (301510) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THOMHLXF4 (301510) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1047 | Single Phase Fault with Stuck Breaker on 5THOMHLXF4 (301510) 161 kV Bus a. Apply Fault at the 5THOMHLXF4 (301510) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THOMHLXF4 (301510) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1048 | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1048 | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1049 | Single Phase Fault with Stuck Breaker on HUGOTON3 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGOTON3 (531481) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1049 | Single Phase Fault with Stuck Breaker on HUGOTON3 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGOTON3 (531481) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_105 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1050 | Single Phase Fault with Stuck Breaker on GEN-2017-009 (532778) 345 kV Bus a. Apply Fault at the GEN-2017-009 (532778) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-009 (532778) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1050 | Single Phase Fault with Stuck Breaker on GEN-2017-009 (532778) 345 kV Bus a. Apply Fault at the GEN-2017-009 (532778) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-009 (532778) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1051 | Single Phase Fault with Stuck Breaker on KINGMAN7 (532783) 345 kV Bus a. Apply Fault at the KINGMAN7 (532783) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGMAN7 (532783) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1051 | Single Phase Fault with Stuck Breaker on KINGMAN7 (532783) 345 kV Bus a. Apply Fault at the KINGMAN7 (532783) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGMAN7 (532783) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1052 | Single Phase Fault with Stuck Breaker on GEN-2016-073 (587500) 345 kV Bus a. Apply Fault at the GEN-2016-073 (587500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-073 (587500) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1052 | Single Phase Fault with Stuck Breaker on GEN-2016-073 (587500) 345 kV Bus a. Apply Fault at the GEN-2016-073 (587500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-073 (587500) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1053 | Single Phase Fault with Stuck Breaker on GEN-2017-220 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1053 | Single Phase Fault with Stuck Breaker on GEN-2017-220 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1054 | Single Phase Fault with Stuck Breaker on G14-001-TAP (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1054 | Single Phase Fault with Stuck Breaker on G14-001-TAP (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1055 | Single Phase Fault with Stuck Breaker on THISTLE4 (539804) 138 kV Bus a. Apply Fault at the THISTLE4 (539804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1055 | Single Phase Fault with Stuck Breaker on THISTLE4 (539804) 138 kV Bus a. Apply Fault at the THISTLE4 (539804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1056 | Single Phase Fault with Stuck Breaker on NLIB 3 (539737) 115 kV Bus a. Apply Fault at the NLIB 3 (539737) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NLIB 3 (539737) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1056 | Single Phase Fault with Stuck Breaker on NLIB 3 (539737) 115 kV Bus a. Apply Fault at the NLIB 3 (539737) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NLIB 3 (539737) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1057 | Single Phase Fault with Stuck Breaker on TRANSFORMER (539813) 345 kV Bus a. Apply Fault at the TRANSFORMER (539813) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TRANSFORMER (539813) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1057 | Single Phase Fault with Stuck Breaker on TRANSFORMER (539813) 345 kV Bus a. Apply Fault at the TRANSFORMER (539813) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TRANSFORMER (539813) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1058 | Single Phase Fault with Stuck Breaker on GEN-2011-008 (539840) 345 kV Bus a. Apply Fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-008 (539840) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1058 | Single Phase Fault with Stuck Breaker on GEN-2011-008 (539840) 345 kV Bus a. Apply Fault at the GEN-2011-008 (539840) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-008 (539840) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1059 | Single Phase Fault with Stuck Breaker on G16-046-TAP (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1059 | Single Phase Fault with Stuck Breaker on G16-046-TAP (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_106 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1060 | Single Phase Fault with Stuck Breaker on MC REAC1 (541411) 345 kV Bus a. Apply Fault at the MC REAC1 (541411) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MC REAC1 (541411) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1060 | Single Phase Fault with Stuck Breaker on MC REAC1 (541411) 345 kV Bus a. Apply Fault at the MC REAC1 (541411) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MC REAC1 (541411) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1061 | Single Phase Fault with Stuck Breaker on MC REAC2 (541412) 345 kV Bus a. Apply Fault at the MC REAC2 (541412) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MC REAC2 (541412) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1061 | Single Phase Fault with Stuck Breaker on MC REAC2 (541412) 345 kV Bus a. Apply Fault at the MC REAC2 (541412) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MC REAC2 (541412) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1062 | Single Phase Fault with Stuck Breaker on MC REAC3 (541413) 345 kV Bus a. Apply Fault at the MC REAC3 (541413) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MC REAC3 (541413) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1062 | Single Phase Fault with Stuck Breaker on MC REAC3 (541413) 345 kV Bus a. Apply Fault at the MC REAC3 (541413) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MC REAC3 (541413) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1063 | Single Phase Fault with Stuck Breaker on GEN-2018-022 (762581) 345 kV Bus a. Apply Fault at the GEN-2018-022 (762581) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-022 (762581) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1063 | Single Phase Fault with Stuck Breaker on GEN-2018-022 (762581) 345 kV Bus a. Apply Fault at the GEN-2018-022 (762581) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-022 (762581) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1064 | Single Phase Fault with Stuck Breaker on URICH 2 (541305) 69 kV Bus a. Apply Fault at the URICH 2 (541305) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. URICH 2 (541305) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1064 | Single Phase Fault with Stuck Breaker on URICH 2 (541305) 69 kV Bus a. Apply Fault at the URICH 2 (541305) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. URICH 2 (541305) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1065 | Single Phase Fault with Stuck Breaker on ASGI-2018-00 (762361) 69 kV Bus a. Apply Fault at the ASGI-2018-00 (762361) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASGI-2018-00 (762361) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1065 | Single Phase Fault with Stuck Breaker on ASGI-2018-00 (762361) 69 kV Bus a. Apply Fault at the ASGI-2018-00 (762361) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASGI-2018-00 (762361) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1066 | Single Phase Fault with Stuck Breaker on NEVJCT 2 (541311) 69 kV Bus a. Apply Fault at the NEVJCT 2 (541311) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVJCT 2 (541311) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1066 | Single Phase Fault with Stuck Breaker on NEVJCT 2 (541311) 69 kV Bus a. Apply Fault at the NEVJCT 2 (541311) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVJCT 2 (541311) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1067 | Single Phase Fault with Stuck Breaker on 3M 2 (541310) 69 kV Bus a. Apply Fault at the 3M 2 (541310) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3M 2 (541310) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1067 | Single Phase Fault with Stuck Breaker on 3M 2 (541310) 69 kV Bus a. Apply Fault at the 3M 2 (541310) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3M 2 (541310) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1068 | Single Phase Fault with Stuck Breaker on ASGI-2018-00 (762372) 69 kV Bus a. Apply Fault at the ASGI-2018-00 (762372) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASGI-2018-00 (762372) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1068 | Single Phase Fault with Stuck Breaker on ASGI-2018-00 (762372) 69 kV Bus a. Apply Fault at the ASGI-2018-00 (762372) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASGI-2018-00 (762372) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1069 | Single Phase Fault with Stuck Breaker on LVISTA 5 (542998) 161 kV Bus a. Apply Fault at the LVISTA 5 (542998) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LVISTA 5 (542998) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1069 | Single Phase Fault with Stuck Breaker on LVISTA 5 (542998) 161 kV Bus a. Apply Fault at the LVISTA 5 (542998) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LVISTA 5 (542998) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_107 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1070 | Single Phase Fault with Stuck Breaker on OSBORN7 (541501) 345 kV Bus a. Apply Fault at the OSBORN7 (541501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSBORN7 (541501) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1070 | Single Phase Fault with Stuck Breaker on OSBORN7 (541501) 345 kV Bus a. Apply Fault at the OSBORN7 (541501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSBORN7 (541501) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1071 | Single Phase Fault with Stuck Breaker on HOLT_REACT7 (541517) 345 kV Bus a. Apply Fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT_REACT7 (541517) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1071 | Single Phase Fault with Stuck Breaker on HOLT_REACT7 (541517) 345 kV Bus a. Apply Fault at the HOLT_REACT7 (541517) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT_REACT7 (541517) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1072 | Single Phase Fault with Stuck Breaker on GEN-2017-115 (760746) 345 kV Bus a. Apply Fault at the GEN-2017-115 (760746) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-115 (760746) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1072 | Single Phase Fault with Stuck Breaker on GEN-2017-115 (760746) 345 kV Bus a. Apply Fault at the GEN-2017-115 (760746) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-115 (760746) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1073 | Single Phase Fault with Stuck Breaker on OUTLAW (541543) 345 kV Bus a. Apply Fault at the OUTLAW (541543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OUTLAW (541543) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1073 | Single Phase Fault with Stuck Breaker on OUTLAW (541543) 345 kV Bus a. Apply Fault at the OUTLAW (541543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OUTLAW (541543) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1074 | Single Phase Fault with Stuck Breaker on CEDRCRK5 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1074 | Single Phase Fault with Stuck Breaker on CEDRCRK5 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1075 | Single Phase Fault with Stuck Breaker on CEDARNL5 (543054) 161 kV Bus a. Apply Fault at the CEDARNL5 (543054) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARNL5 (543054) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1075 | Single Phase Fault with Stuck Breaker on CEDARNL5 (543054) 161 kV Bus a. Apply Fault at the CEDARNL5 (543054) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARNL5 (543054) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1076 | Single Phase Fault with Stuck Breaker on BULLCRK5 (543105) 161 kV Bus a. Apply Fault at the BULLCRK5 (543105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BULLCRK5 (543105) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1076 | Single Phase Fault with Stuck Breaker on BULLCRK5 (543105) 161 kV Bus a. Apply Fault at the BULLCRK5 (543105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BULLCRK5 (543105) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1077 | Single Phase Fault with Stuck Breaker on BNSF 5 (543132) 161 kV Bus a. Apply Fault at the BNSF 5 (543132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BNSF 5 (543132) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1077 | Single Phase Fault with Stuck Breaker on BNSF 5 (543132) 161 kV Bus a. Apply Fault at the BNSF 5 (543132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BNSF 5 (543132) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1078 | Single Phase Fault with Stuck Breaker on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1078 | Single Phase Fault with Stuck Breaker on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1079 | Single Phase Fault with Stuck Breaker on NEASTOTTW5 (543166) 161 kV Bus a. Apply Fault at the NEASTOTTW5 (543166) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTOTTW5 (543166) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1079 | Single Phase Fault with Stuck Breaker on NEASTOTTW5 (543166) 161 kV Bus a. Apply Fault at the NEASTOTTW5 (543166) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTOTTW5 (543166) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_108 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1080 | Single Phase Fault with Stuck Breaker on ASG-2018-011 (762416) 161 kV Bus a. Apply Fault at the ASG-2018-011 (762416) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASG-2018-011 (762416) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1080 | Single Phase Fault with Stuck Breaker on ASG-2018-011 (762416) 161 kV Bus a. Apply Fault at the ASG-2018-011 (762416) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASG-2018-011 (762416) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1081 | Single Phase Fault with Stuck Breaker on OSAWAT 5 (543112) 161 kV Bus a. Apply Fault at the OSAWAT 5 (543112) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAWAT 5 (543112) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1081 | Single Phase Fault with Stuck Breaker on OSAWAT 5 (543112) 161 kV Bus a. Apply Fault at the OSAWAT 5 (543112) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAWAT 5 (543112) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1082 | Single Phase Fault with Stuck Breaker on ASG-2018-010 (762405) 161 kV Bus a. Apply Fault at the ASG-2018-010 (762405) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASG-2018-010 (762405) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1082 | Single Phase Fault with Stuck Breaker on ASG-2018-010 (762405) 161 kV Bus a. Apply Fault at the ASG-2018-010 (762405) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASG-2018-010 (762405) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1083 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1083 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1084 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1084 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1085 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1085 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1086 | Single Phase Fault with Stuck Breaker on SEWARD-3 (531467) 115 kV Bus a. Apply Fault at the SEWARD-3 (531467) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1086 | Single Phase Fault with Stuck Breaker on SEWARD-3 (531467) 115 kV Bus a. Apply Fault at the SEWARD-3 (531467) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1087 | Single Phase Fault with Stuck Breaker on HARBNGR7 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1087 | Single Phase Fault with Stuck Breaker on HARBNGR7 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1088 | Single Phase Fault with Stuck Breaker on HOYT 3 (533163) 115 kV Bus a. Apply Fault at the HOYT 3 (533163) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 3 (533163) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1088 | Single Phase Fault with Stuck Breaker on HOYT 3 (533163) 115 kV Bus a. Apply Fault at the HOYT 3 (533163) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 3 (533163) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1089 | Single Phase Fault with Stuck Breaker on JEC 6 (532852) 230 kV Bus a. Apply Fault at the JEC 6 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1089 | Single Phase Fault with Stuck Breaker on JEC 6 (532852) 230 kV Bus a. Apply Fault at the JEC 6 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_109 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1090 | Single Phase Fault with Stuck Breaker on STRANGR3 (533268) 115 kV Bus a. Apply Fault at the STRANGR3 (533268) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1090 | Single Phase Fault with Stuck Breaker on STRANGR3 (533268) 115 kV Bus a. Apply Fault at the STRANGR3 (533268) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1091 | Single Phase Fault with Stuck Breaker on 87TH 3 (533283) 115 kV Bus a. Apply Fault at the 87TH 3 (533283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 3 (533283) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1091 | Single Phase Fault with Stuck Breaker on 87TH 3 (533283) 115 kV Bus a. Apply Fault at the 87TH 3 (533283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 3 (533283) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1092 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1092 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1093 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1093 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1094 | Single Phase Fault with Stuck Breaker on WOLFCRK2 (533653) 69 kV Bus a. Apply Fault at the WOLFCRK2 (533653) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK2 (533653) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1094 | Single Phase Fault with Stuck Breaker on WOLFCRK2 (533653) 69 kV Bus a. Apply Fault at the WOLFCRK2 (533653) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK2 (533653) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1095 | Single Phase Fault with Stuck Breaker on SUMMIT 3 (533381) 115 kV Bus a. Apply Fault at the SUMMIT 3 (533381) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 3 (533381) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1095 | Single Phase Fault with Stuck Breaker on SUMMIT 3 (533381) 115 kV Bus a. Apply Fault at the SUMMIT 3 (533381) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 3 (533381) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1096 | Single Phase Fault with Stuck Breaker on KELLY 3 (533217) 115 kV Bus a. Apply Fault at the KELLY 3 (533217) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 3 (533217) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1096 | Single Phase Fault with Stuck Breaker on KELLY 3 (533217) 115 kV Bus a. Apply Fault at the KELLY 3 (533217) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 3 (533217) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1097 | Single Phase Fault with Stuck Breaker on TECHILW3 (533181) 115 kV Bus a. Apply Fault at the TECHILW3 (533181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1097 | Single Phase Fault with Stuck Breaker on TECHILW3 (533181) 115 kV Bus a. Apply Fault at the TECHILW3 (533181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1098 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1098 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1099 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1099 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_11 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. HERRON 5 (513591) 161.0 kV to IGLOOV1 5 (513593) 161.0 kV Transmission Circuit #1 b.3. IGLOTER1 1 (513592) 13.2 kV to IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV Three Winding #1 b.4. IGLOOV1 5 (513593) 161.0 kV to IGLOOV 7 (513596) 345.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_110 | Single Phase Fault with Stuck Breaker on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. HERRON 5 (513591) 161.0 kV to IGLOOV1 5 (513593) 161.0 kV Transmission Circuit #1 b.3. IGLOTER1 1 (513592) 13.2 kV to IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV Three Winding #1 b.4. IGLOOV1 5 (513593) 161.0 kV to IGLOOV 7 (513596) 345.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1100 | Single Phase Fault with Stuck Breaker on NEOSHON2 (533768) 69 kV Bus a. Apply Fault at the NEOSHON2 (533768) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1100 | Single Phase Fault with Stuck Breaker on NEOSHON2 (533768) 69 kV Bus a. Apply Fault at the NEOSHON2 (533768) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1101 | Single Phase Fault with Stuck Breaker on CHISHLM2 (533786) 69 kV Bus a. Apply Fault at the CHISHLM2 (533786) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM2 (533786) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1101 | Single Phase Fault with Stuck Breaker on CHISHLM2 (533786) 69 kV Bus a. Apply Fault at the CHISHLM2 (533786) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM2 (533786) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1102 | Single Phase Fault with Stuck Breaker on ARNOLD 2 (533471) 69 kV Bus a. Apply Fault at the ARNOLD 2 (533471) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 2 (533471) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1102 | Single Phase Fault with Stuck Breaker on ARNOLD 2 (533471) 69 kV Bus a. Apply Fault at the ARNOLD 2 (533471) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 2 (533471) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1103 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1103 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1104 | Single Phase Fault with Stuck Breaker on SIBLEY 5 (541202) 161 kV Bus a. Apply Fault at the SIBLEY 5 (541202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1104 | Single Phase Fault with Stuck Breaker on SIBLEY 5 (541202) 161 kV Bus a. Apply Fault at the SIBLEY 5 (541202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1105 | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1105 | Single Phase Fault with Stuck Breaker on NEVADA 5 (541208) 161 kV Bus a. Apply Fault at the NEVADA 5 (541208) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEVADA 5 (541208) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1106 | Single Phase Fault with Stuck Breaker on EASTOWN5 (541401) 161 kV Bus a. Apply Fault at the EASTOWN5 (541401) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1106 | Single Phase Fault with Stuck Breaker on EASTOWN5 (541401) 161 kV Bus a. Apply Fault at the EASTOWN5 (541401) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1107 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1107 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1108 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1108 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1109 | Single Phase Fault with Stuck Breaker on NASHUA-5 (543028) 161 kV Bus a. Apply Fault at the NASHUA-5 (543028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1109 | Single Phase Fault with Stuck Breaker on NASHUA-5 (543028) 161 kV Bus a. Apply Fault at the NASHUA-5 (543028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. HERRON 5 (513591) 161.0 kV to IGLOOV2 5 (513595) 161.0 kV Transmission Circuit #1 b.3. IGLOTER2 1 (513594) 13.2 kV to IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV Three Winding #2 b.4. IGLOOV2 5 (513595) 161.0 kV to IGLOOV 7 (513596) 345.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_111 | Single Phase Fault with Stuck Breaker on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. HERRON 5 (513591) 161.0 kV to IGLOOV2 5 (513595) 161.0 kV Transmission Circuit #1 b.3. IGLOTER2 1 (513594) 13.2 kV to IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV Three Winding #2 b.4. IGLOOV2 5 (513595) 161.0 kV to IGLOOV 7 (513596) 345.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1110 | Single Phase Fault with Stuck Breaker on LACYGNE2 (543659) 69 kV Bus a. Apply Fault at the LACYGNE2 (543659) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE2 (543659) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1110 | Single Phase Fault with Stuck Breaker on LACYGNE2 (543659) 69 kV Bus a. Apply Fault at the LACYGNE2 (543659) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE2 (543659) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1111 | Single Phase Fault with Stuck Breaker on IATAN5 (541350) 161 kV Bus a. Apply Fault at the IATAN5 (541350) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1111 | Single Phase Fault with Stuck Breaker on IATAN5 (541350) 161 kV Bus a. Apply Fault at the IATAN5 (541350) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1112 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1112 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_1113 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_1113 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV (Trip Bus) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATOOSA4 (509790) 138.0 kV to CATSAGR5 (512638) 161.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_112 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATOOSA4 (509790) 138.0 kV to CATSAGR5 (512638) 161.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATOOSA4 (509790) 138.0 kV to CATSAGR5 (512638) 161.0 kV to CATTER2 1 (512834) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_113 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATOOSA4 (509790) 138.0 kV to CATSAGR5 (512638) 161.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_114 | Single Phase Fault with Stuck Breaker on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_115 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_116 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_117 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_118 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_119 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_12 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_120 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_121 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_122 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_123 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_124 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_125 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_126 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_127 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_128 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_129 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_13 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.3. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_130 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.3. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_131 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_132 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.3. TONECE5 (512751) 161.0 kV to TONNEC2 (512753) 69.0 kV to TONNEC1 (512754) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_133 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.3. TONECE5 (512751) 161.0 kV to TONNEC2 (512753) 69.0 kV to TONNEC1 (512754) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILMCTY5 (512643) 161.0 kV to TONECE5 (512751) 161.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_134 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILMCTY5 (512643) 161.0 kV to TONECE5 (512751) 161.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 b.4. FARML 4 (512734) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_135 | Single Phase Fault with Stuck Breaker on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 b.4. FARML 4 (512734) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on MIAMI 5 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_136 | Single Phase Fault with Stuck Breaker on MIAMI 5 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 b.4. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR2 (512815) 13.8 kV Three Winding #2 b.5. CLARMR 5 (512651) 161.0 kV to CLARMR 4 (512707) 138.0 kV to CLARMR4 (512813) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_137 | Single Phase Fault with Stuck Breaker on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 b.4. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR2 (512815) 13.8 kV Three Winding #2 b.5. CLARMR 5 (512651) 161.0 kV to CLARMR 4 (512707) 138.0 kV to CLARMR4 (512813) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_138 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_139 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_14 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_140 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECSTG_1 (512615) 17.5 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_141 | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECSTG_1 (512615) 17.5 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECCTG_1 (512614) 20.0 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_142 | Single Phase Fault with Stuck Breaker on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECCTG_1 (512614) 20.0 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_143 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on DRYGULCH5 (512629) 161 kV Bus a. Apply Fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 b.3. DRYGULCH5 (512629) 161.0 kV to GEN-2017-073 (589110) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_144 | Single Phase Fault with Stuck Breaker on DRYGULCH5 (512629) 161 kV Bus a. Apply Fault at the DRYGULCH5 (512629) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 b.3. DRYGULCH5 (512629) 161.0 kV to GEN-2017-073 (589110) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on GERALDGAY5 (512760) 161 kV Bus a. Apply Fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_145 | Single Phase Fault with Stuck Breaker on GERALDGAY5 (512760) 161 kV Bus a. Apply Fault at the GERALDGAY5 (512760) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_146 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.4. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_147 | Single Phase Fault with Stuck Breaker on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.4. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_148 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_149 | Single Phase Fault with Stuck Breaker on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_15 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_150 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_151 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on LOCSTGVKM 5 (513050) 161 kV Bus a. Apply Fault at the LOCSTGVKM 5 (513050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.3. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_152 | Single Phase Fault with Stuck Breaker on LOCSTGVKM 5 (513050) 161 kV Bus a. Apply Fault at the LOCSTGVKM 5 (513050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.3. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on AFTON 5 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_153 | Single Phase Fault with Stuck Breaker on AFTON 5 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on PAWN-ED3 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.4. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.6. KINSLEY3 (530619) 115.0 kV to GEN-2016-016 (587120) 115.0 kV Transmission Circuit #1 b.7. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.8. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.9. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.10. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.11. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_154 | Single Phase Fault with Stuck Breaker on PAWN-ED3 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.4. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.6. KINSLEY3 (530619) 115.0 kV to GEN-2016-016 (587120) 115.0 kV Transmission Circuit #1 b.7. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.8. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.9. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.10. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.11. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_155 | Single Phase Fault with Stuck Breaker on GRTBEND6 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_156 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_157 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_158 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_159 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_16 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_160 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_161 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_162 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_163 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_164 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_165 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_166 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_167 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_168 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_169 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_17 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_170 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_171 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_172 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_173 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_174 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_175 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_176 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_177 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_178 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_179 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_18 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_180 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_181 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_182 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_183 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_184 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_185 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on S3761 3 (645761) 345 kV Bus a. Apply Fault at the S3761 3 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_186 | Single Phase Fault with Stuck Breaker on S3761 3 (645761) 345 kV Bus a. Apply Fault at the S3761 3 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_187 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_188 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_189 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_19 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_190 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_191 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on S1263 5 (646263) 161 kV Bus a. Apply Fault at the S1263 5 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.5. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_192 | Single Phase Fault with Stuck Breaker on S1263 5 (646263) 161 kV Bus a. Apply Fault at the S1263 5 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.5. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on S1280 5 (646280) 161 kV Bus a. Apply Fault at the S1280 5 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_193 | Single Phase Fault with Stuck Breaker on S1280 5 (646280) 161 kV Bus a. Apply Fault at the S1280 5 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_194 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_195 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_196 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on S1398 5 (646398) 161 kV Bus a. Apply Fault at the S1398 5 (646398) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV (Trip Generation) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_197 | Single Phase Fault with Stuck Breaker on S1398 5 (646398) 161 kV Bus a. Apply Fault at the S1398 5 (646398) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV (Trip Generation) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on KELLY 5 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.4. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_198 | Single Phase Fault with Stuck Breaker on KELLY 5 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.4. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on S1398 5 (646398) 161 kV Bus a. Apply Fault at the S1398 5 (646398) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV (Trip Generation) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_199 | Single Phase Fault with Stuck Breaker on S1398 5 (646398) 161 kV Bus a. Apply Fault at the S1398 5 (646398) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV (Trip Generation) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on JOHNSON5 (631093) 161 kV Bus a. Apply Fault at the JOHNSON5 (631093) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHLW5 (631034) 161.0 kV to JOHNSON5 (631093) 161.0 kV Transmission Circuit #1 b.2. JOHNSON5 (631093) 161.0 kV to JOHNSON8 (630809) 69.0 kV Two Winding #1 b.3. JOHNSON5 (631093) 161.0 kV to NORTHLIBERT5 (631222) 161.0 kV Transmission Circuit #1 b.4. JOHNSON3 (631208) 345.0 kV to JOHNSON5 (631093) 161.0 kV Two Winding #1 b.5. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_2 | Single Phase Fault with Stuck Breaker on JOHNSON5 (631093) 161 kV Bus a. Apply Fault at the JOHNSON5 (631093) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHLW5 (631034) 161.0 kV to JOHNSON5 (631093) 161.0 kV Transmission Circuit #1 b.2. JOHNSON5 (631093) 161.0 kV to JOHNSON8 (630809) 69.0 kV Two Winding #1 b.3. JOHNSON5 (631093) 161.0 kV to NORTHLIBERT5 (631222) 161.0 kV Transmission Circuit #1 b.4. JOHNSON3 (631208) 345.0 kV to JOHNSON5 (631093) 161.0 kV Two Winding #1 b.5. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_20 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_200 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_201 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on S963 8 (647963) 69 kV Bus a. Apply Fault at the S963 8 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_202 | Single Phase Fault with Stuck Breaker on S963 8 (647963) 69 kV Bus a. Apply Fault at the S963 8 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_203 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.2. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.3. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 b.5. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_204 | Single Phase Fault with Stuck Breaker on HUMBOLT5 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.2. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.3. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 b.5. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on S993 8 (647993) 69 kV Bus a. Apply Fault at the S993 8 (647993) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.5. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.6. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.7. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_205 | Single Phase Fault with Stuck Breaker on S993 8 (647993) 69 kV Bus a. Apply Fault at the S993 8 (647993) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.5. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.6. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.7. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on AUBRNT 8 (647101) 69 kV Bus a. Apply Fault at the AUBRNT 8 (647101) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_206 | Single Phase Fault with Stuck Breaker on AUBRNT 8 (647101) 69 kV Bus a. Apply Fault at the AUBRNT 8 (647101) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 b.2. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 b.3. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.7. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_207 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 b.2. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 b.3. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.7. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_208 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2NEOSHO (300750) 69.0 kV to 2SPGCTP (300754) 69.0 kV Transmission Circuit #1 b.6. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.7. 2SPGCTP (300754) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.8. 2SPGCTP (300754) 69.0 kV to 2SPURGNTP (300764) 69.0 kV Transmission Circuit #1 b.9. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.10. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_209 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2NEOSHO (300750) 69.0 kV to 2SPGCTP (300754) 69.0 kV Transmission Circuit #1 b.6. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.7. 2SPGCTP (300754) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.8. 2SPGCTP (300754) 69.0 kV to 2SPURGNTP (300764) 69.0 kV Transmission Circuit #1 b.9. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.10. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_21 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on NWARSAW5 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_210 | Single Phase Fault with Stuck Breaker on NWARSAW5 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on Y ROAD 3 (522912) 115 kV Bus a. Apply Fault at the Y ROAD 3 (522912) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 b.2. Y ROAD 3 (522912) 115.0 kV to POWELL CNR 3 (522957) 115.0 kV Transmission Circuit #1 b.3. Y ROAD 3 (522912) 115.0 kV to TEXAS_CNTY 3 (523090) 115.0 kV Transmission Circuit #1 b.4. RED DEVIL 3 (522930) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_211 | Single Phase Fault with Stuck Breaker on Y ROAD 3 (522912) 115 kV Bus a. Apply Fault at the Y ROAD 3 (522912) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 b.2. Y ROAD 3 (522912) 115.0 kV to POWELL CNR 3 (522957) 115.0 kV Transmission Circuit #1 b.3. Y ROAD 3 (522912) 115.0 kV to TEXAS_CNTY 3 (523090) 115.0 kV Transmission Circuit #1 b.4. RED DEVIL 3 (522930) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_212 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_213 | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_214 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_215 | Single Phase Fault with Stuck Breaker on BADGER 7 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_216 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_217 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_218 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_219 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_22 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_220 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_221 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_222 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_223 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_224 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on GRANTCO4 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_225 | Single Phase Fault with Stuck Breaker on GRANTCO4 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on GRANTCO4 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.4. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_226 | Single Phase Fault with Stuck Breaker on GRANTCO4 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.4. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_227 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_228 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_229 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_23 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on KNOBHIL4 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_230 | Single Phase Fault with Stuck Breaker on KNOBHIL4 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_231 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_232 | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_233 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_234 | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_235 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_236 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_237 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_238 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on RDRUNNR4 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_239 | Single Phase Fault with Stuck Breaker on RDRUNNR4 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_24 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on RDRUNNR4 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to RCKFALL4 (515427) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_240 | Single Phase Fault with Stuck Breaker on RDRUNNR4 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to RCKFALL4 (515427) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_241 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_242 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_243 | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_244 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_245 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_246 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_247 | Single Phase Fault with Stuck Breaker on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on GRDNCTY3 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 b.5. GRDNCTY3 (531445) 115.0 kV to S5 GEN 1 (531462) 13.2 kV Two Winding #1 b.6. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.7. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.8. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.9. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.10. GRDNCTY3 (531445) 115.0 kV to GC-C 1 (531421) 34.5 kV to GC-CITY (531254) 13.8 kV Three Winding #1 b.11. GRDNCTY3 (531445) 115.0 kV to GARDNCY2 (531423) 69.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_248 | Single Phase Fault with Stuck Breaker on GRDNCTY3 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 b.5. GRDNCTY3 (531445) 115.0 kV to S5 GEN 1 (531462) 13.2 kV Two Winding #1 b.6. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.7. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.8. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.9. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.10. GRDNCTY3 (531445) 115.0 kV to GC-C 1 (531421) 34.5 kV to GC-CITY (531254) 13.8 kV Three Winding #1 b.11. GRDNCTY3 (531445) 115.0 kV to GARDNCY2 (531423) 69.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on 29TH 4 (533024) 138 kV Bus a. Apply Fault at the 29TH 4 (533024) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_249 | Single Phase Fault with Stuck Breaker on 29TH 4 (533024) 138 kV Bus a. Apply Fault at the 29TH 4 (533024) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_25 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on CHISHLM4 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_250 | Single Phase Fault with Stuck Breaker on CHISHLM4 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on MIDIAN 4 (532990) 138 kV Bus a. Apply Fault at the MIDIAN 4 (532990) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. MIDIAN 4 (532990) 138.0 kV to TCBURNS4 (532994) 138.0 kV Transmission Circuit #1 b.4. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_251 | Single Phase Fault with Stuck Breaker on MIDIAN 4 (532990) 138 kV Bus a. Apply Fault at the MIDIAN 4 (532990) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. MIDIAN 4 (532990) 138.0 kV to TCBURNS4 (532994) 138.0 kV Transmission Circuit #1 b.4. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on MAIZE 4 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_252 | Single Phase Fault with Stuck Breaker on MAIZE 4 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on TIOGA 4 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_253 | Single Phase Fault with Stuck Breaker on TIOGA 4 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on 12&CLAY3 (533184) 115 kV Bus a. Apply Fault at the 12&CLAY3 (533184) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 12&CLAY3 (533184) 115.0 kV Transmission Circuit #1 b.2. 12&CLAY3 (533184) 115.0 kV to 4VAN S 3 (533200) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_254 | Single Phase Fault with Stuck Breaker on 12&CLAY3 (533184) 115 kV Bus a. Apply Fault at the 12&CLAY3 (533184) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 12&CLAY3 (533184) 115.0 kV Transmission Circuit #1 b.2. 12&CLAY3 (533184) 115.0 kV to 4VAN S 3 (533200) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on 6 GOLDN3 (533177) 115 kV Bus a. Apply Fault at the 6 GOLDN3 (533177) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_255 | Single Phase Fault with Stuck Breaker on 6 GOLDN3 (533177) 115 kV Bus a. Apply Fault at the 6 GOLDN3 (533177) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on AEC 3 (533361) 115 kV Bus a. Apply Fault at the AEC 3 (533361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AEC 3 (533361) 115.0 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.2. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.4. AEC 3 (533361) 115.0 kV to AEC W1 (533887) 34.5 kV Two Winding #1 b.5. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_256 | Single Phase Fault with Stuck Breaker on AEC 3 (533361) 115 kV Bus a. Apply Fault at the AEC 3 (533361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AEC 3 (533361) 115.0 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.2. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.4. AEC 3 (533361) 115.0 kV to AEC W1 (533887) 34.5 kV Two Winding #1 b.5. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on DAVIS 3 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.3. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_257 | Single Phase Fault with Stuck Breaker on DAVIS 3 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.3. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on EDWRDVL5 (532912) 161 kV Bus a. Apply Fault at the EDWRDVL5 (532912) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. EDWARVL3 (533238) 115.0 kV to EDWRDVL5 (532912) 161.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_258 | Single Phase Fault with Stuck Breaker on EDWRDVL5 (532912) 161 kV Bus a. Apply Fault at the EDWRDVL5 (532912) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. EDWARVL3 (533238) 115.0 kV to EDWRDVL5 (532912) 161.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on KERFORD3 (533216) 115 kV Bus a. Apply Fault at the KERFORD3 (533216) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 b.2. AMELIA 3 (533215) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 b.3. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_259 | Single Phase Fault with Stuck Breaker on KERFORD3 (533216) 115 kV Bus a. Apply Fault at the KERFORD3 (533216) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 b.2. AMELIA 3 (533215) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 b.3. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_26 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on LEC U4 3 (533249) 115 kV Bus a. Apply Fault at the LEC U4 3 (533249) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 (532662) 14.4 kV to LEC U4 3 (533249) 115.0 kV Two Winding #1 b.2. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.3. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_260 | Single Phase Fault with Stuck Breaker on LEC U4 3 (533249) 115 kV Bus a. Apply Fault at the LEC U4 3 (533249) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 (532662) 14.4 kV to LEC U4 3 (533249) 115.0 kV Two Winding #1 b.2. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.3. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on SMOKYHLLS3 (533378) 115 kV Bus a. Apply Fault at the SMOKYHLLS3 (533378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 b.2. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_261 | Single Phase Fault with Stuck Breaker on SMOKYHLLS3 (533378) 115 kV Bus a. Apply Fault at the SMOKYHLLS3 (533378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 b.2. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_262 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_263 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_264 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_265 | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on LANG 7 (532769) 345 kV Bus a. Apply Fault at the LANG 7 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_266 | Single Phase Fault with Stuck Breaker on LANG 7 (532769) 345 kV Bus a. Apply Fault at the LANG 7 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_267 | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_268 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_269 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_27 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_270 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_271 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_272 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_273 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_273 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_274 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_275 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_276 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_277 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_278 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_279 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_28 | Single Phase Fault with Stuck Breaker on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_280 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_281 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_282 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_283 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_284 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_285 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_286 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_287 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_288 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_289 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_29 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_290 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_290 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_291 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_291 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_292 | Single Phase Fault with Stuck Breaker on AUBURN 6 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.3. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_292 | Single Phase Fault with Stuck Breaker on AUBURN 6 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.3. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_293 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_293 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_294 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_294 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_295 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_295 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_296 | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_296 | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_297 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U1 (532651) 26.0 kV to JEC 6 (532852) 230.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_297 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U1 (532651) 26.0 kV to JEC 6 (532852) 230.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_298 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_298 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_299 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_299 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_3 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_30 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_300 | Single Phase Fault with Stuck Breaker on LAWHILL6 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_300 | Single Phase Fault with Stuck Breaker on LAWHILL6 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_301 | Single Phase Fault with Stuck Breaker on LAWHILL6 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_301 | Single Phase Fault with Stuck Breaker on LAWHILL6 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_302 | Single Phase Fault with Stuck Breaker on MORRIS 7 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_302 | Single Phase Fault with Stuck Breaker on MORRIS 7 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_303 | Single Phase Fault with Stuck Breaker on MORRIS 7 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_303 | Single Phase Fault with Stuck Breaker on MORRIS 7 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_304 | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_304 | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_305 | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_305 | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_306 | Single Phase Fault with Stuck Breaker on SUMMIT 7 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_306 | Single Phase Fault with Stuck Breaker on SUMMIT 7 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_307 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_307 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_308 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_308 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_309 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_309 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_31 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_310 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_310 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_311 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_311 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_312 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_312 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_313 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_313 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_314 | Single Phase Fault with Stuck Breaker on SWISVAL6 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_314 | Single Phase Fault with Stuck Breaker on SWISVAL6 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_315 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_315 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_316 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_316 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_317 | Single Phase Fault with Stuck Breaker on SWISVAL6 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_317 | Single Phase Fault with Stuck Breaker on SWISVAL6 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_318 | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_318 | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_319 | Single Phase Fault with Stuck Breaker on EDWRDVL5 (532912) 161 kV Bus a. Apply Fault at the EDWRDVL5 (532912) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_319 | Single Phase Fault with Stuck Breaker on EDWRDVL5 (532912) 161 kV Bus a. Apply Fault at the EDWRDVL5 (532912) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_32 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_320 | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.3. FRANKLIN5 (532938) 161.0 kV to FRANKLIN2 (533876) 69.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_320 | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.3. FRANKLIN5 (532938) 161.0 kV to FRANKLIN2 (533876) 69.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_321 | Single Phase Fault with Stuck Breaker on KELLY 5 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to GEN-2018-053 (762878) 161.0 kV Transmission Circuit #1 b.4. ENEMAHA3 (533210) 115.0 kV to KELLY 3 (533217) 115.0 kV Transmission Circuit #1 b.5. KELLY 3 (533217) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.6. KELLY 3 (533217) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.7. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_321 | Single Phase Fault with Stuck Breaker on KELLY 5 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to GEN-2018-053 (762878) 161.0 kV Transmission Circuit #1 b.4. ENEMAHA3 (533210) 115.0 kV to KELLY 3 (533217) 115.0 kV Transmission Circuit #1 b.5. KELLY 3 (533217) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.6. KELLY 3 (533217) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.7. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_322 | Single Phase Fault with Stuck Breaker on TECHILL5 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_322 | Single Phase Fault with Stuck Breaker on TECHILL5 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_323 | Single Phase Fault with Stuck Breaker on 17TH 4 (533064) 138 kV Bus a. Apply Fault at the 17TH 4 (533064) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.3. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_323 | Single Phase Fault with Stuck Breaker on 17TH 4 (533064) 138 kV Bus a. Apply Fault at the 17TH 4 (533064) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.3. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_324 | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.6. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.8. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_324 | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.6. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.8. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_325 | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.6. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_325 | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.6. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_326 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_326 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_327 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_327 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_328 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_328 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_329 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_329 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_33 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_330 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_330 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_331 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_331 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_332 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_332 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_333 | Single Phase Fault with Stuck Breaker on BUTLERS4 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.4. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_333 | Single Phase Fault with Stuck Breaker on BUTLERS4 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.4. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_334 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_334 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_335 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_335 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_336 | Single Phase Fault with Stuck Breaker on DEARING4 (533002) 138 kV Bus a. Apply Fault at the DEARING4 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.5. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_336 | Single Phase Fault with Stuck Breaker on DEARING4 (533002) 138 kV Bus a. Apply Fault at the DEARING4 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.5. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_337 | Single Phase Fault with Stuck Breaker on ELPASO 4 (533039) 138 kV Bus a. Apply Fault at the ELPASO 4 (533039) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.4. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_337 | Single Phase Fault with Stuck Breaker on ELPASO 4 (533039) 138 kV Bus a. Apply Fault at the ELPASO 4 (533039) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.4. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_338 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_338 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_339 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_339 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_34 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_340 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_340 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_341 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_341 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage and tripping; GEN-2018-058 and GEN-2018-059 | Build a 50 MVAR SVC at GEN-2018-058 345 kV
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_342 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_342 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_343 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_343 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_344 | Single Phase Fault with Stuck Breaker on LAKERDG4 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEC DG 1 (532730) 4.2 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_344 | Single Phase Fault with Stuck Breaker on LAKERDG4 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEC DG 1 (532730) 4.2 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_345 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_345 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_346 | Single Phase Fault with Stuck Breaker on 45TH ST4 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_346 | Single Phase Fault with Stuck Breaker on 45TH ST4 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_347 | Single Phase Fault with Stuck Breaker on 45TH ST4 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_347 | Single Phase Fault with Stuck Breaker on 45TH ST4 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_348 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_348 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_349 | Single Phase Fault with Stuck Breaker on HALSTD 4 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.5. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 b.6. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_349 | Single Phase Fault with Stuck Breaker on HALSTD 4 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.5. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 b.6. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_35 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_350 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_350 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_351 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_351 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_352 | Single Phase Fault with Stuck Breaker on LIBERTY4 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_352 | Single Phase Fault with Stuck Breaker on LIBERTY4 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_353 | Single Phase Fault with Stuck Breaker on MONTGOM4 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_353 | Single Phase Fault with Stuck Breaker on MONTGOM4 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_354 | Single Phase Fault with Stuck Breaker on MOUND 4 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_354 | Single Phase Fault with Stuck Breaker on MOUND 4 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_355 | Single Phase Fault with Stuck Breaker on GILL W 4 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_355 | Single Phase Fault with Stuck Breaker on GILL W 4 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_356 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.6. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_356 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.6. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_357 | Single Phase Fault with Stuck Breaker on GILL E 4 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_357 | Single Phase Fault with Stuck Breaker on GILL E 4 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_358 | Single Phase Fault with Stuck Breaker on NOEASTW4 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. NEAST3X1 (533110) 11.3 kV to NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_358 | Single Phase Fault with Stuck Breaker on NOEASTW4 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. NEAST3X1 (533110) 11.3 kV to NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_359 | Single Phase Fault with Stuck Breaker on NOEASTE4 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.4. NEAST5X1 (533111) 13.2 kV to NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_359 | Single Phase Fault with Stuck Breaker on NOEASTE4 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.4. NEAST5X1 (533111) 13.2 kV to NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_36 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_360 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.8. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.10. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_360 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.8. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.10. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_361 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_361 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_362 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_362 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_363 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_363 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_364 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. ROSEH3 1 (532831) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_364 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. ROSEH3 1 (532831) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_365 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEH3 1 (532831) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 b.2. ROSEHIL4 (533062) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_365 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEH3 1 (532831) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 b.2. ROSEHIL4 (533062) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_366 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 b.2. ROSEH1 1 (532826) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_366 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 b.2. ROSEH1 1 (532826) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_367 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEH1 1 (532826) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 b.2. ROSEHIL4 (533062) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_367 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEH1 1 (532826) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 b.2. ROSEHIL4 (533062) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_368 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_368 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_369 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEH5 1 (532827) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 b.2. ROSEHIL4 (533062) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_369 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEH5 1 (532827) 13.8 kV to ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV Three Winding #1 b.2. ROSEHIL4 (533062) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_37 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_370 | Single Phase Fault with Stuck Breaker on SUMNER 4 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.4. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.5. SUMNER 4 (532984) 138.0 kV to GEN-2017-121 (761838) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_370 | Single Phase Fault with Stuck Breaker on SUMNER 4 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.4. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.5. SUMNER 4 (532984) 138.0 kV to GEN-2017-121 (761838) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_371 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_371 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_372 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.7. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.8. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.9. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_372 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.7. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.8. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.9. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_373 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.7. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_373 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.7. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_374 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.7. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_374 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.7. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_375 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_375 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_376 | Single Phase Fault with Stuck Breaker on 17&FAIR3 (533175) 115 kV Bus a. Apply Fault at the 17&FAIR3 (533175) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 b.2. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.3. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 17&FAIR3 (533175) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_376 | Single Phase Fault with Stuck Breaker on 17&FAIR3 (533175) 115 kV Bus a. Apply Fault at the 17&FAIR3 (533175) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 b.2. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.3. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 17&FAIR3 (533175) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_377 | Single Phase Fault with Stuck Breaker on 3 VANBU3 (533435) 115 kV Bus a. Apply Fault at the 3 VANBU3 (533435) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. 3 VANBU3 (533435) 115.0 kV to 3 VANBU2 (533527) 69.0 kV to 3VANBUR1 (533446) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_377 | Single Phase Fault with Stuck Breaker on 3 VANBU3 (533435) 115 kV Bus a. Apply Fault at the 3 VANBU3 (533435) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. 3 VANBU3 (533435) 115.0 kV to 3 VANBU2 (533527) 69.0 kV to 3VANBUR1 (533446) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_378 | Single Phase Fault with Stuck Breaker on FORBES 3 (533157) 115 kV Bus a. Apply Fault at the FORBES 3 (533157) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORBES 3 (533157) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.2. FORBES 3 (533157) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.3. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.4. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_378 | Single Phase Fault with Stuck Breaker on FORBES 3 (533157) 115 kV Bus a. Apply Fault at the FORBES 3 (533157) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORBES 3 (533157) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.2. FORBES 3 (533157) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.3. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.4. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_379 | Single Phase Fault with Stuck Breaker on 41CALIF3 (533160) 115 kV Bus a. Apply Fault at the 41CALIF3 (533160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.3. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_379 | Single Phase Fault with Stuck Breaker on 41CALIF3 (533160) 115 kV Bus a. Apply Fault at the 41CALIF3 (533160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.3. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_38 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_380 | Single Phase Fault with Stuck Breaker on 87TH 7 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.3. 87TH 1X1 (532818) 13.8 kV to 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_380 | Single Phase Fault with Stuck Breaker on 87TH 7 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.3. 87TH 1X1 (532818) 13.8 kV to 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_381 | Single Phase Fault with Stuck Breaker on CHAPMAN3 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_381 | Single Phase Fault with Stuck Breaker on CHAPMAN3 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_382 | Single Phase Fault with Stuck Breaker on ANZIO 3 (533321) 115 kV Bus a. Apply Fault at the ANZIO 3 (533321) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.3. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_382 | Single Phase Fault with Stuck Breaker on ANZIO 3 (533321) 115 kV Bus a. Apply Fault at the ANZIO 3 (533321) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.3. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_383 | Single Phase Fault with Stuck Breaker on CHAPMAN3 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_383 | Single Phase Fault with Stuck Breaker on CHAPMAN3 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_384 | Single Phase Fault with Stuck Breaker on CHAPMAN3 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_384 | Single Phase Fault with Stuck Breaker on CHAPMAN3 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_385 | Single Phase Fault with Stuck Breaker on CLAYCTR3 (533323) 115 kV Bus a. Apply Fault at the CLAYCTR3 (533323) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCSS3 (533320) 115.0 kV to CLAYCTR3 (533323) 115.0 kV Transmission Circuit #1 b.2. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_385 | Single Phase Fault with Stuck Breaker on CLAYCTR3 (533323) 115 kV Bus a. Apply Fault at the CLAYCTR3 (533323) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCSS3 (533320) 115.0 kV to CLAYCTR3 (533323) 115.0 kV Transmission Circuit #1 b.2. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_386 | Single Phase Fault with Stuck Breaker on WJCCTYW3 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_386 | Single Phase Fault with Stuck Breaker on WJCCTYW3 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_387 | Single Phase Fault with Stuck Breaker on CIRCLE 3 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.4. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.5. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.6. CIRCLE 3 (533413) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_387 | Single Phase Fault with Stuck Breaker on CIRCLE 3 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.4. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.5. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.6. CIRCLE 3 (533413) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_388 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_388 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_389 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.2. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.5. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_389 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.2. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.5. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_39 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_390 | Single Phase Fault with Stuck Breaker on HEC GT 3 (533421) 115 kV Bus a. Apply Fault at the HEC GT 3 (533421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.5. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_390 | Single Phase Fault with Stuck Breaker on HEC GT 3 (533421) 115 kV Bus a. Apply Fault at the HEC GT 3 (533421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.5. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_391 | Single Phase Fault with Stuck Breaker on CITIES 3 (533414) 115 kV Bus a. Apply Fault at the CITIES 3 (533414) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.3. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.4. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_391 | Single Phase Fault with Stuck Breaker on CITIES 3 (533414) 115 kV Bus a. Apply Fault at the CITIES 3 (533414) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.3. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.4. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_392 | Single Phase Fault with Stuck Breaker on MANVILE3 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to MCPHGT4 (532705) 13.8 kV Two Winding #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_392 | Single Phase Fault with Stuck Breaker on MANVILE3 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to MCPHGT4 (532705) 13.8 kV Two Winding #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_393 | Single Phase Fault with Stuck Breaker on MCPHER 3 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to MCPHGT3 (532704) 13.8 kV Two Winding #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_393 | Single Phase Fault with Stuck Breaker on MCPHER 3 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to MCPHGT3 (532704) 13.8 kV Two Winding #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_394 | Single Phase Fault with Stuck Breaker on COLINE 3 (533153) 115 kV Bus a. Apply Fault at the COLINE 3 (533153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.3. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.5. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_394 | Single Phase Fault with Stuck Breaker on COLINE 3 (533153) 115 kV Bus a. Apply Fault at the COLINE 3 (533153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.3. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.5. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_395 | Single Phase Fault with Stuck Breaker on BISMARK3 (533234) 115 kV Bus a. Apply Fault at the BISMARK3 (533234) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.5. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_395 | Single Phase Fault with Stuck Breaker on BISMARK3 (533234) 115 kV Bus a. Apply Fault at the BISMARK3 (533234) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.5. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_396 | Single Phase Fault with Stuck Breaker on FT JCT 3 (533328) 115 kV Bus a. Apply Fault at the FT JCT 3 (533328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.3. FT JCT 3 (533328) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_396 | Single Phase Fault with Stuck Breaker on FT JCT 3 (533328) 115 kV Bus a. Apply Fault at the FT JCT 3 (533328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.3. FT JCT 3 (533328) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_397 | Single Phase Fault with Stuck Breaker on JCTCTY 3 (533330) 115 kV Bus a. Apply Fault at the JCTCTY 3 (533330) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.3. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_397 | Single Phase Fault with Stuck Breaker on JCTCTY 3 (533330) 115 kV Bus a. Apply Fault at the JCTCTY 3 (533330) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.3. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_398 | Single Phase Fault with Stuck Breaker on FT JCT 3 (533328) 115 kV Bus a. Apply Fault at the FT JCT 3 (533328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_398 | Single Phase Fault with Stuck Breaker on FT JCT 3 (533328) 115 kV Bus a. Apply Fault at the FT JCT 3 (533328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_399 | Single Phase Fault with Stuck Breaker on FT JCT 3 (533328) 115 kV Bus a. Apply Fault at the FT JCT 3 (533328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_399 | Single Phase Fault with Stuck Breaker on FT JCT 3 (533328) 115 kV Bus a. Apply Fault at the FT JCT 3 (533328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on 5LEVASY (300320) 161 kV Bus a. Apply Fault at the 5LEVASY (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.4. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.5. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_4 | Single Phase Fault with Stuck Breaker on 5LEVASY (300320) 161 kV Bus a. Apply Fault at the 5LEVASY (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.4. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.5. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_40 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_400 | Single Phase Fault with Stuck Breaker on HEC 3 (533419) 115 kV Bus a. Apply Fault at the HEC 3 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.4. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_400 | Single Phase Fault with Stuck Breaker on HEC 3 (533419) 115 kV Bus a. Apply Fault at the HEC 3 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.4. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_401 | Single Phase Fault with Stuck Breaker on HEC 3 (533419) 115 kV Bus a. Apply Fault at the HEC 3 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_401 | Single Phase Fault with Stuck Breaker on HEC 3 (533419) 115 kV Bus a. Apply Fault at the HEC 3 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_402 | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLVL3 (533152) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. KELLY 3 (533217) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.6. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_402 | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLVL3 (533152) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. KELLY 3 (533217) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.6. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_403 | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_403 | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_404 | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_404 | Single Phase Fault with Stuck Breaker on HOYT 7 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_405 | Single Phase Fault with Stuck Breaker on INDNOLA3 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_405 | Single Phase Fault with Stuck Breaker on INDNOLA3 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_406 | Single Phase Fault with Stuck Breaker on INDNOLA3 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_406 | Single Phase Fault with Stuck Breaker on INDNOLA3 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_407 | Single Phase Fault with Stuck Breaker on INDNOLA3 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to N TYLER3 (533168) 115.0 kV Transmission Circuit #1 b.3. N TYLER3 (533168) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_407 | Single Phase Fault with Stuck Breaker on INDNOLA3 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to N TYLER3 (533168) 115.0 kV Transmission Circuit #1 b.3. N TYLER3 (533168) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_408 | Single Phase Fault with Stuck Breaker on JARBALO3 (533244) 115 kV Bus a. Apply Fault at the JARBALO3 (533244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.4. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.5. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.6. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.7. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_408 | Single Phase Fault with Stuck Breaker on JARBALO3 (533244) 115 kV Bus a. Apply Fault at the JARBALO3 (533244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.4. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.5. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.6. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.7. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_409 | Single Phase Fault with Stuck Breaker on JARBALO3 (533244) 115 kV Bus a. Apply Fault at the JARBALO3 (533244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.3. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.4. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.5. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.6. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.7. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.8. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_409 | Single Phase Fault with Stuck Breaker on JARBALO3 (533244) 115 kV Bus a. Apply Fault at the JARBALO3 (533244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.3. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.4. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.5. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.6. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.7. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.8. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_41 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_410 | Single Phase Fault with Stuck Breaker on JARBALO3 (533244) 115 kV Bus a. Apply Fault at the JARBALO3 (533244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.4. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.5. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.6. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.7. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.8. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_410 | Single Phase Fault with Stuck Breaker on JARBALO3 (533244) 115 kV Bus a. Apply Fault at the JARBALO3 (533244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.4. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.5. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.6. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.7. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.8. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_411 | Single Phase Fault with Stuck Breaker on KELLY 5 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLVL3 (533152) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.2. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.3. HTI 3 (533164) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. ENEMAHA3 (533210) 115.0 kV to KELLY 3 (533217) 115.0 kV Transmission Circuit #1 b.5. KELLY 3 (533217) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.6. KELLY 3 (533217) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.7. KELLY 3 (533217) 115.0 kV to KELLY 5 (532913) 161.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_411 | Single Phase Fault with Stuck Breaker on KELLY 5 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLVL3 (533152) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.2. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.3. HTI 3 (533164) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. ENEMAHA3 (533210) 115.0 kV to KELLY 3 (533217) 115.0 kV Transmission Circuit #1 b.5. KELLY 3 (533217) 115.0 kV to GOFF 3 (533331) 115.0 kV Transmission Circuit #1 b.6. KELLY 3 (533217) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.7. KELLY 3 (533217) 115.0 kV to KELLY 5 (532913) 161.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_412 | Single Phase Fault with Stuck Breaker on LANG 7 (532769) 345 kV Bus a. Apply Fault at the LANG 7 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.3. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.4. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.5. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_412 | Single Phase Fault with Stuck Breaker on LANG 7 (532769) 345 kV Bus a. Apply Fault at the LANG 7 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.3. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.4. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.5. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_413 | Single Phase Fault with Stuck Breaker on STULL T3 (533270) 115 kV Bus a. Apply Fault at the STULL T3 (533270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.3. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_413 | Single Phase Fault with Stuck Breaker on STULL T3 (533270) 115 kV Bus a. Apply Fault at the STULL T3 (533270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.3. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_414 | Single Phase Fault with Stuck Breaker on MCDOWEL6 (532862) 230 kV Bus a. Apply Fault at the MCDOWEL6 (532862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT3 (533326) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 b.3. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 b.4. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 b.5. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.6. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.7. MCDOWEL3 (533335) 115.0 kV to MCDOWEL6 (532862) 230.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_414 | Single Phase Fault with Stuck Breaker on MCDOWEL6 (532862) 230 kV Bus a. Apply Fault at the MCDOWEL6 (532862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT3 (533326) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 b.3. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 b.4. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 b.5. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.6. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.7. MCDOWEL3 (533335) 115.0 kV to MCDOWEL6 (532862) 230.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_415 | Single Phase Fault with Stuck Breaker on MIDLADS3 (533260) 115 kV Bus a. Apply Fault at the MIDLADS3 (533260) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_415 | Single Phase Fault with Stuck Breaker on MIDLADS3 (533260) 115 kV Bus a. Apply Fault at the MIDLADS3 (533260) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_416 | Single Phase Fault with Stuck Breaker on MOUND 4 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.7. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_416 | Single Phase Fault with Stuck Breaker on MOUND 4 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.7. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_417 | Single Phase Fault with Stuck Breaker on MOUND 4 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_417 | Single Phase Fault with Stuck Breaker on MOUND 4 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_418 | Single Phase Fault with Stuck Breaker on NORTHST3 (533370) 115 kV Bus a. Apply Fault at the NORTHST3 (533370) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #2 b.3. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.4. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #2 b.5. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.6. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_418 | Single Phase Fault with Stuck Breaker on NORTHST3 (533370) 115 kV Bus a. Apply Fault at the NORTHST3 (533370) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #2 b.3. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.4. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #2 b.5. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.6. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_419 | Single Phase Fault with Stuck Breaker on NW LEAV3 (533259) 115 kV Bus a. Apply Fault at the NW LEAV3 (533259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 b.2. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.3. NW LEAV3 (533259) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.4. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.5. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_419 | Single Phase Fault with Stuck Breaker on NW LEAV3 (533259) 115 kV Bus a. Apply Fault at the NW LEAV3 (533259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 b.2. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.3. NW LEAV3 (533259) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.4. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.5. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_42 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_420 | Single Phase Fault with Stuck Breaker on PENTAGN3 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.4. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.5. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.6. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_420 | Single Phase Fault with Stuck Breaker on PENTAGN3 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.4. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.5. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.6. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_421 | Single Phase Fault with Stuck Breaker on PENTAGN3 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.2. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.4. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.5. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_421 | Single Phase Fault with Stuck Breaker on PENTAGN3 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.2. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.4. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.5. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_422 | Single Phase Fault with Stuck Breaker on PENTAGN3 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.4. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.5. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_422 | Single Phase Fault with Stuck Breaker on PENTAGN3 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.4. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.5. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_423 | Single Phase Fault with Stuck Breaker on QUINTON3 (533172) 115 kV Bus a. Apply Fault at the QUINTON3 (533172) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. QUINTON3 (533172) 115.0 kV to 12&CLAY3 (533184) 115.0 kV Transmission Circuit #1 b.3. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.4. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_423 | Single Phase Fault with Stuck Breaker on QUINTON3 (533172) 115 kV Bus a. Apply Fault at the QUINTON3 (533172) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. QUINTON3 (533172) 115.0 kV to 12&CLAY3 (533184) 115.0 kV Transmission Circuit #1 b.3. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.4. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_424 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. RENO 1X1 (532807) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_424 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. RENO 1X1 (532807) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_425 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. RENO 2X1 (532810) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_425 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. RENO 2X1 (532810) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_426 | Single Phase Fault with Stuck Breaker on RENO 3 (533416) 115 kV Bus a. Apply Fault at the RENO 3 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_426 | Single Phase Fault with Stuck Breaker on RENO 3 (533416) 115 kV Bus a. Apply Fault at the RENO 3 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_427 | Single Phase Fault with Stuck Breaker on NORTHST3 (533370) 115 kV Bus a. Apply Fault at the NORTHST3 (533370) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.3. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #2 b.4. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.5. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_427 | Single Phase Fault with Stuck Breaker on NORTHST3 (533370) 115 kV Bus a. Apply Fault at the NORTHST3 (533370) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.3. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #2 b.4. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.5. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_428 | Single Phase Fault with Stuck Breaker on 29EVENG3 (533185) 115 kV Bus a. Apply Fault at the 29EVENG3 (533185) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_428 | Single Phase Fault with Stuck Breaker on 29EVENG3 (533185) 115 kV Bus a. Apply Fault at the 29EVENG3 (533185) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_429 | Single Phase Fault with Stuck Breaker on SENECA 3 (533337) 115 kV Bus a. Apply Fault at the SENECA 3 (533337) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 3 (533217) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.2. MARSHAL3 (533303) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 b.3. BAILEYV3 (533322) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.4. BAILEYV3 (533322) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 b.5. SENECA 3 (533337) 115.0 kV to TCSENCA3 (533348) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_429 | Single Phase Fault with Stuck Breaker on SENECA 3 (533337) 115 kV Bus a. Apply Fault at the SENECA 3 (533337) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 3 (533217) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.2. MARSHAL3 (533303) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 b.3. BAILEYV3 (533322) 115.0 kV to SENECA 3 (533337) 115.0 kV Transmission Circuit #1 b.4. BAILEYV3 (533322) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 b.5. SENECA 3 (533337) 115.0 kV to TCSENCA3 (533348) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP#1 (541165) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.2. S.HARP#2 (541166) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.3. S.HARP#3 (541167) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.4. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_43 | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP#1 (541165) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.2. S.HARP#2 (541166) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.3. S.HARP#3 (541167) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.4. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_430 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 b.2. STRAN3 1 (532816) 14.4 kV to STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_430 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 b.2. STRAN3 1 (532816) 14.4 kV to STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_431 | Single Phase Fault with Stuck Breaker on STRANGR3 (533268) 115 kV Bus a. Apply Fault at the STRANGR3 (533268) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.2. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_431 | Single Phase Fault with Stuck Breaker on STRANGR3 (533268) 115 kV Bus a. Apply Fault at the STRANGR3 (533268) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.2. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_432 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.2. STRAN1 1 (532811) 14.4 kV to STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_432 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.2. STRAN1 1 (532811) 14.4 kV to STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_433 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.3. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.4. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.5. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_433 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.3. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.4. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.5. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_434 | Single Phase Fault with Stuck Breaker on SWLWRNC3 (533271) 115 kV Bus a. Apply Fault at the SWLWRNC3 (533271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.8. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_434 | Single Phase Fault with Stuck Breaker on SWLWRNC3 (533271) 115 kV Bus a. Apply Fault at the SWLWRNC3 (533271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.8. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_435 | Single Phase Fault with Stuck Breaker on TECHILL6 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.8. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.9. AEC E1 (533886) 34.5 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.10. AEC E1 (533886) 34.5 kV to AEC W1 (533887) 34.5 kV Transmission Circuit #z1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_435 | Single Phase Fault with Stuck Breaker on TECHILL6 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.8. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.9. AEC E1 (533886) 34.5 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.10. AEC E1 (533886) 34.5 kV to AEC W1 (533887) 34.5 kV Transmission Circuit #z1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_436 | Single Phase Fault with Stuck Breaker on TECHILL6 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.4. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.5. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.7. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.8. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.10. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.11. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_436 | Single Phase Fault with Stuck Breaker on TECHILL6 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.4. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.5. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.7. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.8. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.10. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.11. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_437 | Single Phase Fault with Stuck Breaker on HALLMRK3 (533242) 115 kV Bus a. Apply Fault at the HALLMRK3 (533242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.4. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_437 | Single Phase Fault with Stuck Breaker on HALLMRK3 (533242) 115 kV Bus a. Apply Fault at the HALLMRK3 (533242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.4. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_438 | Single Phase Fault with Stuck Breaker on SPRUCE 3 (533266) 115 kV Bus a. Apply Fault at the SPRUCE 3 (533266) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.2. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.3. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_438 | Single Phase Fault with Stuck Breaker on SPRUCE 3 (533266) 115 kV Bus a. Apply Fault at the SPRUCE 3 (533266) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.2. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.3. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_439 | Single Phase Fault with Stuck Breaker on TIMBRLN3 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.5. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_439 | Single Phase Fault with Stuck Breaker on TIMBRLN3 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.5. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.4. NORTON 5 (543064) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_44 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.4. NORTON 5 (543064) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_440 | Single Phase Fault with Stuck Breaker on TIMBRLN3 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_440 | Single Phase Fault with Stuck Breaker on TIMBRLN3 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_441 | Single Phase Fault with Stuck Breaker on WALNUT 3 (533220) 115 kV Bus a. Apply Fault at the WALNUT 3 (533220) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 b.3. WALNUT 3 (533220) 115.0 kV to TCSEVRN3 (533226) 115.0 kV Transmission Circuit #1 b.4. WALNUT 3 (533220) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.5. WALNUT 3 (533220) 115.0 kV to CHEYENN2 (533480) 115.0 kV Transmission Circuit #1 b.6. WALNUT 3 (533220) 115.0 kV to WALNUT 2 (533484) 69.0 kV to WALNUT 1 (533451) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_441 | Single Phase Fault with Stuck Breaker on WALNUT 3 (533220) 115 kV Bus a. Apply Fault at the WALNUT 3 (533220) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 b.3. WALNUT 3 (533220) 115.0 kV to TCSEVRN3 (533226) 115.0 kV Transmission Circuit #1 b.4. WALNUT 3 (533220) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.5. WALNUT 3 (533220) 115.0 kV to CHEYENN2 (533480) 115.0 kV Transmission Circuit #1 b.6. WALNUT 3 (533220) 115.0 kV to WALNUT 2 (533484) 69.0 kV to WALNUT 1 (533451) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_442 | Single Phase Fault with Stuck Breaker on WEMPORI3 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.6. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.7. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.8. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_442 | Single Phase Fault with Stuck Breaker on WEMPORI3 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.6. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.7. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.8. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_443 | Single Phase Fault with Stuck Breaker on WJCCTY 3 (533342) 115 kV Bus a. Apply Fault at the WJCCTY 3 (533342) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.3. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.5. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_443 | Single Phase Fault with Stuck Breaker on WJCCTY 3 (533342) 115 kV Bus a. Apply Fault at the WJCCTY 3 (533342) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.3. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.5. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_444 | Single Phase Fault with Stuck Breaker on WMCPHER3 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_444 | Single Phase Fault with Stuck Breaker on WMCPHER3 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_445 | Single Phase Fault with Stuck Breaker on WMCPHER3 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_445 | Single Phase Fault with Stuck Breaker on WMCPHER3 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_446 | Single Phase Fault with Stuck Breaker on LYONS 3 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_446 | Single Phase Fault with Stuck Breaker on LYONS 3 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_447 | Single Phase Fault with Stuck Breaker on WMCPHER3 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_447 | Single Phase Fault with Stuck Breaker on WMCPHER3 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_448 | Single Phase Fault with Stuck Breaker on BUTLERS4 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.6. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.7. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_448 | Single Phase Fault with Stuck Breaker on BUTLERS4 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.6. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.7. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_449 | Single Phase Fault with Stuck Breaker on ELPASOE4 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 b.6. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.8. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_449 | Single Phase Fault with Stuck Breaker on ELPASOE4 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 b.6. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.8. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_45 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_450 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 b.5. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_450 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 b.5. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_451 | Single Phase Fault with Stuck Breaker on GILL E 4 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_451 | Single Phase Fault with Stuck Breaker on GILL E 4 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_452 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.7. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.8. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_452 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.7. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.8. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_453 | Single Phase Fault with Stuck Breaker on NOEASTW4 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.5. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 b.6. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_453 | Single Phase Fault with Stuck Breaker on NOEASTW4 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.5. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 b.6. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_454 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.7. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_454 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.7. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_455 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.7. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_455 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.7. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_456 | Single Phase Fault with Stuck Breaker on WACO N 4 (533073) 138 kV Bus a. Apply Fault at the WACO N 4 (533073) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.2. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 b.3. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_456 | Single Phase Fault with Stuck Breaker on WACO N 4 (533073) 138 kV Bus a. Apply Fault at the WACO N 4 (533073) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.2. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 b.3. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_457 | Single Phase Fault with Stuck Breaker on WACO S 4 (533071) 138 kV Bus a. Apply Fault at the WACO S 4 (533071) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.2. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 b.3. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_457 | Single Phase Fault with Stuck Breaker on WACO S 4 (533071) 138 kV Bus a. Apply Fault at the WACO S 4 (533071) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.2. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 b.3. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_458 | Single Phase Fault with Stuck Breaker on 4VAN 3 (533159) 115 kV Bus a. Apply Fault at the 4VAN 3 (533159) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4VAN 3 (533159) 115.0 kV to 2MADISN3 (533174) 115.0 kV Transmission Circuit #1 b.2. 4VAN 3 (533159) 115.0 kV to 4VAN S 3 (533200) 115.0 kV Transmission Circuit #z1 b.3. 4VAN 3 (533159) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #z1 b.4. 12&CLAY3 (533184) 115.0 kV to 4VAN S 3 (533200) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_458 | Single Phase Fault with Stuck Breaker on 4VAN 3 (533159) 115 kV Bus a. Apply Fault at the 4VAN 3 (533159) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4VAN 3 (533159) 115.0 kV to 2MADISN3 (533174) 115.0 kV Transmission Circuit #1 b.2. 4VAN 3 (533159) 115.0 kV to 4VAN S 3 (533200) 115.0 kV Transmission Circuit #z1 b.3. 4VAN 3 (533159) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #z1 b.4. 12&CLAY3 (533184) 115.0 kV to 4VAN S 3 (533200) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_459 | Single Phase Fault with Stuck Breaker on MIDLAND6 (532855) 230 kV Bus a. Apply Fault at the MIDLAND6 (532855) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.5. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 b.6. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.7. MIDLADN3 (533252) 115.0 kV to MIDLAND6 (532855) 230.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_459 | Single Phase Fault with Stuck Breaker on MIDLAND6 (532855) 230 kV Bus a. Apply Fault at the MIDLAND6 (532855) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.5. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 b.6. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.7. MIDLADN3 (533252) 115.0 kV to MIDLAND6 (532855) 230.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV (Trip Generation) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_46 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV (Trip Generation) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_460 | Single Phase Fault with Stuck Breaker on TECHILL5 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 b.6. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILW3 (533181) 115.0 kV to TECHILL5 (532920) 161.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 b.13. TECHIL4X (533885) 12.5 kV to TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_460 | Single Phase Fault with Stuck Breaker on TECHILL5 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 b.6. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILW3 (533181) 115.0 kV to TECHILL5 (532920) 161.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 b.13. TECHIL4X (533885) 12.5 kV to TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_461 | Single Phase Fault with Stuck Breaker on 5THMHILB1 (300120) 161 kV Bus a. Apply Fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_461 | Single Phase Fault with Stuck Breaker on 5THMHILB1 (300120) 161 kV Bus a. Apply Fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_462 | Single Phase Fault with Stuck Breaker on 5NOVELY_SW (300106) 161 kV Bus a. Apply Fault at the 5NOVELY_SW (300106) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5NEWARK (300363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_462 | Single Phase Fault with Stuck Breaker on 5NOVELY_SW (300106) 161 kV Bus a. Apply Fault at the 5NOVELY_SW (300106) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5NEWARK (300363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_463 | Single Phase Fault with Stuck Breaker on 5ADAIR1 (344004) 161 kV Bus a. Apply Fault at the 5ADAIR1 (344004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 b.4. 4FREDERCK (347084) 138.0 kV to 4MERE_138 (347680) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_463 | Single Phase Fault with Stuck Breaker on 5ADAIR1 (344004) 161 kV Bus a. Apply Fault at the 5ADAIR1 (344004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 b.4. 4FREDERCK (347084) 138.0 kV to 4MERE_138 (347680) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_464 | Single Phase Fault with Stuck Breaker on 7BELLEAU (344102) 345 kV Bus a. Apply Fault at the 7BELLEAU (344102) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 b.2. 7BELLEAU (344102) 345.0 kV to 7ENON_TP (344536) 345.0 kV Transmission Circuit #1 b.3. 7BELLEAU (344102) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_464 | Single Phase Fault with Stuck Breaker on 7BELLEAU (344102) 345 kV Bus a. Apply Fault at the 7BELLEAU (344102) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 b.2. 7BELLEAU (344102) 345.0 kV to 7ENON_TP (344536) 345.0 kV Transmission Circuit #1 b.3. 7BELLEAU (344102) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_465 | Single Phase Fault with Stuck Breaker on 4BELLEAU (344103) 138 kV Bus a. Apply Fault at the 4BELLEAU (344103) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 b.2. 4BELLEAU (344103) 138.0 kV to 4FTZUM T3 (344603) 138.0 kV Transmission Circuit #1 b.3. 4BELLEAU (344103) 138.0 kV to 4FTZUM T1 (344604) 138.0 kV Transmission Circuit #1 b.4. 4BELLEAU (344103) 138.0 kV to 4OFALN TP (345359) 138.0 kV Transmission Circuit #z b.5. 4BELLEAU (344103) 138.0 kV to 4OFALN TP2 (345360) 138.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_465 | Single Phase Fault with Stuck Breaker on 4BELLEAU (344103) 138 kV Bus a. Apply Fault at the 4BELLEAU (344103) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 b.2. 4BELLEAU (344103) 138.0 kV to 4FTZUM T3 (344603) 138.0 kV Transmission Circuit #1 b.3. 4BELLEAU (344103) 138.0 kV to 4FTZUM T1 (344604) 138.0 kV Transmission Circuit #1 b.4. 4BELLEAU (344103) 138.0 kV to 4OFALN TP (345359) 138.0 kV Transmission Circuit #z b.5. 4BELLEAU (344103) 138.0 kV to 4OFALN TP2 (345360) 138.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_466 | Single Phase Fault with Stuck Breaker on 5MOBERLY (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.2. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.5. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_466 | Single Phase Fault with Stuck Breaker on 5MOBERLY (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.2. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.5. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_467 | Single Phase Fault with Stuck Breaker on 7OVERTON (345408) 345 kV Bus a. Apply Fault at the 7OVERTON (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_467 | Single Phase Fault with Stuck Breaker on 7OVERTON (345408) 345 kV Bus a. Apply Fault at the 7OVERTON (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_468 | Single Phase Fault with Stuck Breaker on 5APCH TP (344026) 161 kV Bus a. Apply Fault at the 5APCH TP (344026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.5. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_468 | Single Phase Fault with Stuck Breaker on 5APCH TP (344026) 161 kV Bus a. Apply Fault at the 5APCH TP (344026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.5. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_469 | Single Phase Fault with Stuck Breaker on 4OFALN TP (345359) 138 kV Bus a. Apply Fault at the 4OFALN TP (345359) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5TROYB1 (300606) 161.0 kV to 5DARD12 (344449) 161.0 kV Transmission Circuit #1 b.2. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 b.3. 4BELLEAU (344103) 138.0 kV to 4FTZUM T1 (344604) 138.0 kV Transmission Circuit #1 b.4. 4BELLEAU (344103) 138.0 kV to 4OFALN TP (345359) 138.0 kV Transmission Circuit #z b.5. 4DARD12 (344448) 138.0 kV to 4OFALN TP (345359) 138.0 kV Transmission Circuit #1 b.6. 5DARD12 (344449) 161.0 kV to 4DARD12 (344448) 138.0 kV Two Winding #1 b.7. 5DARD12 (344449) 161.0 kV to 4DARD12 (344448) 138.0 kV Two Winding #2 b.8. 1OFALLON (346112) 34.5 kV to 4OFALN TP (345359) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_469 | Single Phase Fault with Stuck Breaker on 4OFALN TP (345359) 138 kV Bus a. Apply Fault at the 4OFALN TP (345359) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5TROYB1 (300606) 161.0 kV to 5DARD12 (344449) 161.0 kV Transmission Circuit #1 b.2. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 b.3. 4BELLEAU (344103) 138.0 kV to 4FTZUM T1 (344604) 138.0 kV Transmission Circuit #1 b.4. 4BELLEAU (344103) 138.0 kV to 4OFALN TP (345359) 138.0 kV Transmission Circuit #z b.5. 4DARD12 (344448) 138.0 kV to 4OFALN TP (345359) 138.0 kV Transmission Circuit #1 b.6. 5DARD12 (344449) 161.0 kV to 4DARD12 (344448) 138.0 kV Two Winding #1 b.7. 5DARD12 (344449) 161.0 kV to 4DARD12 (344448) 138.0 kV Two Winding #2 b.8. 1OFALLON (346112) 34.5 kV to 4OFALN TP (345359) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV (Trip Generation) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_47 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV (Trip Generation) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_470 | Single Phase Fault with Stuck Breaker on 4MCCLAY 3 (345080) 138 kV Bus a. Apply Fault at the 4MCCLAY 3 (345080) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 b.2. 4BELLEAU (344103) 138.0 kV to 4FTZUM T3 (344603) 138.0 kV Transmission Circuit #1 b.3. 4BELLEAU (344103) 138.0 kV to 4OFALN TP (345359) 138.0 kV Transmission Circuit #z b.4. 4FTZUM 3 (344601) 138.0 kV to 4FTZUM T3 (344603) 138.0 kV Transmission Circuit #1 b.5. 4FTZUM T3 (344603) 138.0 kV to 4MCCLAY 3 (345080) 138.0 kV Transmission Circuit #1 b.6. 4MCCLAY 2 (345078) 138.0 kV to 4MCCLAY 3 (345080) 138.0 kV Transmission Circuit #z b.7. 1FTZUM (346053) 34.5 kV to 4FTZUM 3 (344601) 138.0 kV Two Winding #1 b.8. 1MC CLAY (346103) 34.5 kV to 4MCCLAY 3 (345080) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_470 | Single Phase Fault with Stuck Breaker on 4MCCLAY 3 (345080) 138 kV Bus a. Apply Fault at the 4MCCLAY 3 (345080) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 4BELLEAU (344103) 138.0 kV Two Winding #1 b.2. 4BELLEAU (344103) 138.0 kV to 4FTZUM T3 (344603) 138.0 kV Transmission Circuit #1 b.3. 4BELLEAU (344103) 138.0 kV to 4OFALN TP (345359) 138.0 kV Transmission Circuit #z b.4. 4FTZUM 3 (344601) 138.0 kV to 4FTZUM T3 (344603) 138.0 kV Transmission Circuit #1 b.5. 4FTZUM T3 (344603) 138.0 kV to 4MCCLAY 3 (345080) 138.0 kV Transmission Circuit #1 b.6. 4MCCLAY 2 (345078) 138.0 kV to 4MCCLAY 3 (345080) 138.0 kV Transmission Circuit #z b.7. 1FTZUM (346053) 34.5 kV to 4FTZUM 3 (344601) 138.0 kV Two Winding #1 b.8. 1MC CLAY (346103) 34.5 kV to 4MCCLAY 3 (345080) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_471 | Single Phase Fault with Stuck Breaker on 7SIOUX (345747) 345 kV Bus a. Apply Fault at the 7SIOUX (345747) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 b.2. 7SIOUX (345747) 345.0 kV to 4SIOUX (345754) 138.0 kV Two Winding #1 b.3. 7SIOUX (345747) 345.0 kV to 7ROXFORD (348151) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_471 | Single Phase Fault with Stuck Breaker on 7SIOUX (345747) 345 kV Bus a. Apply Fault at the 7SIOUX (345747) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 b.2. 7SIOUX (345747) 345.0 kV to 4SIOUX (345754) 138.0 kV Two Winding #1 b.3. 7SIOUX (345747) 345.0 kV to 7ROXFORD (348151) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_472 | Single Phase Fault with Stuck Breaker on 7SIOUX (345747) 345 kV Bus a. Apply Fault at the 7SIOUX (345747) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 b.2. 7MASON 1 (345045) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_472 | Single Phase Fault with Stuck Breaker on 7SIOUX (345747) 345 kV Bus a. Apply Fault at the 7SIOUX (345747) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BELLEAU (344102) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 b.2. 7MASON 1 (345045) 345.0 kV to 7SIOUX (345747) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_473 | Single Phase Fault with Stuck Breaker on SUB T HSK 3 (636645) 345 kV Bus a. Apply Fault at the SUB T HSK 3 (636645) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MAYWOOD (345435) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.3. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_473 | Single Phase Fault with Stuck Breaker on SUB T HSK 3 (636645) 345 kV Bus a. Apply Fault at the SUB T HSK 3 (636645) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MAYWOOD (345435) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.3. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_474 | Single Phase Fault with Stuck Breaker on 7HERLEMAN (347010) 345 kV Bus a. Apply Fault at the 7HERLEMAN (347010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MAYWOOD (345435) 345.0 kV to 7HERLEMAN (347010) 345.0 kV Transmission Circuit #1 b.2. 7HERLEMAN (347010) 345.0 kV to 4HERLEMAN (347080) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_474 | Single Phase Fault with Stuck Breaker on 7HERLEMAN (347010) 345 kV Bus a. Apply Fault at the 7HERLEMAN (347010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MAYWOOD (345435) 345.0 kV to 7HERLEMAN (347010) 345.0 kV Transmission Circuit #1 b.2. 7HERLEMAN (347010) 345.0 kV to 4HERLEMAN (347080) 138.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_475 | Single Phase Fault with Stuck Breaker on 7HERLEMAN (347010) 345 kV Bus a. Apply Fault at the 7HERLEMAN (347010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MAYWOOD (345435) 345.0 kV to 7HERLEMAN (347010) 345.0 kV Transmission Circuit #1 b.2. 7HERLEMAN (347010) 345.0 kV to 7MDOS_345 (347688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_475 | Single Phase Fault with Stuck Breaker on 7HERLEMAN (347010) 345 kV Bus a. Apply Fault at the 7HERLEMAN (347010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MAYWOOD (345435) 345.0 kV to 7HERLEMAN (347010) 345.0 kV Transmission Circuit #1 b.2. 7HERLEMAN (347010) 345.0 kV to 7MDOS_345 (347688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_476 | Single Phase Fault with Stuck Breaker on 5ADAIR1 (344004) 161 kV Bus a. Apply Fault at the 5ADAIR1 (344004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR2 (344001) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #z b.4. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.5. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_476 | Single Phase Fault with Stuck Breaker on 5ADAIR1 (344004) 161 kV Bus a. Apply Fault at the 5ADAIR1 (344004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR2 (344001) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #z b.4. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.5. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_477 | Single Phase Fault with Stuck Breaker on 5ADAIR3 (344006) 161 kV Bus a. Apply Fault at the 5ADAIR3 (344006) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR2 (344001) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #z b.4. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.5. 5ADAIR3 (344006) 161.0 kV to 5ZACHARY (344010) 161.0 kV Transmission Circuit #1 b.6. 2ADAIR 2 (346006) 69.0 kV to 5ADAIR3 (344006) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_477 | Single Phase Fault with Stuck Breaker on 5ADAIR3 (344006) 161 kV Bus a. Apply Fault at the 5ADAIR3 (344006) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NOVELY_SW (300106) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR2 (344001) 161.0 kV to 5ADAIR3 (344006) 161.0 kV Transmission Circuit #z b.4. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.5. 5ADAIR3 (344006) 161.0 kV to 5ZACHARY (344010) 161.0 kV Transmission Circuit #1 b.6. 2ADAIR 2 (346006) 69.0 kV to 5ADAIR3 (344006) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_478 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_478 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_479 | Single Phase Fault with Stuck Breaker on APANOSE5 (631112) 161 kV Bus a. Apply Fault at the APANOSE5 (631112) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODY 5 (631110) 161.0 kV to WAPELLO8 (630048) 69.0 kV Two Winding #2 b.2. WOODY 5 (631110) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.3. WOODY 5 (631110) 161.0 kV to OTTUMWA5 (631115) 161.0 kV Transmission Circuit #2 b.4. APANOSE5 (631112) 161.0 kV to APANOSE8 (630033) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_479 | Single Phase Fault with Stuck Breaker on APANOSE5 (631112) 161 kV Bus a. Apply Fault at the APANOSE5 (631112) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODY 5 (631110) 161.0 kV to WAPELLO8 (630048) 69.0 kV Two Winding #2 b.2. WOODY 5 (631110) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.3. WOODY 5 (631110) 161.0 kV to OTTUMWA5 (631115) 161.0 kV Transmission Circuit #2 b.4. APANOSE5 (631112) 161.0 kV to APANOSE8 (630033) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_48 | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_480 | Single Phase Fault with Stuck Breaker on APANOSE5 (631112) 161 kV Bus a. Apply Fault at the APANOSE5 (631112) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.2. WOODY 5 (631110) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.3. APANOSE5 (631112) 161.0 kV to APANOSE8 (630033) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_480 | Single Phase Fault with Stuck Breaker on APANOSE5 (631112) 161 kV Bus a. Apply Fault at the APANOSE5 (631112) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5ADAIR2 (344001) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.2. WOODY 5 (631110) 161.0 kV to APANOSE5 (631112) 161.0 kV Transmission Circuit #1 b.3. APANOSE5 (631112) 161.0 kV to APANOSE8 (630033) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_481 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_481 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_482 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_482 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_483 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_483 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_484 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_484 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_485 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_485 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_486 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_486 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_487 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_487 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_488 | Single Phase Fault with Stuck Breaker on HILLS 3 (636400) 345 kV Bus a. Apply Fault at the HILLS 3 (636400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.3. HILLS 3 (636400) 345.0 kV to HILLS 5 (636401) 161.0 kV to HILL1XT9 (636406) 13.8 kV Three Winding #1 b.6. HILLS 3 (636400) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_488 | Single Phase Fault with Stuck Breaker on HILLS 3 (636400) 345 kV Bus a. Apply Fault at the HILLS 3 (636400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.3. HILLS 3 (636400) 345.0 kV to HILLS 5 (636401) 161.0 kV to HILL1XT9 (636406) 13.8 kV Three Winding #1 b.6. HILLS 3 (636400) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_489 | Single Phase Fault with Stuck Breaker on HILLS 3 (636400) 345 kV Bus a. Apply Fault at the HILLS 3 (636400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to HILLS 5 (636401) 161.0 kV to HILL1XT9 (636406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_489 | Single Phase Fault with Stuck Breaker on HILLS 3 (636400) 345 kV Bus a. Apply Fault at the HILLS 3 (636400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to HILLS 5 (636401) 161.0 kV to HILL1XT9 (636406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on PHILL 7 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_49 | Single Phase Fault with Stuck Breaker on PHILL 7 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_490 | Single Phase Fault with Stuck Breaker on SUB 92 3 (636630) 345 kV Bus a. Apply Fault at the SUB 92 3 (636630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNSON3 (631208) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.3. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.4. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_490 | Single Phase Fault with Stuck Breaker on SUB 92 3 (636630) 345 kV Bus a. Apply Fault at the SUB 92 3 (636630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNSON3 (631208) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.3. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.4. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_491 | Single Phase Fault with Stuck Breaker on TIFFIN 3 (636420) 345 kV Bus a. Apply Fault at the TIFFIN 3 (636420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORGN VLLY 3 (631148) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.3. TIFFIN 5 (636421) 161.0 kV to TIFFIN 3 (636420) 345.0 kV Two Winding #1 b.4. TIFFIN 5 (636421) 161.0 kV to CRLRIDG5 (636422) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_491 | Single Phase Fault with Stuck Breaker on TIFFIN 3 (636420) 345 kV Bus a. Apply Fault at the TIFFIN 3 (636420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORGN VLLY 3 (631148) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.2. HILLS 3 (636400) 345.0 kV to TIFFIN 3 (636420) 345.0 kV Transmission Circuit #1 b.3. TIFFIN 5 (636421) 161.0 kV to TIFFIN 3 (636420) 345.0 kV Two Winding #1 b.4. TIFFIN 5 (636421) 161.0 kV to CRLRIDG5 (636422) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_492 | Single Phase Fault with Stuck Breaker on HILLS 3 (636400) 345 kV Bus a. Apply Fault at the HILLS 3 (636400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 5 (636401) 161.0 kV to IC ENRON 5 (636423) 161.0 kV Transmission Circuit #1 b.2. IC ENRON 5 (636423) 161.0 kV to SUB J IC 5 (636425) 161.0 kV Transmission Circuit #1 b.3. HILLS 3 (636400) 345.0 kV to HILLS 5 (636401) 161.0 kV to HILL1XT9 (636406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_492 | Single Phase Fault with Stuck Breaker on HILLS 3 (636400) 345 kV Bus a. Apply Fault at the HILLS 3 (636400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 5 (636401) 161.0 kV to IC ENRON 5 (636423) 161.0 kV Transmission Circuit #1 b.2. IC ENRON 5 (636423) 161.0 kV to SUB J IC 5 (636425) 161.0 kV Transmission Circuit #1 b.3. HILLS 3 (636400) 345.0 kV to HILLS 5 (636401) 161.0 kV to HILL1XT9 (636406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_493 | Single Phase Fault with Stuck Breaker on SUB 92 3 (636630) 345 kV Bus a. Apply Fault at the SUB 92 3 (636630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.2. WALCOTT3 (636620) 345.0 kV to IPSCO 3 (636625) 345.0 kV Transmission Circuit #1 b.3. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.4. IPSCO 3 (636625) 345.0 kV to IPSCOSV9 (636627) 34.0 kV Two Winding #1 b.5. IPSCO 3 (636625) 345.0 kV to IPSCO 9 (636628) 13.8 kV Two Winding #1 b.6. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_493 | Single Phase Fault with Stuck Breaker on SUB 92 3 (636630) 345 kV Bus a. Apply Fault at the SUB 92 3 (636630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.2. WALCOTT3 (636620) 345.0 kV to IPSCO 3 (636625) 345.0 kV Transmission Circuit #1 b.3. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.4. IPSCO 3 (636625) 345.0 kV to IPSCOSV9 (636627) 34.0 kV Two Winding #1 b.5. IPSCO 3 (636625) 345.0 kV to IPSCO 9 (636628) 13.8 kV Two Winding #1 b.6. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_494 | Single Phase Fault with Stuck Breaker on SB 56 3 (636615) 345 kV Bus a. Apply Fault at the SB 56 3 (636615) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.2. SUB 91 3 (636610) 345.0 kV to SB 56 3 (636615) 345.0 kV Transmission Circuit #1 b.3. SB 56 3 (636615) 345.0 kV to WALCOTT3 (636620) 345.0 kV Transmission Circuit #1 b.4. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.5. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 b.6. SB 56 3 (636615) 345.0 kV to SB 56 5 (636616) 161.0 kV to SB561XT9 (636619) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_494 | Single Phase Fault with Stuck Breaker on SB 56 3 (636615) 345 kV Bus a. Apply Fault at the SB 56 3 (636615) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.2. SUB 91 3 (636610) 345.0 kV to SB 56 3 (636615) 345.0 kV Transmission Circuit #1 b.3. SB 56 3 (636615) 345.0 kV to WALCOTT3 (636620) 345.0 kV Transmission Circuit #1 b.4. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.5. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 b.6. SB 56 3 (636615) 345.0 kV to SB 56 5 (636616) 161.0 kV to SB561XT9 (636619) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_495 | Single Phase Fault with Stuck Breaker on SUB 93 3 (636640) 345 kV Bus a. Apply Fault at the SUB 93 3 (636640) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. OAKGROV3 (636635) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 b.3. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.4. SUB 93 3 (636640) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_495 | Single Phase Fault with Stuck Breaker on SUB 93 3 (636640) 345 kV Bus a. Apply Fault at the SUB 93 3 (636640) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. OAKGROV3 (636635) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 b.3. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.4. SUB 93 3 (636640) 345.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_496 | Single Phase Fault with Stuck Breaker on SUB 93 3 (636640) 345 kV Bus a. Apply Fault at the SUB 93 3 (636640) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.2. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.3. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 b.4. SUB 93 3 (636640) 345.0 kV to LOUISA G (636641) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_496 | Single Phase Fault with Stuck Breaker on SUB 93 3 (636640) 345 kV Bus a. Apply Fault at the SUB 93 3 (636640) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.2. WALCOTT3 (636620) 345.0 kV to SUB 92 3 (636630) 345.0 kV Transmission Circuit #1 b.3. SUB 92 3 (636630) 345.0 kV to SUB 93 3 (636640) 345.0 kV Transmission Circuit #1 b.4. SUB 93 3 (636640) 345.0 kV to LOUISA G (636641) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_497 | Single Phase Fault with Stuck Breaker on SUB T HSK 3 (636645) 345 kV Bus a. Apply Fault at the SUB T HSK 3 (636645) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. SUB 93 3 (636640) 345.0 kV to LOUISA G (636641) 24.0 kV Two Winding #1 b.3. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_497 | Single Phase Fault with Stuck Breaker on SUB T HSK 3 (636645) 345 kV Bus a. Apply Fault at the SUB T HSK 3 (636645) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILLS 3 (636400) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 b.2. SUB 93 3 (636640) 345.0 kV to LOUISA G (636641) 24.0 kV Two Winding #1 b.3. SUB 93 3 (636640) 345.0 kV to SUB T HSK 3 (636645) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_498 | Single Phase Fault with Stuck Breaker on 5PERCHE (343004) 161 kV Bus a. Apply Fault at the 5PERCHE (343004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 b.2. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 b.3. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_498 | Single Phase Fault with Stuck Breaker on 5PERCHE (343004) 161 kV Bus a. Apply Fault at the 5PERCHE (343004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 b.2. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 b.3. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_499 | Single Phase Fault with Stuck Breaker on QUAD 6-7 (270866) 345 kV Bus a. Apply Fault at the QUAD 6-7 (270866) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUAD 6-7 (270866) 345.0 kV to SUB 91 3 (636610) 345.0 kV Transmission Circuit #1 b.2. JOHNSON3 (631208) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_499 | Single Phase Fault with Stuck Breaker on QUAD 6-7 (270866) 345 kV Bus a. Apply Fault at the QUAD 6-7 (270866) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUAD 6-7 (270866) 345.0 kV to SUB 91 3 (636610) 345.0 kV Transmission Circuit #1 b.2. JOHNSON3 (631208) 345.0 kV to HILLS 3 (636400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_5 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on OUSPRT 4 (515398) 138 kV Bus a. Apply Fault at the OUSPRT 4 (515398) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. OUSPRT 1 (515397) 34.5 kV to OUSPRTC1 (515928) 34.5 kV Transmission Circuit #1 b.3. OUSPRT 1 (515397) 34.5 kV to OUSPRT 4 (515398) 138.0 kV to OUSPRT T (515396) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_50 | Single Phase Fault with Stuck Breaker on OUSPRT 4 (515398) 138 kV Bus a. Apply Fault at the OUSPRT 4 (515398) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. OUSPRT 1 (515397) 34.5 kV to OUSPRTC1 (515928) 34.5 kV Transmission Circuit #1 b.3. OUSPRT 1 (515397) 34.5 kV to OUSPRT 4 (515398) 138.0 kV to OUSPRT T (515396) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_500 | Single Phase Fault with Stuck Breaker on OAK KNOL (546670) 69 kV Bus a. Apply Fault at the OAK KNOL (546670) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK KNOL (546670) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_500 | Single Phase Fault with Stuck Breaker on OAK KNOL (546670) 69 kV Bus a. Apply Fault at the OAK KNOL (546670) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK KNOL (546670) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_501 | Single Phase Fault with Stuck Breaker on OAK KNOL (546670) 69 kV Bus a. Apply Fault at the OAK KNOL (546670) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK KNOL (546670) 69.0 kV to MAYWOOD2 (546677) 69.0 kV Transmission Circuit #1 b.2. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_501 | Single Phase Fault with Stuck Breaker on OAK KNOL (546670) 69 kV Bus a. Apply Fault at the OAK KNOL (546670) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK KNOL (546670) 69.0 kV to MAYWOOD2 (546677) 69.0 kV Transmission Circuit #1 b.2. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_502 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_502 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_503 | Single Phase Fault with Stuck Breaker on SEDEAST5 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_503 | Single Phase Fault with Stuck Breaker on SEDEAST5 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_504 | Single Phase Fault with Stuck Breaker on SEDALIA5 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_504 | Single Phase Fault with Stuck Breaker on SEDALIA5 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_505 | Single Phase Fault with Stuck Breaker on SEDALIA5 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_505 | Single Phase Fault with Stuck Breaker on SEDALIA5 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_506 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_506 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_507 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_507 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_508 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_508 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_509 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_509 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_51 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_510 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_510 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_511 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_511 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_512 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_512 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_513 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_513 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_514 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_514 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_515 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_515 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_516 | Single Phase Fault with Stuck Breaker on HAWTHS5 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_516 | Single Phase Fault with Stuck Breaker on HAWTHS5 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_517 | Single Phase Fault with Stuck Breaker on IATAN 7 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_517 | Single Phase Fault with Stuck Breaker on IATAN 7 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_518 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_518 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_519 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_519 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV (Trip Generation) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_52 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV (Trip Generation) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_520 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_520 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_521 | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_521 | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_522 | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.4. SALSBRY5 (543062) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_522 | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.4. SALSBRY5 (543062) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_523 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_523 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_524 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_524 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_525 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_525 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_526 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_526 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_527 | Single Phase Fault with Stuck Breaker on JOP145 5 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_527 | Single Phase Fault with Stuck Breaker on JOP145 5 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_528 | Single Phase Fault with Stuck Breaker on JOP389 5 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_528 | Single Phase Fault with Stuck Breaker on JOP389 5 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_529 | Single Phase Fault with Stuck Breaker on RIV167 5 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_529 | Single Phase Fault with Stuck Breaker on RIV167 5 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_53 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_530 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_530 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_531 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_531 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_532 | Single Phase Fault with Stuck Breaker on RIV452T 5 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_532 | Single Phase Fault with Stuck Breaker on RIV452T 5 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_533 | Single Phase Fault with Stuck Breaker on RIV452T 5 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_533 | Single Phase Fault with Stuck Breaker on RIV452T 5 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_534 | Single Phase Fault with Stuck Breaker on CAR395 5 (547485) 161 kV Bus a. Apply Fault at the CAR395 5 (547485) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.4. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_534 | Single Phase Fault with Stuck Breaker on CAR395 5 (547485) 161 kV Bus a. Apply Fault at the CAR395 5 (547485) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.4. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_535 | Single Phase Fault with Stuck Breaker on FIR417 5 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_535 | Single Phase Fault with Stuck Breaker on FIR417 5 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_536 | Single Phase Fault with Stuck Breaker on STL439 5 (547498) 161 kV Bus a. Apply Fault at the STL439 5 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_536 | Single Phase Fault with Stuck Breaker on STL439 5 (547498) 161 kV Bus a. Apply Fault at the STL439 5 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_537 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_537 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_538 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_538 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_539 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_539 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_54 | Single Phase Fault with Stuck Breaker on WAGENER 3 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_540 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_540 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_541 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_541 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_542 | Single Phase Fault with Stuck Breaker on HOC404 5 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_542 | Single Phase Fault with Stuck Breaker on HOC404 5 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_543 | Single Phase Fault with Stuck Breaker on HOC404 5 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_543 | Single Phase Fault with Stuck Breaker on HOC404 5 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_544 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_544 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_545 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_545 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_546 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_546 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_547 | Single Phase Fault with Stuck Breaker on HAWTHS5 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_547 | Single Phase Fault with Stuck Breaker on HAWTHS5 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_548 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_548 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_549 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_549 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_55 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_550 | Single Phase Fault with Stuck Breaker on LEVEE 5 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_550 | Single Phase Fault with Stuck Breaker on LEVEE 5 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_551 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.5. NEASTN5 (543666) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_551 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.5. NEASTN5 (543666) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_552 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NRTHST_B34_1 (543081) 13.8 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_552 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NRTHST_B34_1 (543081) 13.8 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_553 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B90_1 (543082) 13.8 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_553 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B90_1 (543082) 13.8 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_554 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_554 | Single Phase Fault with Stuck Breaker on NEASTN5 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_555 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. NORTON1 (543123) 34.5 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_555 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. NORTON1 (543123) 34.5 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_556 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_556 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_557 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_557 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_558 | Single Phase Fault with Stuck Breaker on ARCHIE 5 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 b.4. ARCHIE 5 (541207) 161.0 kV to G17-111-TAP (762010) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_558 | Single Phase Fault with Stuck Breaker on ARCHIE 5 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 b.4. ARCHIE 5 (541207) 161.0 kV to G17-111-TAP (762010) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_559 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_559 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.4. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.5. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.6. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_56 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.4. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.5. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.6. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_560 | Single Phase Fault with Stuck Breaker on LEESUM 5 (541233) 161 kV Bus a. Apply Fault at the LEESUM 5 (541233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.3. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.4. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_560 | Single Phase Fault with Stuck Breaker on LEESUM 5 (541233) 161 kV Bus a. Apply Fault at the LEESUM 5 (541233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.3. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.4. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_561 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_561 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_562 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_562 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_563 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_563 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_564 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_564 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_565 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_565 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_566 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_566 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_567 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_567 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_568 | Single Phase Fault with Stuck Breaker on HONEYWL5 (541382) 161 kV Bus a. Apply Fault at the HONEYWL5 (541382) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 b.2. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_568 | Single Phase Fault with Stuck Breaker on HONEYWL5 (541382) 161 kV Bus a. Apply Fault at the HONEYWL5 (541382) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 b.2. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_569 | Single Phase Fault with Stuck Breaker on KCSOUTH5 (541245) 161 kV Bus a. Apply Fault at the KCSOUTH5 (541245) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 b.2. G18-054-TAP (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_569 | Single Phase Fault with Stuck Breaker on KCSOUTH5 (541245) 161 kV Bus a. Apply Fault at the KCSOUTH5 (541245) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 b.2. G18-054-TAP (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on QUIND 5 (546652) 161 kV Bus a. Apply Fault at the QUIND 5 (546652) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 b.2. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 b.3. QUIND 5 (546652) 161.0 kV to QGEN2 1 (546698) 15.0 kV Two Winding #1 b.4. QUIND 5 (546652) 161.0 kV to QCT3 1 (546701) 13.8 kV Two Winding #1 b.5. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_57 | Single Phase Fault with Stuck Breaker on QUIND 5 (546652) 161 kV Bus a. Apply Fault at the QUIND 5 (546652) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 b.2. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 b.3. QUIND 5 (546652) 161.0 kV to QGEN2 1 (546698) 15.0 kV Two Winding #1 b.4. QUIND 5 (546652) 161.0 kV to QCT3 1 (546701) 13.8 kV Two Winding #1 b.5. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_570 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_570 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_571 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_571 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_572 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 b.2. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.3. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.4. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.5. MARMTNW5 (532935) 161.0 kV to MARMATN2 (533639) 69.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_572 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 b.2. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.3. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.4. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.5. MARMTNW5 (532935) 161.0 kV to MARMATN2 (533639) 69.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_573 | Single Phase Fault with Stuck Breaker on TECHILL6 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.5. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.6. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.9. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_573 | Single Phase Fault with Stuck Breaker on TECHILL6 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.5. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.6. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.9. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_574 | Single Phase Fault with Stuck Breaker on AMELIA 3 (533215) 115 kV Bus a. Apply Fault at the AMELIA 3 (533215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 b.2. AMELIA 3 (533215) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_574 | Single Phase Fault with Stuck Breaker on AMELIA 3 (533215) 115 kV Bus a. Apply Fault at the AMELIA 3 (533215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 b.2. AMELIA 3 (533215) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_575 | Single Phase Fault with Stuck Breaker on CORONAD3 (533394) 115 kV Bus a. Apply Fault at the CORONAD3 (533394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_575 | Single Phase Fault with Stuck Breaker on CORONAD3 (533394) 115 kV Bus a. Apply Fault at the CORONAD3 (533394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_576 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_576 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_577 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_577 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_578 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_578 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_579 | Single Phase Fault with Stuck Breaker on BELAIRE4 (532988) 138 kV Bus a. Apply Fault at the BELAIRE4 (532988) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 b.2. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_579 | Single Phase Fault with Stuck Breaker on BELAIRE4 (532988) 138 kV Bus a. Apply Fault at the BELAIRE4 (532988) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 b.2. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on NEARMAN5 (546653) 161 kV Bus a. Apply Fault at the NEARMAN5 (546653) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 b.2. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 b.3. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.4. NEARMAN5 (546653) 161.0 kV to NMISOBUS (546703) 20.0 kV Two Winding #1 b.5. NEARMAN5 (546653) 161.0 kV to NM4BUS (546751) 161.0 kV Transmission Circuit #1 b.6. NEARMAN5 (546653) 161.0 kV to GEN-2018-062 (762976) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_58 | Single Phase Fault with Stuck Breaker on NEARMAN5 (546653) 161 kV Bus a. Apply Fault at the NEARMAN5 (546653) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 b.2. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 b.3. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.4. NEARMAN5 (546653) 161.0 kV to NMISOBUS (546703) 20.0 kV Two Winding #1 b.5. NEARMAN5 (546653) 161.0 kV to NM4BUS (546751) 161.0 kV Transmission Circuit #1 b.6. NEARMAN5 (546653) 161.0 kV to GEN-2018-062 (762976) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_580 | Single Phase Fault with Stuck Breaker on LYONS 3 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_580 | Single Phase Fault with Stuck Breaker on LYONS 3 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_581 | Single Phase Fault with Stuck Breaker on WMCPHER3 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_581 | Single Phase Fault with Stuck Breaker on WMCPHER3 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_582 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_582 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_583 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_583 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_584 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 b.2. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_584 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 b.2. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_585 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 b.2. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_585 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 b.2. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_586 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 b.3. ARNOLD 3 (533211) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_586 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 b.3. ARNOLD 3 (533211) 115.0 kV (Trip Shunt Device) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_587 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.2. ARNOLD 1 (533449) 7.2 kV to ARNOLD 3 (533211) 115.0 kV to ARNOLD 2 (533471) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_587 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 b.2. ARNOLD 1 (533449) 7.2 kV to ARNOLD 3 (533211) 115.0 kV to ARNOLD 2 (533471) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_588 | Single Phase Fault with Stuck Breaker on WJCCTYW3 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_588 | Single Phase Fault with Stuck Breaker on WJCCTYW3 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_589 | Single Phase Fault with Stuck Breaker on 17TH 4 (533064) 138 kV Bus a. Apply Fault at the 17TH 4 (533064) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MASCOT 2 (533814) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.2. MEAD S 2 (533815) 69.0 kV to MEAD N 2 (533818) 69.0 kV Transmission Circuit #z1 b.3. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.4. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.5. MEAD N 2 (533818) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.6. MOSSMAN2 (533820) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.7. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.8. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.9. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.10. 17TH 2 (533840) 69.0 kV to 17TH 4 (533064) 138.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_589 | Single Phase Fault with Stuck Breaker on 17TH 4 (533064) 138 kV Bus a. Apply Fault at the 17TH 4 (533064) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MASCOT 2 (533814) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.2. MEAD S 2 (533815) 69.0 kV to MEAD N 2 (533818) 69.0 kV Transmission Circuit #z1 b.3. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.4. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.5. MEAD N 2 (533818) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.6. MOSSMAN2 (533820) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.7. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.8. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.9. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.10. 17TH 2 (533840) 69.0 kV to 17TH 4 (533064) 138.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on SUNSET 5 (546654) 161 kV Bus a. Apply Fault at the SUNSET 5 (546654) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 b.2. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_59 | Single Phase Fault with Stuck Breaker on SUNSET 5 (546654) 161 kV Bus a. Apply Fault at the SUNSET 5 (546654) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 b.2. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_590 | Single Phase Fault with Stuck Breaker on ALLEN 2 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.5. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_590 | Single Phase Fault with Stuck Breaker on ALLEN 2 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.5. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_591 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.2. WALNUT 3 (533220) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.3. ARNOLD 2 (533471) 69.0 kV to NORTONV2 (533481) 69.0 kV Transmission Circuit #1 b.4. ARNOLD 2 (533471) 69.0 kV to ARNOLD 3 (533211) 115.0 kV to ARNOLD 1 (533449) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_591 | Single Phase Fault with Stuck Breaker on ARNOLD 3 (533211) 115 kV Bus a. Apply Fault at the ARNOLD 3 (533211) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.2. WALNUT 3 (533220) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.3. ARNOLD 2 (533471) 69.0 kV to NORTONV2 (533481) 69.0 kV Transmission Circuit #1 b.4. ARNOLD 2 (533471) 69.0 kV to ARNOLD 3 (533211) 115.0 kV to ARNOLD 1 (533449) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_592 | Single Phase Fault with Stuck Breaker on ATHENS 2 (533623) 69 kV Bus a. Apply Fault at the ATHENS 2 (533623) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. ATHENS 2 (533623) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.3. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.4. BURLING2 (533624) 69.0 kV to BURLJCT2 (533626) 69.0 kV Transmission Circuit #1 b.5. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.6. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_592 | Single Phase Fault with Stuck Breaker on ATHENS 2 (533623) 69 kV Bus a. Apply Fault at the ATHENS 2 (533623) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. ATHENS 2 (533623) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.3. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.4. BURLING2 (533624) 69.0 kV to BURLJCT2 (533626) 69.0 kV Transmission Circuit #1 b.5. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.6. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_593 | Single Phase Fault with Stuck Breaker on BUTLERS4 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLERN2 (533583) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 b.3. BUTLERN2 (533583) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #z1 b.4. BUTLERN2 (533583) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #1 b.5. FRNTR N2 (533593) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #1 b.6. BUTLERS2 (533609) 69.0 kV to BUTLERS4 (532989) 138.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_593 | Single Phase Fault with Stuck Breaker on BUTLERS4 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLERN2 (533583) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 b.3. BUTLERN2 (533583) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #z1 b.4. BUTLERN2 (533583) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #1 b.5. FRNTR N2 (533593) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #1 b.6. BUTLERS2 (533609) 69.0 kV to BUTLERS4 (532989) 138.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_594 | Single Phase Fault with Stuck Breaker on CANAL 4 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.3. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 b.4. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 b.5. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.6. CANAL 4 (533033) 138.0 kV to CANALS 2 (533784) 69.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_594 | Single Phase Fault with Stuck Breaker on CANAL 4 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.3. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 b.4. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 b.5. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.6. CANAL 4 (533033) 138.0 kV to CANALS 2 (533784) 69.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_595 | Single Phase Fault with Stuck Breaker on CANAL 4 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 b.2. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 b.3. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. GLENDAL2 (533797) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 b.5. CANALS 2 (533784) 69.0 kV to CANAL 4 (533033) 138.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_595 | Single Phase Fault with Stuck Breaker on CANAL 4 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 b.2. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 b.3. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. GLENDAL2 (533797) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 b.5. CANALS 2 (533784) 69.0 kV to CANAL 4 (533033) 138.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_596 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHENEY 2 (533785) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.4. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.5. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 b.6. GALE TP2 (533845) 69.0 kV to SG4ANDL2 (533872) 69.0 kV Transmission Circuit #1 b.7. GALE TP2 (533845) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.8. COWSKIN2 (533788) 69.0 kV to COWSKIN4 (533038) 138.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_596 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHENEY 2 (533785) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.4. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.5. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 b.6. GALE TP2 (533845) 69.0 kV to SG4ANDL2 (533872) 69.0 kV Transmission Circuit #1 b.7. GALE TP2 (533845) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.8. COWSKIN2 (533788) 69.0 kV to COWSKIN4 (533038) 138.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_597 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.4. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.5. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.6. COWSKIN2 (533788) 69.0 kV to COWSKIN4 (533038) 138.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_597 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.4. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.5. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.6. COWSKIN2 (533788) 69.0 kV to COWSKIN4 (533038) 138.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_598 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.4. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.5. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.6. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_598 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.4. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.5. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.6. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_599 | Single Phase Fault with Stuck Breaker on DEPAUL 2 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_599 | Single Phase Fault with Stuck Breaker on DEPAUL 2 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_6 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on KAW W 5 (546655) 161 kV Bus a. Apply Fault at the KAW W 5 (546655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.2. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_60 | Single Phase Fault with Stuck Breaker on KAW W 5 (546655) 161 kV Bus a. Apply Fault at the KAW W 5 (546655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.2. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_600 | Single Phase Fault with Stuck Breaker on DEARING4 (533002) 138 kV Bus a. Apply Fault at the DEARING4 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.5. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_600 | Single Phase Fault with Stuck Breaker on DEARING4 (533002) 138 kV Bus a. Apply Fault at the DEARING4 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.5. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_601 | Single Phase Fault with Stuck Breaker on FTSCOTT2 (533635) 69 kV Bus a. Apply Fault at the FTSCOTT2 (533635) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.4. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.5. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_601 | Single Phase Fault with Stuck Breaker on FTSCOTT2 (533635) 69 kV Bus a. Apply Fault at the FTSCOTT2 (533635) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.4. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.5. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_602 | Single Phase Fault with Stuck Breaker on CRAWFOR2 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_602 | Single Phase Fault with Stuck Breaker on CRAWFOR2 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_603 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.5. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.6. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_603 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.5. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.6. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_604 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.4. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.5. HOOVERN2 (533805) 69.0 kV to HOOVERN4 (533049) 138.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_604 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.4. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.5. HOOVERN2 (533805) 69.0 kV to HOOVERN4 (533049) 138.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_605 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.5. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.6. HOOVERN2 (533805) 69.0 kV to HOOVERN4 (533049) 138.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_605 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.5. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.6. HOOVERN2 (533805) 69.0 kV to HOOVERN4 (533049) 138.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_606 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.6. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.7. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_606 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.6. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.7. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_607 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.3. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.6. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.7. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_607 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.3. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.6. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.7. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_608 | Single Phase Fault with Stuck Breaker on LIBERTY4 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. SUNFLRS2 (533670) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.5. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_608 | Single Phase Fault with Stuck Breaker on LIBERTY4 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. SUNFLRS2 (533670) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.5. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_609 | Single Phase Fault with Stuck Breaker on LITCH 5 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH1 1 (532952) 13.2 kV to LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_609 | Single Phase Fault with Stuck Breaker on LITCH 5 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH1 1 (532952) 13.2 kV to LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on MAYWOOD5 (546656) 161 kV Bus a. Apply Fault at the MAYWOOD5 (546656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.4. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_61 | Single Phase Fault with Stuck Breaker on MAYWOOD5 (546656) 161 kV Bus a. Apply Fault at the MAYWOOD5 (546656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.4. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_610 | Single Phase Fault with Stuck Breaker on MACARTH2 (533813) 69 kV Bus a. Apply Fault at the MACARTH2 (533813) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.3. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.5. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.6. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_610 | Single Phase Fault with Stuck Breaker on MACARTH2 (533813) 69 kV Bus a. Apply Fault at the MACARTH2 (533813) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.3. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.5. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.6. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_611 | Single Phase Fault with Stuck Breaker on MACARTH2 (533813) 69 kV Bus a. Apply Fault at the MACARTH2 (533813) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.4. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.6. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.7. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_611 | Single Phase Fault with Stuck Breaker on MACARTH2 (533813) 69 kV Bus a. Apply Fault at the MACARTH2 (533813) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.4. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.6. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.7. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_612 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_612 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_613 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.4. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.5. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.6. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_613 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.4. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.5. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.6. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_614 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.3. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.4. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.5. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.6. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.7. GILL E 2 (533795) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_614 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.3. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.4. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.5. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.6. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.7. GILL E 2 (533795) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_615 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_615 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_616 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_616 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_617 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.3. NEC U3 (532711) 12.0 kV to NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV Three Winding #1 b.4. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_617 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.3. NEC U3 (532711) 12.0 kV to NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV Three Winding #1 b.4. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_618 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.3. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_618 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.3. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_619 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. GIRARD 2 (533761) 69.0 kV to GIR JCT2 (533762) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.6. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.7. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.8. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_619 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. GIRARD 2 (533761) 69.0 kV to GIR JCT2 (533762) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.6. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.7. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.8. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on GIBBS 5 (546658) 161 kV Bus a. Apply Fault at the GIBBS 5 (546658) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.2. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_62 | Single Phase Fault with Stuck Breaker on GIBBS 5 (546658) 161 kV Bus a. Apply Fault at the GIBBS 5 (546658) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.2. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_620 | Single Phase Fault with Stuck Breaker on NOEASTE4 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 b.5. NOEASTW2 (533822) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #z1 b.6. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_620 | Single Phase Fault with Stuck Breaker on NOEASTE4 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 b.5. NOEASTW2 (533822) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #z1 b.6. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_621 | Single Phase Fault with Stuck Breaker on NOEASTW4 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. CRESTVW2 (533789) 69.0 kV to NOEASTW2 (533822) 69.0 kV Transmission Circuit #1 b.4. INNOVAT2 (533811) 69.0 kV to NOEASTW2 (533822) 69.0 kV Transmission Circuit #1 b.5. NOEASTW2 (533822) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #z1 b.6. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_621 | Single Phase Fault with Stuck Breaker on NOEASTW4 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. CRESTVW2 (533789) 69.0 kV to NOEASTW2 (533822) 69.0 kV Transmission Circuit #1 b.4. INNOVAT2 (533811) 69.0 kV to NOEASTW2 (533822) 69.0 kV Transmission Circuit #1 b.5. NOEASTW2 (533822) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #z1 b.6. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_622 | Single Phase Fault with Stuck Breaker on PARSONS2 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_622 | Single Phase Fault with Stuck Breaker on PARSONS2 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_623 | Single Phase Fault with Stuck Breaker on ALTAMNS2 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_623 | Single Phase Fault with Stuck Breaker on ALTAMNS2 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_624 | Single Phase Fault with Stuck Breaker on PLAZA E2 (533829) 69 kV Bus a. Apply Fault at the PLAZA E2 (533829) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.4. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.5. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.6. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_624 | Single Phase Fault with Stuck Breaker on PLAZA E2 (533829) 69 kV Bus a. Apply Fault at the PLAZA E2 (533829) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.4. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.5. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.6. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_625 | Single Phase Fault with Stuck Breaker on 17TH TP2 (533835) 69 kV Bus a. Apply Fault at the 17TH TP2 (533835) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.6. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.7. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_625 | Single Phase Fault with Stuck Breaker on 17TH TP2 (533835) 69 kV Bus a. Apply Fault at the 17TH TP2 (533835) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.6. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.7. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_626 | Single Phase Fault with Stuck Breaker on RIPLEYW2 (533832) 69 kV Bus a. Apply Fault at the RIPLEYW2 (533832) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAHANNA2 (533738) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.2. NEWTON 2 (533745) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.3. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.5. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_626 | Single Phase Fault with Stuck Breaker on RIPLEYW2 (533832) 69 kV Bus a. Apply Fault at the RIPLEYW2 (533832) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAHANNA2 (533738) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.2. NEWTON 2 (533745) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.3. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.5. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_627 | Single Phase Fault with Stuck Breaker on RIPLEYW2 (533832) 69 kV Bus a. Apply Fault at the RIPLEYW2 (533832) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.3. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 b.5. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_627 | Single Phase Fault with Stuck Breaker on RIPLEYW2 (533832) 69 kV Bus a. Apply Fault at the RIPLEYW2 (533832) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.3. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 b.5. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_628 | Single Phase Fault with Stuck Breaker on SHERIDN2 (533841) 69 kV Bus a. Apply Fault at the SHERIDN2 (533841) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.4. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.6. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_628 | Single Phase Fault with Stuck Breaker on SHERIDN2 (533841) 69 kV Bus a. Apply Fault at the SHERIDN2 (533841) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.4. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.6. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_629 | Single Phase Fault with Stuck Breaker on SUNSET-2 (533844) 69 kV Bus a. Apply Fault at the SUNSET-2 (533844) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 b.3. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_629 | Single Phase Fault with Stuck Breaker on SUNSET-2 (533844) 69 kV Bus a. Apply Fault at the SUNSET-2 (533844) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 b.3. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on CTR CTY5 (546659) 161 kV Bus a. Apply Fault at the CTR CTY5 (546659) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 b.2. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_63 | Single Phase Fault with Stuck Breaker on CTR CTY5 (546659) 161 kV Bus a. Apply Fault at the CTR CTY5 (546659) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 b.2. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_630 | Single Phase Fault with Stuck Breaker on WALNUT 3 (533220) 115 kV Bus a. Apply Fault at the WALNUT 3 (533220) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.2. WALNUT 3 (533220) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.3. WALNUT 2 (533484) 69.0 kV to WATHENA2 (533485) 69.0 kV Transmission Circuit #1 b.4. WALNUT 2 (533484) 69.0 kV to WALNUT 3 (533220) 115.0 kV to WALNUT 1 (533451) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_630 | Single Phase Fault with Stuck Breaker on WALNUT 3 (533220) 115 kV Bus a. Apply Fault at the WALNUT 3 (533220) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.2. WALNUT 3 (533220) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 b.3. WALNUT 2 (533484) 69.0 kV to WATHENA2 (533485) 69.0 kV Transmission Circuit #1 b.4. WALNUT 2 (533484) 69.0 kV to WALNUT 3 (533220) 115.0 kV to WALNUT 1 (533451) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_631 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. BU10BEN2 (533585) 69.0 kV to WEAVER 2 (533604) 69.0 kV Transmission Circuit #1 b.7. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.8. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_631 | Single Phase Fault with Stuck Breaker on WEAVER 4 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. BU10BEN2 (533585) 69.0 kV to WEAVER 2 (533604) 69.0 kV Transmission Circuit #1 b.7. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.8. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_632 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC2SHAR2 (533629) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.5. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.6. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.7. WOLFCRK2 (533653) 69.0 kV to WOLFCRK7 (532797) 345.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_632 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC2SHAR2 (533629) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.5. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.6. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.7. WOLFCRK2 (533653) 69.0 kV to WOLFCRK7 (532797) 345.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_633 | Single Phase Fault with Stuck Breaker on CANAL 4 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 b.2. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 b.3. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.5. CANALS 2 (533784) 69.0 kV to CANAL 4 (533033) 138.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_633 | Single Phase Fault with Stuck Breaker on CANAL 4 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 b.2. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 b.3. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.5. CANALS 2 (533784) 69.0 kV to CANAL 4 (533033) 138.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_634 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.4. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.6. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.7. HOOVERN2 (533805) 69.0 kV to HOOVERN4 (533049) 138.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 b.8. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_634 | Single Phase Fault with Stuck Breaker on HOOVERS4 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.4. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.5. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.6. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.7. HOOVERN2 (533805) 69.0 kV to HOOVERN4 (533049) 138.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 b.8. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_635 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_635 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_636 | Single Phase Fault with Stuck Breaker on PLAZA W2 (533858) 69 kV Bus a. Apply Fault at the PLAZA W2 (533858) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 b.2. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.3. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_636 | Single Phase Fault with Stuck Breaker on PLAZA W2 (533858) 69 kV Bus a. Apply Fault at the PLAZA W2 (533858) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 b.2. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.3. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_637 | Single Phase Fault with Stuck Breaker on PLAZA E2 (533829) 69 kV Bus a. Apply Fault at the PLAZA E2 (533829) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.4. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 b.5. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_637 | Single Phase Fault with Stuck Breaker on PLAZA E2 (533829) 69 kV Bus a. Apply Fault at the PLAZA E2 (533829) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.4. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 b.5. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_638 | Single Phase Fault with Stuck Breaker on RIPLEYW2 (533832) 69 kV Bus a. Apply Fault at the RIPLEYW2 (533832) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 b.2. MASCOT 2 (533814) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #1 b.3. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 b.5. RIPLEYE2 (533859) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_638 | Single Phase Fault with Stuck Breaker on RIPLEYW2 (533832) 69 kV Bus a. Apply Fault at the RIPLEYW2 (533832) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 b.2. MASCOT 2 (533814) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #1 b.3. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 b.5. RIPLEYE2 (533859) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_639 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 b.2. MOORLND2 (520995) 69.0 kV to MOORLND4 (520999) 138.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_639 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 b.2. MOORLND2 (520995) 69.0 kV to MOORLND4 (520999) 138.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on ARMDALE5 (546661) 161 kV Bus a. Apply Fault at the ARMDALE5 (546661) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 b.2. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_64 | Single Phase Fault with Stuck Breaker on ARMDALE5 (546661) 161 kV Bus a. Apply Fault at the ARMDALE5 (546661) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 b.2. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_640 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_640 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_641 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_641 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_642 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_642 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_643 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.5. MOORLND4 (520999) 138.0 kV to MORLND2 (520997) 18.0 kV Two Winding #1 b.6. MOORLND4 (520999) 138.0 kV to MORLND3 (520998) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_643 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.5. MOORLND4 (520999) 138.0 kV to MORLND2 (520997) 18.0 kV Two Winding #1 b.6. MOORLND4 (520999) 138.0 kV to MORLND3 (520998) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_644 | Single Phase Fault with Stuck Breaker on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MOORLND4 (520999) 138.0 kV to MORLND2 (520997) 18.0 kV Two Winding #1 b.6. MOORLND4 (520999) 138.0 kV to MORLND3 (520998) 18.0 kV Two Winding #1 b.7. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_P4_FAULT_644 | Single Phase Fault with Stuck Breaker on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MOORLND4 (520999) 138.0 kV to MORLND2 (520997) 18.0 kV Two Winding #1 b.6. MOORLND4 (520999) 138.0 kV to MORLND3 (520998) 18.0 kV Two Winding #1 b.7. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_P4_FAULT_645 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 b.4. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes