## Executive Summary
Executive Summary: DISIS-2018-002/DISIS-2019-001-1 Restudy of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on 3/31/2018. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 3.0 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2018-002/DISIS-2019-001 Phase 2 includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest )
DISIS Manual Version 3.0
https://spp.org/documents/71111/DISIS%20Study%20Manual%2020240424.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
6419.43 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade: $424,854,829.00 Steady State Network Upgrade: $78,765,700.00 Stability Network Upgrade: $0.00 Steady State/Stability Network Upgrade: $14,662,500.00 Interconnection Costs: $331,426,629.00
Models Used in Steady State Study
2021 ITP Series
Winter: 2026
Summer: 2023, 2026
Light: 2026
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
Published: 5/23/2025
Costs for Solar/Battery Requests were allocated using the 26SP (summer peak) model.
Costs for Wind Requests were allocated using the 26L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Proxy or Potential P4 contingencies were tested for steady state analysis, and verified with the TOs for validity if the contingencies report the most limiting constraint.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
2024-12-02 | SPP | Phase 2 Restudy 1 Draft Report
2024-12-10 | SPP | Phase 2 Final Report
2025-05-21 | SPP | Phase 2 Final Report Repost
2025-05-23 | SPP | Phase 2 Final Report Repost

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
2024-12-09 | Upgrade Name/Details | 9 | Contingent Upgrades - Screening | Updated the estimated in-service date for "Denison to Boyer 69kV Terminal Upgrade".
2024-12-09 | Results Formatting | 12 | Stability Analysis Results | Added "No" under the "Rotor Angle Stability" column for faults that had previously been identified as requiring "Build Strandahl to Black Tail 115 kV line" upgrade.
2024-12-09 | Upgrade Cost Update | 6, 8 | Upgrade Summary/Assigned Upgrade Costs | Updated Interconnection costs for UIDs 156777, 156778, 156788
2024-12-09 | Upgrade Name/Details | 6, 8 | Upgrade Summary/Assigned Upgrade Costs | Updated the Minimum Rating for the "Rebuild SWEETWT6 to WHEELER6 230 kV Line 1"
2024-12-09 | Results Update | 10 | All Thermal | Removed Invalid P4 Contingencies for G04 ERIS
2024-12-09 | Results Update | 10 | All Thermal | Removed Invalid P4 Contingencies & Updated G04 CF ERIS Results
2024-12-09 | Results Update | 7 | Constraints Summary | Updated TC Loading for Sweetwater - Wheeler 230 kV constraint
2024-12-10 | Upgrade Cost Update | 1 | Executive Summary | Updated Upgrade Cost Summaries
2024-12-10 | Upgrade Cost Update | 8 | Assigned Upgrade Cost | Allocation percentage corrected for UID 166779
2024-12-21 | Upgrade Name/Details | 6, 8 | Upgrade Summary/Assigned Upgrade Costs | Updated the upgrade details for UID 170500, 170501, and 170502
2024-12-21 | Upgrade Name/Details | 6 | Upgrade Summary | Updated the owner name for UID 170493 and 170494
2024-12-21 | Upgrade Name/Details | 6 | Upgrade Summary | Updated the owner name for UID 170506
2025-01-08 | Upgrade Cost Update | 8 | Assigned Upgrade Cost | Corrected the assignment of TOIF and NSNU costs for GEN-2018-064
2025-01-08 | Upgrade Name/Details | 6, 8 | Upgrade Summary/Assigned Upgrade Costs | Corrected the UID for CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade
2025-01-08 | Upgrade Name/Details | 6, 8 | Upgrade Summary/Assigned Upgrade Costs | Combined the interconnection upgrade name and details for GEN-2018-065/068/131/132 with UID 156668
2025-01-08 | Upgrade Name/Details | 6 | Upgrade Summary | Updated the UIDs for "Antelope 345kV GEN-2018-065 Interconnection (TOIF) (NPPD)" and "Antelope 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001)"
2025-01-08 | Upgrade Name/Details | 8 | Assigned Upgrade Cost | Updated UID for "Great Bend - Spearville 230kV GEN-2019-055 Interconnection (TOIF) (SUNC)"
2025-01-08 | Upgrade Name/Details | 6 | Upgrade Summary | Updated the UID for "Great Bend - Spearville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001)"
2025-01-08 | Upgrade Name/Details | 6 | Upgrade Summary | Updated Lead Times for Interconnection Upgrades
2025-05-21 | Project Status | 4 | Requests | Updated the status of GEN-2018-063, GEN-2018-065, GEN-2018-068, GEN-2018-088, GEN-2018-116, GEN-2019-013, GEN-2019-035, GEN-2019-048, and GEN-2019-051 to "Withdrawn"
2025-05-21 | Seasonal LOIS | 5 | Seasonal LOIS | Changed the Seasonal LOIS values to "N/A" for the withdrawn requests
2025-05-21 | Network Upgrades | 6,7,8,10 | Upgrade Summary/Constraints Summary/Assigned Upgrade Costs/All Thermal | Removed network upgrades that are no longer required due to the withdrawn requests
2025-05-21 | Network Upgrades | 6,7,8,10 | Upgrade Summary/Constraints Summary/Assigned Upgrade Costs/All Thermal | Updated the network upgrades to address the DENISON8 to J6BOYER_-NI8 69kV overload issue according to the facility studies
2025-05-21 | Network Upgrades | 6,7,8,10 | Upgrade Summary/Constraints Summary/Assigned Upgrade Costs/All Thermal | Updated results from the 00NR base and contingent facilities analysis
2025-05-21 | Seasonal LOIS | 4,5 | Requests/Seasonal LOIS | Updated Seasonal LOIS for multiple requests based on updated analysis
2025-05-23 | Results | 7,10 | Constraints Summary/All Thermal | Updated the Group 02 results and changed the need for "Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) from a Non-Conv mitigation to a Thermal mitigation
2025-05-23 | Seasonal LOIS | 4,5 | Requests/Seasonal LOIS | Updated Seasonal LOIS values for the affected units in Group 02 after the results update

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.7306 | ER | MWEC | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 121.9889 | 121.9889 | -1.0905 | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | 33.8431 | 33.8431 | 0 | 18.9081 | 33.8431 | 33.8431 | 0 | 0 | -4.2 | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2018-065 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | ER/NR | NPPD | Antelope - Hoskins 345 kV Substation | WITHDRAWN
GEN-2018-068 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | ER/NR | NPPD | Antelope - Hoskins 345 kV Substation | WITHDRAWN
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 250 | 250 | 250 | 186.0611 | 179.0634 | 250 | 250 | 172.7981 | 172.7981 | -13.57 | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | 231 | 231 | 231 | 231 | 231 | 231 | 231 | 231 | -2.0484 | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | 219.1738 | 219.6103 | 219.1738 | 219.6103 | 219.1738 | 219.6103 | 220.6361 | 220.6361 | -1.9 | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | 199.5728 | 199.9703 | 199.5728 | 199.9703 | 199.5728 | 199.9703 | 200.9044 | 200.9044 | -3.2 | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-063 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -0.062933 | ER | EDE | Sedalia Marshfield Springfield Nichols Street 69kV circuit | WITHDRAWN
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | -2.5 | ER | ITCGP | Thistle 345kV substation | DISIS STAGE
GEN-2018-116 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -4 | ER/NR | SUNC | Frey Street 115kV bus | WITHDRAWN
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | 200.22 | 200.22 | 200.22 | 200.22 | 200.22 | 200.22 | 200.22 | 200.22 | -7.5608 | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | -0.61 | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | -20.31 | ER/NR | OGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 1.51 | ER/NR | OGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | -8.52 | ER | AEP | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | -15.6 | ER | AEP | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-088 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -7.54 | ER | AEP | Lydia 345kV substation | WITHDRAWN
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | -5.03 | ER | AEP | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | -4.89 | ER/NR | AEP | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | -8.79 | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | -6.28 | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal | 15.15 | 15.15 | 15.15 | 15.15 | 15.15 | 15.15 | 15.15 | 15.15 | 15.15 | -0.075975 | ER/NR | NIPCO | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid | 110 | 107.3502 | 107.3502 | 110 | 110 | 107.3502 | 107.3502 | 107.3502 | 107.3502 | -4.6095 | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -4.4962 | ER/NR | BEPC | Leland Olds 345kV substation | DISIS STAGE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -1.1315 | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | 138.814 | 138.548 | 138.814 | 138.548 | 138.814 | 138.548 | 139.57 | 139.57 | -0.9 | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | -0.38636 | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | 69.1192 | 69.1192 | 74.4244 | 71.6254 | 69.1192 | 69.1192 | 69.1192 | 69.1192 | -4.8 | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 50 | 34.5596 | 34.5596 | 37.2122 | 35.8127 | 34.5596 | 34.5596 | 34.5596 | 34.5596 | -1.9 | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | 69.1192 | 69.1192 | 74.4244 | 71.6254 | 69.1192 | 69.1192 | 69.1192 | 69.1192 | -4.8 | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -5.7163 | ER | EDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 0 | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | -12.6006 | ER/NR | ITCGP | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-035 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -0.73621 | ER/NR | EDE | Reeds Spring-Aurora 161kV Line | WITHDRAWN
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | 66.406 | 89.6437 | 66.406 | 89.6437 | 66.406 | 89.6437 | 100 | 100 | -5.1557 | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-048 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -1.9512 | ER | KCPL | Duncan 69kV substation | WITHDRAWN
GEN-2019-051 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.3 | ER/NR | SUNC | Frey St 115kV bus | WITHDRAWN
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0.4 | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -3.7 | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -2.9 | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -1.9 | ER/NR | ITCGP | Clark County 345kV substation | DISIS STAGE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0.4 | ER/NR | ITCGP | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0.4 | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -0.13 | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -0.19 | ER/NR | OGE | Woodward 345kV substation | DISIS STAGE
GEN-2019-013 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -4.29 | ER/NR | AEP | Dempsey 230kV sub/Sweetwater 230kV | WITHDRAWN
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | -9.93 | ER | OGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | -1.07 | ER | AEP | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -3.19 | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | -0.22 | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -0.88 | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
MPC4300 | 01 NORTH | 20.5 | DIS-18-2-PQ | WIND | 400 | [9 empty] | ER/NR | OTP
GIA-100 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 40 | [9 empty] | ER/NR | AECI
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 75 | [9 empty] | ER/NR | AECI
GIA-99 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 470 | [9 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | WIND | 40 | [9 empty] | ER | WAPA |  | DISIS STAGE
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | BEPC-SPP | Neset 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | [9 empty] | ER | WERE | Neosho 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | [9 empty] | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | IA PENDING
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | Done: Phase 3
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery/Storage | 20 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Done: Phase 3
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Adams 345 kV Substation | Done: Phase 3
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | Done: Phase 3
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV Substation | Done: Phase 3
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER | ALTW | Magnolia 161 kV Substation | Done: Phase 3
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | XEL | Grant 115 kV Substation | Done: Phase 3
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Hazleton - Mitchell county 345 kV line | Done: Phase 3
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | Active: Phase 3
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | XEL | Grant 115 kV Substation | Done: Phase 3
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | DPC | Apple River 161 kV Substation | Done: Phase 3
J1325 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Magnolia 161 kV substation | Done: Phase 3
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Benton County 115kV Substation | Done: Phase 3
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | Done: Phase 3
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | Active: Phase 3
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Active: Phase 3
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Active: Phase 3
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV | Active: Phase 3
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Rutland Substation 161kV | Active: Phase 3
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 150 | [9 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | Active: Phase 3
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [9 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Active: Phase 3
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Nobles County 345 kV Substation | Active: Phase 3
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Bison 345kV | Active: Phase 3
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Sherburne 345kV | Active: Phase 3
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 174 | [9 empty] | ER/NR | XEL | Langola 115kV Tap | Active: Phase 3
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL | Pipestone to Split Rock 115kV | Active: Phase 3
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Pine Lake to Apple River 161 kV | Active: Phase 3
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | Active: Phase 3
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 120 | [9 empty] | ER/NR | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Active: Phase 3
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | DPC | Barron 161 kV | Active: Phase 3
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [9 empty] | ER/NR | XEL | Cannon Falls Transmission 69 kV | Done: Phase 3
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER/NR | XEL | Adams 345kV Substation | Done: Phase 3
MPC3600 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 100 | [9 empty] | ER | OTP |  | DISIS STAGE
MPC3700 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 75 | [9 empty] | ER | OTP |  | DISIS STAGE
MPC3800 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 250 | [9 empty] | ER/NR | OTP |  | DISIS STAGE
MPC3900 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 151.2 | [9 empty] | ER/NR | OTP
MPC4000 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 300 | [9 empty] | ER/NR | OTP
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [9 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | Done: Phase 3
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW | Creston East 69 kV Substation | Done: Phase 3
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Done: Phase 3
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [9 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | Done: Phase 3
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Kossuth - O'Brien 345 kV Line Tap | Done: Phase 3
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | ALTW | 161kV bus at Karma substation | Done: Phase 3
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [9 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | Active: Phase 3
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [9 empty] | ER/NR | ALTW | Traer 161-kV Substation | Active: Phase 3
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | Active: Phase 3
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV | Active: Phase 3
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Active: Phase 3
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Active: Phase 3
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | Active: Phase 3
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | O'Brien - Raun 345 kV | Active: Phase 3
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Done: Phase 3
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Done: GIA
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 400 | [9 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | Done: GIA
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Done: GIA
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | Done: GIA
J1191 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 64 | [9 empty] | ER/NR | CWLD | Bolstad 69 kV Substation | Active
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 68.4 | [9 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | Done
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | Done
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Done
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [9 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | Done
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMIL | Ashley 138 kV Substation | Active
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | Done
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | Done
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | Done
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | Active
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | Active
J1352 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | Done
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 500 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Active
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 1000 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Active
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | Done: GIA
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Done: GIA
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Montgomery 161kV Substation | Done: GIA
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Guthrie 161 kV Substation | Done: GIA
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Active: Phase 3
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [9 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Done: GIA
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Done: GIA
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Done: GIA
J1231 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | BREC | Barkley - Caldwell 161kV Line | Done: Study Not Started
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | Done
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | Done: GIA
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Poco - Menard 138kV Line Tao | Done: GIA
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 500 | [9 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | Done: GIA
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | Done: GIA
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | Done: GIA
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | CLEC | Centennial - West Bay 138kV Line | Done: Phase 3
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | Done: Phase 3
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | EES | Rilla 115 kV Substation | Done: Phase 3
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: Phase 3
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | Done: Phase 3
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | Done: Phase 3
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 0 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | Done: Phase 3
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: Phase 3
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | Done: Phase 3
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | Done: Phase 3
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | EES | Oak Ridge 115 kV Substation | Done: Phase 3
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [9 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | Done: Phase 3
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | Done: Phase 3
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230kV | Active: Phase 3
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Active: Phase 3
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Active: Phase 3
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Active: Phase 3
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Hardin West SS (Endpoint A) to Sheridan (Endpoint B) 115 kV | Done: Phase 3
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [9 empty] | ER/NR | EES | Goos Ferry | Active: Phase 3
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 25 | [9 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Active: Phase 3
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Active: Phase 3
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Active: Phase 3
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Active: Phase 3
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | Active: Phase 3
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | Active: Phase 3
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Active: Phase 3
J1709 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 100 | [9 empty] | ER | EES | 138 kV Grimes | Active: Phase 3
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Active: Phase 3
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EMI | J830 POI | Active: Phase 3
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | Active: Phase 3
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [9 empty] | ER/NR | EES | Timberland 230kV | Active: Phase 3
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Active: Phase 3
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [9 empty] | ER/NR | EES | Bastrop tap point | Active: Phase 3
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [9 empty] | ER/NR | EES | Sabine 138/230 kV Substation | Active: Phase 3
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [9 empty] | ER | EES-EAI | Forrest City to Wynne S 161 KV | Active: Phase 3
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 97.5 | [9 empty] | ER | AECI
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid: Solar | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | [9 empty] | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 29.6 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-202 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 | [9 empty] | ER/NR | SWPA | New Madrid - Sikeston 161kV | WITHDRAWN
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | Hybrid: Solar | 300 | [9 empty] | ER | KCPL | LaCygne - Neosho 345kV | TERMINATED
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-154 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 255 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | TERMINATED
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-167 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Sunnyside 345kV | TERMINATED
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Hybrid: Solar | 210 | [9 empty] | ER | OKGE | Renfrow 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL | Buffalo 115kV Substation | Done: Phase 3
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP | Big Stone South 230kV Substation | Done: Phase 3
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | Done: Phase 3
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Done: Phase 3
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap | Done: Phase 3
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 101.28 | [9 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line | Done: Phase 3
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW | Ledyard 345kV Substation | Done: Phase 3
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Done: Phase 3
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW | Murray Junction 69 kV substation
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | AEPW | Chamber Springs 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | WAPA | NELSON 7
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2017-006GIA-53 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 238 | [9 empty] | ER/NR | AECI | 5MARYVL
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 01 NORTH | 16 | DIS-16-1 | Wind | 100.05 | [9 empty] | ER | WAPA | Valley City 115 kV | TERMINATED
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 5.3 | [9 empty] | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 20 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 | [9 empty] | ER | OKGE | Gracemont 345kV | TERMINATED
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [9 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [9 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 11.72 | [9 empty] | ER/NR | BEPC | Williston 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC2100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP | Center - Mandan 230 kV
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Hybrid: Solar and Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Hybrid: Solar and Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS | FE-Clovis Interchange 115kV
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [9 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 SOUTHEAST | 8 | PQ | Wind | 150 | [9 empty] | ER | AECI | Remington 138kV
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 23SP | ERIS 26SP | ERIS 26L | ERIS 26WP | NRIS 23SP | NRIS 26SP | NRIS 26L | NRIS 26WP | Stability 25SP | Stability 25WP
GEN-2018-067 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 255 | 0 | Non-converge | Build Strandahl to Black Tail 115 kV line | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2018-067 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 255 | 0 | Non-converge | Build Strandahl to Black Tail 115 kV line | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2018-067 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 255 | 0 | Non-converge | Build Strandahl to Black Tail 115 kV line | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2018-067 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 255 | 0 | Non-converge | Build Strandahl to Black Tail 115 kV line | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2018-067 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 255 | 0 | Non-converge | Build Strandahl to Black Tail 115 kV line | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2018-067 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 255 | 0 | Non-converge | Build Strandahl to Black Tail 115 kV line | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2018-067 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 255 | 0 | Stability | Build Strandahl to Black Tail 115 kV line | N/A | N/A | N/A | 255 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2018-067 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 255 | 0 | Stability | Build Strandahl to Black Tail 115 kV line | N/A | N/A | N/A | 255 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2018-069 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 125 | 125 | None | None | N/A | N/A | 125 | N/A | N/A | N/A | 125 | N/A | 125 | 125
GEN-2018-069 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 125 | 125 | None | None | N/A | N/A | 125 | N/A | N/A | N/A | 125 | N/A | 125 | 125
GEN-2018-069 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 125 | 125 | None | None | 125 | N/A | N/A | N/A | 86.794 | N/A | N/A | N/A | 125 | N/A
GEN-2018-069 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 125 | 125 | None | None | N/A | 125 | N/A | N/A | N/A | 125 | N/A | N/A | 125 | N/A
GEN-2018-069 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 125 | 125 | None | None | N/A | N/A | 125 | N/A | N/A | N/A | 125 | N/A | 125 | 125
GEN-2018-069 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 125 | 125 | None | None | N/A | N/A | 125 | N/A | N/A | N/A | 125 | N/A | 125 | 125
GEN-2018-069 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 125 | 121.9889 | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 ftlo P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | East Fork 345/115 kV Substation | N/A | N/A | N/A | 121.9889 | N/A | N/A | N/A | 0 | N/A | 125
GEN-2018-069 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 125 | 121.9889 | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 ftlo P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | East Fork 345/115 kV Substation | N/A | N/A | N/A | 121.9889 | N/A | N/A | N/A | 0 | N/A | 125
GEN-2018-074 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 72 | 33.8431 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Build a new 69 kV tap station cutting off Denison - Denison Main and K338 - K318 circuits | N/A | N/A | 33.8431 | N/A | N/A | N/A | N/A | N/A | 72 | 72
GEN-2018-074 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 72 | 33.8431 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Build a new 69 kV tap station cutting off Denison - Denison Main and K338 - K318 circuits | N/A | N/A | 33.8431 | N/A | N/A | N/A | N/A | N/A | 72 | 72
GEN-2018-074 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 72 | 0 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT | Build a new 69 kV tap station cutting off Denison - Denison Main and K338 - K318 circuits | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 72 | N/A
GEN-2018-074 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 72 | 18.9081 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Build a new 69 kV tap station cutting off Denison - Denison Main and K338 - K318 circuits | N/A | 18.9081 | N/A | N/A | N/A | N/A | N/A | N/A | 72 | N/A
GEN-2018-074 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 72 | 33.8431 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Build a new 69 kV tap station cutting off Denison - Denison Main and K338 - K318 circuits | N/A | N/A | 33.8431 | N/A | N/A | N/A | N/A | N/A | 72 | 72
GEN-2018-074 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 72 | 33.8431 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Build a new 69 kV tap station cutting off Denison - Denison Main and K338 - K318 circuits | N/A | N/A | 33.8431 | N/A | N/A | N/A | N/A | N/A | 72 | 72
GEN-2018-074 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 72 | 0 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Build a new 69 kV tap station cutting off Denison - Denison Main and K338 - K318 circuits | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 72
GEN-2018-074 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 72 | 0 | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 ftlo P12:161:WAPA:DENISON-EXIRA:1 | Build a new 69 kV tap station cutting off Denison - Denison Main and K338 - K318 circuits | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 72
GEN-2019-019 | 01 NORTH | Thermal | April 1 - May 31 (Near Term) | 15.15 | 15.15 | None | None | 15.15 | N/A | N/A | 15.15 | 15.15 | N/A | N/A | 15.15 | 15.15 | 15.15
GEN-2019-019 | 01 NORTH | Thermal | April 1 - May 31 (Long Term) | 15.15 | 15.15 | None | None | N/A | 15.15 | N/A | 15.15 | N/A | 15.15 | N/A | 15.15 | 15.15 | 15.15
GEN-2019-019 | 01 NORTH | Thermal | June 1 - Sept 30 (Near Term) | 15.15 | 15.15 | None | None | N/A | 15.15 | N/A | N/A | N/A | 15.15 | N/A | N/A | 15.15 | N/A
GEN-2019-019 | 01 NORTH | Thermal | June 1 - Sept 30 (Long Term) | 15.15 | 15.15 | None | None | N/A | 15.15 | N/A | N/A | N/A | 15.15 | N/A | N/A | 15.15 | N/A
GEN-2019-019 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Near Term) | 15.15 | 15.15 | None | None | 15.15 | N/A | N/A | 15.15 | 15.15 | N/A | N/A | 15.15 | 15.15 | 15.15
GEN-2019-019 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Long Term) | 15.15 | 15.15 | None | None | N/A | 15.15 | N/A | 15.15 | N/A | 15.15 | N/A | 15.15 | 15.15 | 15.15
GEN-2019-019 | 01 NORTH | Thermal | Dec 1 - March 31 (Near Term) | 15.15 | 15.15 | None | None | N/A | N/A | N/A | 15.15 | N/A | N/A | N/A | 15.15 | N/A | 15.15
GEN-2019-019 | 01 NORTH | Thermal | Dec 1 - March 31 (Long Term) | 15.15 | 15.15 | None | None | N/A | N/A | N/A | 15.15 | N/A | N/A | N/A | 15.15 | N/A | 15.15
GEN-2019-023 | 01 NORTH | Hybrid | April 1 - May 31 (Near Term) | 110 | 107.3502 | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 ftlo P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | East Fork 345/115 kV Substation | 110 | N/A | N/A | 107.3502 | 76.3784 | N/A | N/A | 0 | 110 | 110
GEN-2019-023 | 01 NORTH | Hybrid | April 1 - May 31 (Long Term) | 110 | 107.3502 | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 ftlo P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | East Fork 345/115 kV Substation | N/A | 110 | N/A | 107.3502 | N/A | 100.2592 | N/A | 0 | 110 | 110
GEN-2019-023 | 01 NORTH | Hybrid | June 1 - Sept 30 (Near Term) | 110 | 110 | None | None | 110 | N/A | N/A | N/A | 76.3784 | N/A | N/A | N/A | 110 | N/A
GEN-2019-023 | 01 NORTH | Hybrid | June 1 - Sept 30 (Long Term) | 110 | 110 | None | None | N/A | 110 | N/A | N/A | N/A | 100.2592 | N/A | N/A | 110 | N/A
GEN-2019-023 | 01 NORTH | Hybrid | Oct 1 - Nov 30 (Near Term) | 110 | 107.3502 | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 ftlo P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | East Fork 345/115 kV Substation | 110 | N/A | N/A | 107.3502 | 76.3784 | N/A | N/A | 0 | 110 | 110
GEN-2019-023 | 01 NORTH | Hybrid | Oct 1 - Nov 30 (Long Term) | 110 | 107.3502 | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 ftlo P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | East Fork 345/115 kV Substation | N/A | 110 | N/A | 107.3502 | N/A | 100.2592 | N/A | 0 | 110 | 110
GEN-2019-023 | 01 NORTH | Hybrid | Dec 1 - March 31 (Near Term) | 110 | 107.3502 | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 ftlo P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | East Fork 345/115 kV Substation | N/A | N/A | N/A | 107.3502 | N/A | N/A | N/A | 0 | N/A | 110
GEN-2019-023 | 01 NORTH | Hybrid | Dec 1 - March 31 (Long Term) | 110 | 107.3502 | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 ftlo P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | East Fork 345/115 kV Substation | N/A | N/A | N/A | 107.3502 | N/A | N/A | N/A | 0 | N/A | 110
GEN-2019-037 | 01 NORTH | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-037 | 01 NORTH | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-037 | 01 NORTH | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2019-037 | 01 NORTH | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2019-037 | 01 NORTH | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-037 | 01 NORTH | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-037 | 01 NORTH | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-037 | 01 NORTH | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2018-065 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-065 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-065 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-065 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-065 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-065 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-065 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-065 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 19.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-068 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-068 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-068 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-068 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-068 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-068 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-068 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-068 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 302.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-083 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250 | 250
GEN-2018-083 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250 | 250
GEN-2018-083 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 250 | 186.0611 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 186.0611 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 250 | N/A
GEN-2018-083 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 250 | 179.0634 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 179.0634 | N/A | N/A | N/A | N/A | N/A | N/A | 250 | N/A
GEN-2018-083 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250 | 250
GEN-2018-083 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 250 | 250 | None | None | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250 | 250
GEN-2018-083 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 250 | 172.7981 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | N/A | N/A | 172.7981 | N/A | N/A | N/A | N/A | N/A | 250
GEN-2018-083 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 250 | 172.7981 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | N/A | N/A | 172.7981 | N/A | N/A | N/A | N/A | N/A | 250
GEN-2018-125 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 231 | 231 | None | None | N/A | N/A | 231 | N/A | N/A | N/A | 231 | N/A | 231 | 231
GEN-2018-125 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 231 | 231 | None | None | N/A | N/A | 231 | N/A | N/A | N/A | 231 | N/A | 231 | 231
GEN-2018-125 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 231 | 231 | None | None | 231 | N/A | N/A | N/A | 231 | N/A | N/A | N/A | 231 | N/A
GEN-2018-125 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 231 | 231 | None | None | N/A | 231 | N/A | N/A | N/A | 231 | N/A | N/A | 231 | N/A
GEN-2018-125 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 231 | 231 | None | None | N/A | N/A | 231 | N/A | N/A | N/A | 231 | N/A | 231 | 231
GEN-2018-125 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 231 | 231 | None | None | N/A | N/A | 231 | N/A | N/A | N/A | 231 | N/A | 231 | 231
GEN-2018-125 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 231 | 231 | None | None | N/A | N/A | N/A | 231 | N/A | N/A | N/A | 0 | N/A | 231
GEN-2018-125 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 231 | 231 | None | None | N/A | N/A | N/A | 231 | N/A | N/A | N/A | 0 | N/A | 231
GEN-2018-131 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 221.4 | 219.1738 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | 164.7757 | N/A | N/A | 153.03 | 219.1738 | N/A | N/A | 220.6361 | 221.4 | 221.4
GEN-2018-131 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 221.4 | 219.6103 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | 158.5785 | N/A | 153.03 | N/A | 219.6103 | N/A | 220.6361 | 221.4 | 221.4
GEN-2018-131 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 221.4 | 219.1738 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | 164.7757 | N/A | N/A | N/A | 219.1738 | N/A | N/A | N/A | 221.4 | N/A
GEN-2018-131 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 221.4 | 219.6103 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | 158.5785 | N/A | N/A | N/A | 219.6103 | N/A | N/A | 221.4 | N/A
GEN-2018-131 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 221.4 | 219.1738 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | 164.7757 | N/A | N/A | 153.03 | 219.1738 | N/A | N/A | 220.6361 | 221.4 | 221.4
GEN-2018-131 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 221.4 | 219.6103 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | 158.5785 | N/A | 153.03 | N/A | 219.6103 | N/A | 220.6361 | 221.4 | 221.4
GEN-2018-131 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 221.4 | 220.6361 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | N/A | N/A | 153.03 | N/A | N/A | N/A | 220.6361 | N/A | 221.4
GEN-2018-131 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 221.4 | 220.6361 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | N/A | N/A | 153.03 | N/A | N/A | N/A | 220.6361 | N/A | 221.4
GEN-2018-132 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 201.6 | 199.5728 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | 150.0396 | N/A | N/A | 139.3444 | 199.5728 | N/A | N/A | 200.9044 | 201.6 | 201.6
GEN-2018-132 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 201.6 | 199.9703 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | 144.3967 | N/A | 139.3444 | N/A | 199.9703 | N/A | 200.9044 | 201.6 | 201.6
GEN-2018-132 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 201.6 | 199.5728 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | 150.0396 | N/A | N/A | N/A | 199.5728 | N/A | N/A | N/A | 201.6 | N/A
GEN-2018-132 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 201.6 | 199.9703 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | 144.3967 | N/A | N/A | N/A | 199.9703 | N/A | N/A | 201.6 | N/A
GEN-2018-132 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 201.6 | 199.5728 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | 150.0396 | N/A | N/A | 139.3444 | 199.5728 | N/A | N/A | 200.9044 | 201.6 | 201.6
GEN-2018-132 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 201.6 | 199.9703 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | 144.3967 | N/A | 139.3444 | N/A | 199.9703 | N/A | 200.9044 | 201.6 | 201.6
GEN-2018-132 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 201.6 | 200.9044 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | N/A | N/A | 139.3444 | N/A | N/A | N/A | 200.9044 | N/A | 201.6
GEN-2018-132 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 201.6 | 200.9044 | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 ftlo 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | N/A | N/A | N/A | 139.3444 | N/A | N/A | N/A | 200.9044 | N/A | 201.6
GEN-2019-009 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-009 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-009 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-009 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-009 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-009 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-009 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-009 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-039 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 174.5 | 138.814 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 ftlo 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Rebuild Rising to G19-039-TAP 115 kV | 138.604 | N/A | N/A | 139.416 | 138.814 | N/A | N/A | 139.57 | 174.5 | 174.5
GEN-2019-039 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 174.5 | 138.548 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 ftlo 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Rebuild Rising to G19-039-TAP 115 kV | N/A | 138.492 | N/A | 139.416 | N/A | 138.548 | N/A | 139.57 | 174.5 | 174.5
GEN-2019-039 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 174.5 | 138.814 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 ftlo 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Rebuild Rising to G19-039-TAP 115 kV | 138.604 | N/A | N/A | N/A | 138.814 | N/A | N/A | N/A | 174.5 | N/A
GEN-2019-039 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 174.5 | 138.548 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 ftlo 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Rebuild Rising to G19-039-TAP 115 kV | N/A | 138.492 | N/A | N/A | N/A | 138.548 | N/A | N/A | 174.5 | N/A
GEN-2019-039 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 174.5 | 138.814 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 ftlo 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Rebuild Rising to G19-039-TAP 115 kV | 138.604 | N/A | N/A | 139.416 | 138.814 | N/A | N/A | 139.57 | 174.5 | 174.5
GEN-2019-039 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 174.5 | 138.548 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 ftlo 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Rebuild Rising to G19-039-TAP 115 kV | N/A | 138.492 | N/A | 139.416 | N/A | 138.548 | N/A | 139.57 | 174.5 | 174.5
GEN-2019-039 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 174.5 | 139.57 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 ftlo 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Rebuild Rising to G19-039-TAP 115 kV | N/A | N/A | N/A | 139.416 | N/A | N/A | N/A | 139.57 | N/A | 174.5
GEN-2019-039 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 174.5 | 139.57 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 ftlo 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Rebuild Rising to G19-039-TAP 115 kV | N/A | N/A | N/A | 139.416 | N/A | N/A | N/A | 139.57 | N/A | 174.5
GEN-2019-041 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 78 | 78 | None | None | N/A | 78 | N/A | 78 | 78 | N/A | N/A | 78 | 78 | 78
GEN-2019-041 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 78 | 78 | None | None | N/A | N/A | N/A | 78 | N/A | 78 | N/A | 78 | 78 | 78
GEN-2019-041 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 78 | 78 | None | None | 78 | N/A | N/A | N/A | 78 | N/A | N/A | N/A | 78 | N/A
GEN-2019-041 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 78 | 78 | None | None | N/A | 78 | N/A | N/A | N/A | 78 | N/A | N/A | 78 | N/A
GEN-2019-041 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 78 | 78 | None | None | 78 | N/A | N/A | 78 | 78 | N/A | N/A | 78 | 78 | 78
GEN-2019-041 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 78 | 78 | None | None | N/A | 78 | N/A | 78 | N/A | 78 | N/A | 78 | 78 | 78
GEN-2019-041 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 78 | 78 | None | None | N/A | N/A | N/A | 78 | N/A | N/A | N/A | 78 | N/A | 78
GEN-2019-041 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 78 | 78 | None | None | N/A | N/A | N/A | 78 | N/A | N/A | N/A | 78 | N/A | 78
GEN-2019-069 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 74.4244 | N/A | N/A | 69.1192 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-069 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 71.6254 | N/A | 69.1192 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-069 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 100 | 74.4244 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 74.4244 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-069 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 100 | 71.6254 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 71.6254 | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-069 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 74.4244 | N/A | N/A | 69.1192 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-069 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 71.6254 | N/A | 69.1192 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-069 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | N/A | N/A | 69.1192 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-069 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997021 HOSKN T4 _1 115 1 ftlo P13:230-345:NPPD:HOSKINS3:T2:::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | N/A | N/A | 69.1192 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-070 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 50 | 34.5596 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 37.2122 | N/A | N/A | 34.5596 | N/A | N/A | N/A | N/A | 50 | 50
GEN-2019-070 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 50 | 34.5596 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 35.8127 | N/A | 34.5596 | N/A | N/A | N/A | N/A | 50 | 50
GEN-2019-070 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 50 | 37.2122 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 37.2122 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 50 | N/A
GEN-2019-070 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 50 | 35.8127 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 35.8127 | N/A | N/A | N/A | N/A | N/A | N/A | 50 | N/A
GEN-2019-070 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 50 | 34.5596 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 37.2122 | N/A | N/A | 34.5596 | N/A | N/A | N/A | N/A | 50 | 50
GEN-2019-070 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 50 | 34.5596 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 35.8127 | N/A | 34.5596 | N/A | N/A | N/A | N/A | 50 | 50
GEN-2019-070 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 50 | 34.5596 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | N/A | N/A | 34.5596 | N/A | N/A | N/A | N/A | N/A | 50
GEN-2019-070 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 50 | 34.5596 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | N/A | N/A | 34.5596 | N/A | N/A | N/A | N/A | N/A | 50
GEN-2019-073 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 74.4244 | N/A | N/A | 69.1192 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-073 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 71.6254 | N/A | 69.1192 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-073 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 100 | 74.4244 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 74.4244 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-073 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 100 | 71.6254 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 71.6254 | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-073 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | 74.4244 | N/A | N/A | 69.1192 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-073 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | 71.6254 | N/A | 69.1192 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-073 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | N/A | N/A | 69.1192 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-073 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 100 | 69.1192 | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 ftlo P13:115-345:NPPD:NUCOR-2::::: | Build a Second 345-230 kV Transformer at Hoskins_345kV | N/A | N/A | N/A | 69.1192 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2018-063 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-063 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-063 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-063 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-063 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-063 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-063 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-063 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 57 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-108 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 95 | 95 | None | None | 95 | N/A | N/A | 95 | N/A | N/A | N/A | N/A | 95 | 95
GEN-2018-108 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 95 | 95 | None | None | N/A | 95 | N/A | 95 | N/A | N/A | N/A | N/A | 95 | 95
GEN-2018-108 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 95 | 95 | None | None | 95 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 95 | N/A
GEN-2018-108 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 95 | 95 | None | None | N/A | 95 | N/A | N/A | N/A | N/A | N/A | N/A | 95 | N/A
GEN-2018-108 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 95 | 95 | None | None | 95 | N/A | N/A | 95 | N/A | N/A | N/A | N/A | 95 | 95
GEN-2018-108 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 95 | 95 | None | None | N/A | 95 | N/A | 95 | N/A | N/A | N/A | N/A | 95 | 95
GEN-2018-108 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 95 | 95 | None | None | N/A | N/A | N/A | 95 | N/A | N/A | N/A | N/A | N/A | 95
GEN-2018-108 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 95 | 95 | None | None | N/A | N/A | N/A | 95 | N/A | N/A | N/A | N/A | N/A | 95
GEN-2018-116 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-116 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-116 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-116 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-116 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-116 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-116 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-116 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-128 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 200.22 | 200.22 | None | None | N/A | N/A | 200.22 | N/A | N/A | N/A | 200.22 | N/A | 200.22 | 200.22
GEN-2018-128 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 200.22 | 200.22 | None | None | N/A | N/A | 200.22 | N/A | N/A | N/A | 200.22 | N/A | 200.22 | 200.22
GEN-2018-128 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 200.22 | 200.22 | None | None | 200.22 | N/A | N/A | N/A | 200.22 | N/A | N/A | N/A | 200.22 | N/A
GEN-2018-128 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 200.22 | 200.22 | None | None | N/A | 200.22 | N/A | N/A | N/A | 200.22 | N/A | N/A | 200.22 | N/A
GEN-2018-128 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 200.22 | 200.22 | None | None | N/A | N/A | 200.22 | N/A | N/A | N/A | 200.22 | N/A | 200.22 | 200.22
GEN-2018-128 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 200.22 | 200.22 | None | None | N/A | N/A | 200.22 | N/A | N/A | N/A | 200.22 | N/A | 200.22 | 200.22
GEN-2018-128 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 200.22 | 200.22 | None | None | N/A | N/A | N/A | 200.22 | N/A | N/A | N/A | 200.22 | N/A | 200.22
GEN-2018-128 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 200.22 | 200.22 | None | None | N/A | N/A | N/A | 200.22 | N/A | N/A | N/A | 200.22 | N/A | 200.22
GEN-2019-001 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 25 | 25 | None | None | N/A | N/A | 25 | N/A | N/A | N/A | N/A | N/A | 25 | 25
GEN-2019-001 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 25 | 25 | None | None | N/A | N/A | 25 | N/A | N/A | N/A | N/A | N/A | 25 | 25
GEN-2019-001 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 25 | 25 | None | None | 25 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 25 | N/A
GEN-2019-001 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 25 | 25 | None | None | N/A | 25 | N/A | N/A | N/A | N/A | N/A | N/A | 25 | N/A
GEN-2019-001 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 25 | 25 | None | None | N/A | N/A | 25 | N/A | N/A | N/A | N/A | N/A | 25 | 25
GEN-2019-001 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 25 | 25 | None | None | N/A | N/A | 25 | N/A | N/A | N/A | N/A | N/A | 25 | 25
GEN-2019-001 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 25 | 25 | None | None | N/A | N/A | N/A | 25 | N/A | N/A | N/A | N/A | N/A | 25
GEN-2019-001 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 25 | 25 | None | None | N/A | N/A | N/A | 25 | N/A | N/A | N/A | N/A | N/A | 25
GEN-2019-016 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2019-016 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2019-016 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 200 | N/A
GEN-2019-016 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | N/A | N/A | N/A | N/A | N/A | 200 | N/A
GEN-2019-016 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2019-016 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | 200 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2019-016 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 200
GEN-2019-016 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | N/A | N/A | 200
GEN-2019-018 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 15.56 | 15.56 | None | None | 15.56 | N/A | N/A | 15.56 | 15.56 | N/A | N/A | 15.56 | 15.56 | 15.56
GEN-2019-018 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 15.56 | 15.56 | None | None | N/A | 15.56 | N/A | 15.56 | N/A | 15.56 | N/A | 15.56 | 15.56 | 15.56
GEN-2019-018 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 15.56 | 15.56 | None | None | N/A | 15.56 | N/A | N/A | N/A | 15.56 | N/A | N/A | 15.56 | N/A
GEN-2019-018 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 15.56 | 15.56 | None | None | N/A | 15.56 | N/A | N/A | N/A | 15.56 | N/A | N/A | 15.56 | N/A
GEN-2019-018 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 15.56 | 15.56 | None | None | 15.56 | N/A | N/A | 15.56 | 15.56 | N/A | N/A | 15.56 | 15.56 | 15.56
GEN-2019-018 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 15.56 | 15.56 | None | None | N/A | 15.56 | N/A | 15.56 | N/A | 15.56 | N/A | 15.56 | 15.56 | 15.56
GEN-2019-018 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 15.56 | 15.56 | None | None | N/A | N/A | N/A | 15.56 | N/A | N/A | N/A | 15.56 | N/A | 15.56
GEN-2019-018 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 15.56 | 15.56 | None | None | N/A | N/A | N/A | 15.56 | N/A | N/A | N/A | 15.56 | N/A | 15.56
GEN-2019-030 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 252 | 252 | None | None | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252 | 252
GEN-2019-030 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 252 | 252 | None | None | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252 | 252
GEN-2019-030 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 252 | 252 | None | None | 252 | N/A | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A
GEN-2019-030 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 252 | 252 | None | None | N/A | 252 | N/A | N/A | N/A | 252 | N/A | N/A | 252 | N/A
GEN-2019-030 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 252 | 252 | None | None | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252 | 252
GEN-2019-030 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 252 | 252 | None | None | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252 | 252
GEN-2019-030 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 252 | 252 | None | None | N/A | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252
GEN-2019-030 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 252 | 252 | None | None | N/A | N/A | N/A | 252 | N/A | N/A | N/A | 252 | N/A | 252
GEN-2019-035 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-035 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-035 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-035 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-035 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-035 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-035 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-035 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 80 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-044 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 100 | 66.406 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 ftlo System Intact | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade | 66.406 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-044 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 100 | 89.6437 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 ftlo System Intact | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade | N/A | 89.6437 | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-044 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 100 | 66.406 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 ftlo System Intact | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade | 66.406 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-044 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 100 | 89.6437 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 ftlo System Intact | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade | N/A | 89.6437 | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-044 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 100 | 66.406 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 ftlo System Intact | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade | 66.406 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-044 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 100 | 89.6437 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 ftlo System Intact | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade | N/A | 89.6437 | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-044 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-044 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-048 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-048 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-048 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-048 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-048 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-048 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-048 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-048 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-051 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-051 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-051 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-051 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-051 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-051 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-051 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-051 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 40 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-053 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2019-053 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2019-053 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A
GEN-2019-053 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | N/A | N/A | 50 | N/A | N/A | 50 | N/A
GEN-2019-053 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2019-053 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2019-053 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2019-053 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2019-054 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-054 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-054 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2019-054 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2019-054 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-054 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-054 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-054 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-055 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-055 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-055 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2019-055 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2019-055 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-055 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-055 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-055 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-058 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-058 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-058 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2019-058 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2019-058 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-058 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-058 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-058 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-063 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2019-063 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2019-063 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A
GEN-2019-063 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | N/A | N/A | 50 | N/A | N/A | 50 | N/A
GEN-2019-063 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2019-063 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2019-063 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2019-063 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2019-068 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2019-068 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2019-068 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A
GEN-2019-068 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | N/A | N/A | 50 | N/A | N/A | 50 | N/A
GEN-2019-068 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2019-068 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2019-068 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2019-068 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2018-064 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 80 | 80 | None | None | 80 | N/A | N/A | 80 | 80 | N/A | N/A | 80 | 80 | 80
GEN-2018-064 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 80 | 80 | None | None | N/A | 80 | N/A | 80 | N/A | 80 | N/A | 80 | 80 | 80
GEN-2018-064 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 80 | 80 | None | None | 80 | N/A | N/A | N/A | 80 | N/A | N/A | N/A | 80 | N/A
GEN-2018-064 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 80 | 80 | None | None | N/A | 80 | N/A | N/A | N/A | 80 | N/A | N/A | 80 | N/A
GEN-2018-064 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 80 | 80 | None | None | 80 | N/A | N/A | 80 | 80 | N/A | N/A | 80 | 80 | 80
GEN-2018-064 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 80 | 80 | None | None | N/A | 80 | N/A | 80 | N/A | 80 | N/A | 80 | 80 | 80
GEN-2018-064 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 80 | 80 | None | None | N/A | N/A | N/A | 80 | N/A | N/A | N/A | 80 | N/A | 80
GEN-2018-064 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 80 | 80 | None | None | N/A | N/A | N/A | 80 | N/A | N/A | N/A | 80 | N/A | 80
GEN-2018-071 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 151 | 151 | None | None | 151 | N/A | N/A | 151 | 151 | N/A | N/A | 151 | 151 | 151
GEN-2018-071 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 151 | 151 | None | None | N/A | 151 | N/A | 151 | N/A | 151 | N/A | 151 | 151 | 151
GEN-2018-071 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 151 | 151 | None | None | 151 | N/A | N/A | N/A | 151 | N/A | N/A | N/A | 151 | N/A
GEN-2018-071 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 151 | 151 | None | None | N/A | 151 | N/A | N/A | N/A | 151 | N/A | N/A | 151 | N/A
GEN-2018-071 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 151 | 151 | None | None | 151 | N/A | N/A | 151 | 151 | N/A | N/A | 151 | 151 | 151
GEN-2018-071 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 151 | 151 | None | None | N/A | 151 | N/A | 151 | N/A | 151 | N/A | 151 | 151 | 151
GEN-2018-071 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 151 | 151 | None | None | N/A | N/A | N/A | 151 | N/A | N/A | N/A | 151 | N/A | 151
GEN-2018-071 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 151 | 151 | None | None | N/A | N/A | N/A | 151 | N/A | N/A | N/A | 151 | N/A | 151
GEN-2018-072 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 151 | 151 | None | None | 151 | N/A | N/A | 151 | 151 | N/A | N/A | 151 | 151 | 151
GEN-2018-072 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 151 | 151 | None | None | N/A | 151 | N/A | 151 | N/A | 151 | N/A | 151 | 151 | 151
GEN-2018-072 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 151 | 151 | None | None | 151 | N/A | N/A | N/A | 151 | N/A | N/A | N/A | 151 | N/A
GEN-2018-072 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 151 | 151 | None | None | N/A | 151 | N/A | N/A | N/A | 151 | N/A | N/A | 151 | N/A
GEN-2018-072 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 151 | 151 | None | None | 151 | N/A | N/A | 151 | 151 | N/A | N/A | 151 | 151 | 151
GEN-2018-072 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 151 | 151 | None | None | N/A | 151 | N/A | 151 | N/A | 151 | N/A | 151 | 151 | 151
GEN-2018-072 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 151 | 151 | None | None | N/A | N/A | N/A | 151 | N/A | N/A | N/A | 151 | N/A | 151
GEN-2018-072 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 151 | 151 | None | None | N/A | N/A | N/A | 151 | N/A | N/A | N/A | 151 | N/A | 151
GEN-2018-079 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 148 | 148 | None | None | 148 | N/A | N/A | 148 | N/A | N/A | N/A | N/A | 148 | 148
GEN-2018-079 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 148 | 148 | None | None | N/A | 148 | N/A | 148 | N/A | N/A | N/A | N/A | 148 | 148
GEN-2018-079 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 148 | 148 | None | None | 148 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 148 | N/A
GEN-2018-079 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 148 | 148 | None | None | N/A | 148 | N/A | N/A | N/A | N/A | N/A | N/A | 148 | N/A
GEN-2018-079 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 148 | 148 | None | None | 148 | N/A | N/A | 148 | N/A | N/A | N/A | N/A | 148 | 148
GEN-2018-079 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 148 | 148 | None | None | N/A | 148 | N/A | 148 | N/A | N/A | N/A | N/A | 148 | 148
GEN-2018-079 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 148 | 148 | None | None | N/A | N/A | N/A | 148 | N/A | N/A | N/A | N/A | N/A | 148
GEN-2018-079 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 148 | 148 | None | None | N/A | N/A | N/A | 148 | N/A | N/A | N/A | N/A | N/A | 148
GEN-2018-082 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 215 | 215 | None | None | N/A | N/A | 215 | N/A | N/A | N/A | N/A | N/A | 215 | 215
GEN-2018-082 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 215 | 215 | None | None | N/A | N/A | 215 | N/A | N/A | N/A | N/A | N/A | 215 | 215
GEN-2018-082 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 215 | 215 | None | None | 215 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 215 | N/A
GEN-2018-082 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 215 | 215 | None | None | N/A | 215 | N/A | N/A | N/A | N/A | N/A | N/A | 215 | N/A
GEN-2018-082 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 215 | 215 | None | None | N/A | N/A | 215 | N/A | N/A | N/A | N/A | N/A | 215 | 215
GEN-2018-082 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 215 | 215 | None | None | N/A | N/A | 215 | N/A | N/A | N/A | N/A | N/A | 215 | 215
GEN-2018-082 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 215 | 215 | None | None | N/A | N/A | N/A | 215 | N/A | N/A | N/A | N/A | N/A | 215
GEN-2018-082 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 215 | 215 | None | None | N/A | N/A | N/A | 215 | N/A | N/A | N/A | N/A | N/A | 215
GEN-2018-088 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-088 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-088 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-088 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-088 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-088 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-088 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-088 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 130 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2018-106 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 165 | 165 | None | None | 165 | N/A | N/A | 165 | N/A | N/A | N/A | N/A | 165 | 165
GEN-2018-106 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 165 | 165 | None | None | N/A | 165 | N/A | 165 | N/A | N/A | N/A | N/A | 165 | 165
GEN-2018-106 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 165 | 165 | None | None | 165 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 165 | N/A
GEN-2018-106 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 165 | 165 | None | None | N/A | 165 | N/A | N/A | N/A | N/A | N/A | N/A | 165 | N/A
GEN-2018-106 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 165 | 165 | None | None | 165 | N/A | N/A | 165 | N/A | N/A | N/A | N/A | 165 | 165
GEN-2018-106 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 165 | 165 | None | None | N/A | 165 | N/A | 165 | N/A | N/A | N/A | N/A | 165 | 165
GEN-2018-106 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 165 | 165 | None | None | N/A | N/A | N/A | 165 | N/A | N/A | N/A | N/A | N/A | 165
GEN-2018-106 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 165 | 165 | None | None | N/A | N/A | N/A | 165 | N/A | N/A | N/A | N/A | N/A | 165
GEN-2018-115 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | 250 | 250 | N/A | N/A | 250 | 250 | 250
GEN-2018-115 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | 250 | N/A | 250 | N/A | 250 | 250 | 250
GEN-2018-115 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A
GEN-2018-115 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | N/A | N/A | 250 | N/A | N/A | 250 | N/A
GEN-2018-115 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | 250 | 250 | N/A | N/A | 250 | 250 | 250
GEN-2018-115 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | 250 | N/A | 250 | N/A | 250 | 250 | 250
GEN-2018-115 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250
GEN-2018-115 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A | 250
GEN-2019-002 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-002 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-002 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-002 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | N/A | N/A | N/A | N/A | N/A | 100 | N/A
GEN-2019-002 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-002 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | N/A | N/A | N/A | 100 | 100
GEN-2019-002 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-002 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | N/A | N/A | 100
GEN-2019-012 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 200 | 200
GEN-2019-012 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 200 | 200
GEN-2019-012 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A
GEN-2019-012 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | N/A | N/A | 200 | N/A | N/A | 200 | N/A
GEN-2019-012 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 200 | 200
GEN-2019-012 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 200 | 200
GEN-2019-012 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2019-012 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2019-013 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 50 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GEN-2019-045 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 155 | 155 | None | None | 155 | N/A | N/A | 155 | N/A | N/A | N/A | N/A | 155 | 155
GEN-2019-045 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 155 | 155 | None | None | N/A | 155 | N/A | 155 | N/A | N/A | N/A | N/A | 155 | 155
GEN-2019-045 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 155 | 155 | None | None | 155 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 155 | N/A
GEN-2019-045 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 155 | 155 | None | None | N/A | 155 | N/A | N/A | N/A | N/A | N/A | N/A | 155 | N/A
GEN-2019-045 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 155 | 155 | None | None | 155 | N/A | N/A | 155 | N/A | N/A | N/A | N/A | 155 | 155
GEN-2019-045 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 155 | 155 | None | None | N/A | 155 | N/A | 155 | N/A | N/A | N/A | N/A | 155 | 155
GEN-2019-045 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 155 | 155 | None | None | N/A | N/A | N/A | 155 | N/A | N/A | N/A | N/A | N/A | 155
GEN-2019-045 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 155 | 155 | None | None | N/A | N/A | N/A | 155 | N/A | N/A | N/A | N/A | N/A | 155
GEN-2019-065 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 180 | 180 | None | None | 180 | N/A | N/A | 180 | N/A | N/A | N/A | N/A | 180 | 180
GEN-2019-065 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 180 | 180 | None | None | N/A | 180 | N/A | 180 | N/A | N/A | N/A | N/A | 180 | 180
GEN-2019-065 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 180 | 180 | None | None | 180 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 180 | N/A
GEN-2019-065 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 180 | 180 | None | None | N/A | 180 | N/A | N/A | N/A | N/A | N/A | N/A | 180 | N/A
GEN-2019-065 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 180 | 180 | None | None | 180 | N/A | N/A | 180 | N/A | N/A | N/A | N/A | 180 | 180
GEN-2019-065 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 180 | 180 | None | None | N/A | 180 | N/A | 180 | N/A | N/A | N/A | N/A | 180 | 180
GEN-2019-065 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 180 | 180 | None | None | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 180
GEN-2019-065 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 180 | 180 | None | None | N/A | N/A | N/A | 180 | N/A | N/A | N/A | N/A | N/A | 180
GEN-2018-089 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 196 | 196 | None | None | N/A | N/A | 196 | N/A | N/A | N/A | N/A | N/A | 196 | 196
GEN-2018-089 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 196 | 196 | None | None | N/A | N/A | 196 | N/A | N/A | N/A | N/A | N/A | 196 | 196
GEN-2018-089 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 196 | 196 | None | None | 196 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 196 | N/A
GEN-2018-089 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 196 | 196 | None | None | N/A | 196 | N/A | N/A | N/A | N/A | N/A | N/A | 196 | N/A
GEN-2018-089 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 196 | 196 | None | None | N/A | N/A | 196 | N/A | N/A | N/A | N/A | N/A | 196 | 196
GEN-2018-089 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 196 | 196 | None | None | N/A | N/A | 196 | N/A | N/A | N/A | N/A | N/A | 196 | 196
GEN-2018-089 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 196 | 196 | None | None | N/A | N/A | N/A | 196 | N/A | N/A | N/A | N/A | N/A | 196
GEN-2018-089 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 196 | 196 | None | None | N/A | N/A | N/A | 196 | N/A | N/A | N/A | N/A | N/A | 196
GEN-2018-099 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2018-099 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2018-099 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 300 | 300 | None | None | 300 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2018-099 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 300 | 300 | None | None | N/A | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 300 | N/A
GEN-2018-099 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2018-099 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 300 | 300 | None | None | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300 | 300
GEN-2018-099 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 300 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300
GEN-2018-099 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 300 | 300 | None | None | N/A | N/A | N/A | 300 | N/A | N/A | N/A | N/A | N/A | 300
GEN-2019-003 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-003 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-003 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2019-003 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2019-003 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2019-003 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2019-003 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-003 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2019-011 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 207 | 207 | None | None | 207 | N/A | N/A | 207 | 207 | N/A | N/A | 207 | 207 | 207
GEN-2019-011 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 207 | 207 | None | None | N/A | 207 | N/A | 207 | N/A | 207 | N/A | 207 | 207 | 207
GEN-2019-011 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 207 | 207 | None | None | 207 | N/A | N/A | N/A | 207 | N/A | N/A | N/A | 207 | N/A
GEN-2019-011 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 207 | 207 | None | None | N/A | 207 | N/A | N/A | N/A | 207 | N/A | N/A | 207 | N/A
GEN-2019-011 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 207 | 207 | None | None | 207 | N/A | N/A | 207 | 207 | N/A | N/A | 207 | 207 | 207
GEN-2019-011 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 207 | 207 | None | None | N/A | 207 | N/A | 207 | N/A | 207 | N/A | 207 | 207 | 207
GEN-2019-011 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 207 | 207 | None | None | N/A | N/A | N/A | 207 | N/A | N/A | N/A | 207 | N/A | 207
GEN-2019-011 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 207 | 207 | None | None | N/A | N/A | N/A | 207 | N/A | N/A | N/A | 207 | N/A | 207
GEN-2019-021 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2019-021 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2019-021 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A
GEN-2019-021 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | N/A | N/A | 50 | N/A | N/A | 50 | N/A
GEN-2019-021 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 50 | 50 | None | None | 50 | N/A | N/A | 50 | 50 | N/A | N/A | 50 | 50 | 50
GEN-2019-021 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 50 | 50 | None | None | N/A | 50 | N/A | 50 | N/A | 50 | N/A | 50 | 50 | 50
GEN-2019-021 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50
GEN-2019-021 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 50 | 50 | None | None | N/A | N/A | N/A | 50 | N/A | N/A | N/A | 50 | N/A | 50

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | 2024ITP | NRIS | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV | 170000/170003/170006 | Belfield - Maurine - Underwood - Laramie River 345 kV New Line | BEPC/WAPA | 60 | 1114609566
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2024ITP | NRIS | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV | 170000/170003/170006 | Belfield - Maurine - Underwood - Laramie River 345 kV New Line | BEPC/WAPA | 60 | 1114609566
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | East Fork 345/115 kV Substation | 144171 | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | BEPC | 2024-11-30 | 18251841
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Kummer Ridge - Round Up 345 kV | 143588 | Build 33.2 mile new 345 kV line from Kummer Ridge to Round Up | BEPC | 2025-04-01 | 83665874
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Leland Olds - Finstad - 345 kV New Line | 144236 | Build a 123 mile 345 kV line from Leland Olds to Finstad. | BEPC | 2026-11-30 | 215340373
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Finstad - Tande 345 kV New Line | 143714 | Build a 48 mile 345 kV line from Finstad to Tande. | BEPC | 2026-11-30 | 76991281
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Finstad 345 kV New Substation | 144230 | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | BEPC | 2026-11-30 | 18932308
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Siouxland 69kV GEN-2019-019 Interconnection (Non-shared NU) (NIPCO) | 143690 | Facilitate the interconnection of GEN-2019-019 | NIPCO | 12 | 1167956
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Siouxland 69kV GEN-2019-019 Interconnection (TOIF) (NIPCO) | 143689 | Facilitate the interconnection of GEN-2019-019 | NIPCO | 12 | 1176290
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Strandahl 115kV GEN-2018-067 Interconnection (Non-shared NU) (MWEC) | 156804 | Facilitate the interconnection of GEN-2018-067 | MWE | 18 | 2343530
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Strandahl 115kV GEN-2018-067 Interconnection (TOIF) (MWEC) | 156803 | Facilitate the interconnection of GEN-2018-067 | MWE | 0 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | WAPA-UGP Mingusville 230kV GEN-2018-069 Interconnection (TOIF) (WAPA) | 156826 | Facilitate the interconnection of GEN-2018-069 | WAPA | 60 | 330000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | WAPA-UGP Mingusville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156828 | Facilitate the interconnection of GEN-2018-069, GEN-2019-023 | WAPA | 60 | 3275000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Denison 230kV GEN-2018-074 Interconnection (Non-shared NU) (WAPA) | 156696 | Facilitate the interconnection of GEN-2018-074. *$0 cost contingent upon the successful interconnection of GEN-2017-222 | WAPA | 60 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Denison 230kV GEN-2018-074 Interconnection (TOIF) (WAPA) | 156695 | Facilitate the interconnection of GEN-2018-074 | WAPA | 1 | 150000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | WAPA-UGP Mingusville 230kV GEN-2019-023 Interconnection (TOIF) (WAPA) | 156827 | Facilitate the interconnection of GEN-2019-023 | WAPA | 60 | 150000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Leland Olds 345kV GEN-2019-037 Interconnection (Non-shared NU) (BEPC) | 156675 | Facilitate the interconnection of GEN-2019-037 | BEPC | 60 | 5916489
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Leland Olds 345kV GEN-2019-037 Interconnection (TOIF) (BEPC) | 156674 | Facilitate the interconnection of GEN-2019-037 | BEPC | 60 | 3066936
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Leland Olds 345 kV Substation | 144237 | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | BEPC | 2026-11-30 | 9338355
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | NE Williston - Folvag 115 kV New Line | 144177 | Build a new 4.5 mile 115 kV line from NE Williston to Folvag. | MWE | 2024-11-01 | 8700000
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits | 170495 | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits | NIPCO | 16 | 2800000
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Rebuild the circuit from K338 to the new 69 kV tap station | 170496 | Rebuild the K338WTCT-NI8 to NEWTAP 69 kV line 1 (3.98 miles) to a minimum rating of 79 MVA | NIPCO | 10 | 1101600
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Rebuild the circuit from WAPA Denison to the new 69 kV tap station | 170498, 170499 | Rebuild the DENISON8 to NEWTAP 69 kV line 1 (0.82 miles) to a minimum rating of 135 MVA | CBPC | 12 | 1580500
Contingent | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2017-002 | ERIS | WAPA DENISON8 69 kV Terminal Upgrade | 143686 | Upgrade the WAPA DENISON8 69 kV Terminal Upgrade to a minimum rating of 125 MVA | WAPA | 36 | 135000
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State/Stability | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Build Strandahl to Black Tail 115 kV line | 170494 | Build a new STRNDAHL-MW7 to BLKTLTAP-MW7 115 kV line 1 (15 miles) to a minimum rating of 239 MVA | MWE | 36 | 14662500
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line | 170497 | Rebuild the K335AMAI-NI8 to K338WTCT-NI8 69 kV line 1 (0.33 miles) to a minimum rating of 79 MVA | NIPCO | 11 | 136800
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1 | 170620 | Rebuild the existing DENISON8 to J6BOYER_-NI8 69 kV line 1 (0.69 miles) to a minimum emergency rating of 125 MVA | NIPCO | 14 | 2073600
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Rebuild the K335AMAI-NI8 to J6BOYER_-NI8 69kV Line 1 | 170492 | Rebuild the existing K335AMAI-NI8 to J6BOYER_-NI8 69 kV line 1 (0.69 miles) to a minimum rating of 70 MVA | NIPCO | 12 | 463200
Contingent | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | 2024ITP | NRIS | NewBranch Dawsonc4 to Wiliston 230 kV | 170512 | Dawson County - Williston 230 kV Ckt 1 New Line | WAPA | 2030-09-01 | 157802000
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | NRIS | NewBranch Dawsonc4 to Wiliston 230 kV | 170512 | Dawson County - Williston 230 kV Ckt 1 New Line | WAPA | TBD | 157802000
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | East Fork 345/115 kV Transformer | 144198 | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | BEPC | 2024-11-30 | 6394630
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Finstad Switched Shunt | 144231 | Install a switched shunt at Finstad. | BEPC | 2026-11-30 | 404512.6881
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Folvag 115 kV Terminal Equipment | 144163 | Install terminal equipment at Folvag 115 kV sub to accommodate new 115 kV line from NE Williston 115 kV sub. | MWE | 2024-11-01 | 500000
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Kummer Ridge 345 kV Terminal Upgrades | 143589 | Install terminal equipment at Kummer Ridge substation 345 kV to support a new 345 kV line from Round Up | BEPC | 2025-03-01 | 342000
Contingent | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | 2020 ITP | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | 122848, 122849, 122858, 133085, 133106, 143176, 143257 | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | OKGE | 2025-01-01 | 128763342
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 04 SOUTHEAST | 2020 ITP | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | 122848, 122849, 122858, 133085, 133106, 143176, 143257 | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | OKGE | 2025-01-01 | 128763342
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | NE Williston 115 kV Terminal Equipment | 144178 | Install terminal equipment at NE Williston 115 kV sub to accommodate new 115 kV line from Folvag 115 kV sub. | MWE | 2024-12-31 | 500000
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2021 ITP | ERIS | Round Up 345 kV Terminal Upgrades | 143590 | Install terminal equipment at Round Up substation 345 kV to support a new 345 kV line from Kummer Ridge | BEPC | 2025-03-01 | 342000
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 01 NORTH | DISIS-2018-002 / DISIS-2019-001 | ERIS | Rebuild Mont to STRNDAHL Line_115kV | 170493 | Rebuild the existing MONT -MW7 to STRNDAHL-MW7 115 kV line 1 (11.97 miles) to a minimum rating of 220 MVA | MWE | 36 | 15710000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Pierce County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156668 | Facilitate the interconnection of GEN-2018-131, GEN-2018-132 | NPPD | 60 | 34300000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Madison 345kv GEN2018-083 Interconnection (TOIF) (NPPD) | 156792 | Facilitate the interconnection of GEN-2018-083 | NPPD | 60 | 250000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Gentleman to Sweetwater 345kV GEN-2018-125 Interconnection (Non-shared NU) (NPPD) | 156709 | Facilitate the interconnection of GEN-2018-125 | NPPD | 60 | 36000000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Gentleman to Sweetwater 345kV GEN-2018-125 Interconnection (TOIF) (NPPD) | 156708 | Facilitate the interconnection of GEN-2018-125 | NPPD | 60 | 1000000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Pierce County 345kV GEN-2018-131 Interconnection (TOIF) (NPPD) | 156669 | Facilitate the interconnection of GEN-2018-131 | NPPD | 60 | 500000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Pierce County 345kV GEN-2018-132 Interconnection (TOIF) (NPPD) | 156670 | Facilitate the interconnection of GEN-2018-132 | NPPD | 60 | 500000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | S1263 Brock 161kV GEN-2019-009 Interconnection (Non-shared NU) (OPPD) | 156781 | Facilitate the interconnection of GEN-2019-009 | OPPD | 48 | 3535000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | S1263 Brock 161kV GEN-2019-009 Interconnection (TOIF) (OPPD) | 156780 | Facilitate the interconnection of GEN-2019-009 | OPPD | 30 | 5335644
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Columbus Southeast - Rising City 115kV GEN-2019-039 Interconnection (Non-shared NU) (NPPD) | 156685 | Facilitate the interconnection of GEN-2019-039 | NPPD | 36 | 7100000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Columbus Southeast - Rising City 115kV GEN-2019-039 Interconnection (TOIF) (NPPD) | 156684 | Facilitate the interconnection of GEN-2019-039 | NPPD | 36 | 700000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Monolith 115kV GEN-2019-041 Interconnection (Non-shared NU) (NPPD) | 156747 | Facilitate the interconnection of GEN-2019-041 | NPPD | 36 | 1500000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Monolith 115kV GEN-2019-041 Interconnection (TOIF) (NPPD) | 156746 | Facilitate the interconnection of GEN-2019-041 | NPPD | 36 | 700000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Madison 345kv GEN-2019-069 Interconnection (TOIF) (NPPD) | 156789 | Facilitate the interconnection of GEN-2019-069 | NPPD | 60 | 250000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Madison 345kv Interconnection (DISIS-2018-002 - DISIS-2019-001) | 156793 | Facilitate the interconnection of GEN-2018-083, GEN-2019-069, GEN-2019-070, GEN-2019-073 | NPPD | 60 | 34100000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Madison 345kv GEN-2019-070 Interconnection (TOIF) (NPPD) | 156790 | Facilitate the interconnection of GEN-2019-070 | NPPD | 60 | 250000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Madison 345kv GEN-2019-073 Interconnection (TOIF) (NPPD) | 156791 | Facilitate the interconnection of GEN-2019-073 | NPPD | 60 | 250000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thistle 345kV GEN-2018-108 Interconnection (Non-shared NU) (ITCGP) | 156813 | Sharing a GEN Tie line with GEN-2018-049 | ITCGP | 0 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thistle 345kV GEN-2018-108 Interconnection (TOIF) (ITCGP) | 156812 | Sharing a GEN Tie line with GEN-2018-049 | ITCGP | 0 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Renfrow-Viola 345 kV GEN-2018-128 Interconnection (Non-shared NU) (WERE) | 156776 | Facilitate the interconnection of GEN-2018-128 | WERE | 56 | 29100153
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Renfrow-Viola 345 kV GEN-2018-128 Interconnection (TOIF) (WERE) | 156775 | Facilitate the interconnection of GEN-2018-128 | WERE | 48 | 1861878
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Buffalo Flats 345kV GEN-2019-001 Interconnection (Non-shared NU) (WERE) | 156815 | Facilitate the interconnection of GEN-2019-001 | WERE | 12 | 112911
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Buffalo Flats 345kV GEN-2019-001 Interconnection (TOIF) (WERE) | 156814 | Facilitate the interconnection of GEN-2019-001 | WERE | 12 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Dadeville 161kV GEN-2019-016 Interconnection (Non-shared NU) (EDE) | 156689 | Facilitate the interconnection of GEN-2019-016 | EDE | 36 | 13073621
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Dadeville 161kV GEN-2019-016 Interconnection (TOIF) (EDE) | 156688 | Facilitate the interconnection of GEN-2019-016 | EDE | 36 | 2238582
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Saxman 115kV Substation GEN-2019-018 Interconnection (Non-shared NU) (MIDW) | 156786 | Facilitate the interconnection of GEN-2019-018 | MIDW | 0 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Saxman 115kV Substation GEN-2019-018 Interconnection (TOIF) (MIDW) | 156785 | Facilitate the interconnection of GEN-2019-018 | MIDW | 0 | 898528
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Spearville to Clark County 345 kV GEN-2019-030 Interconnection (Non-shared NU) (ITCGP) | 156802 | Facilitate the interconnection of GEN-2019-030 | ITCGP | 24 | 17822414
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Spearville to Clark County 345 kV GEN-2019-030 Interconnection (TOIF) (ITCGP) | 156801 | Facilitate the interconnection of GEN-2019-030 | ITCGP | 24 | 1268386
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | North Fort Dodge 115kV GEN-2019-044 Interconnection (Non-shared NU) (SUNC) | 156751 | Facilitate the interconnection of GEN-2019-044 | SUNC | 36 | 6361713
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | North Fort Dodge 115kV GEN-2019-044 Interconnection (TOIF) (SUNC) | 156750 | Facilitate the interconnection of GEN-2019-044 | SUNC | 36 | 297327
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Great Bend - Spearville 230kV GEN-2019-053 Interconnection (TOIF) (SUNC) | 156719 | Facilitate the interconnection of GEN-2019-053 | SUNC | 40 | 795429
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Great Bend - Spearville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156721 | Facilitate the interconnection of GEN-2019-053, GEN-2019-055 | SUNC | 40 | 14722419
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Great Bend - Circle 230kV GEN-2019-054 Interconnection (TOIF) (SUNC) | 156717 | Facilitate the interconnection of GEN-2019-054 | SUNC | 40 | 802997
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Great Bend - Circle 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156718 | Facilitate the interconnection of GEN-2019-054, GEN-2019-068 | SUNC | 40 | 13617457
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Great Bend - Spearville 230kV GEN-2019-055 Interconnection (TOIF) (SUNC) | 156720 | Facilitate the interconnection of GEN-2019-055 | SUNC | 40 | 795429
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Clark County 345kV GEN-2019-058 Interconnection (TOIF) (ITCGP) | 156681 | Facilitate the interconnection of GEN-2019-058 | ITCGP | 24 | 634193
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Clark County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156683 | Facilitate the interconnection of GEN-2019-058, GEN-2019-063 | ITCGP | 36 | 2050964
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Clark County 345kV GEN-2019-063 Interconnection (TOIF) (ITCGP) | 156682 | Facilitate the interconnection of GEN-2019-063 | ITCGP | 24 | 634193
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Great Bend - Circle 230kV GEN-2019-068 Interconnection (TOIF) (SUNC) | 156716 | Facilitate the interconnection of GEN-2019-068 | SUNC | 40 | 802997
Contingent | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | 2024ITP | ERIS | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | 170229 | Build a new HOLT.CO3 to ANTELOPE 3 345 kV line 1 (24 miles) to a standard rating of 1792 MVA | NPPD | TBD | 89100000
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | 170507 | Build a new HOSKINS3 to HOSKINS4 345-230 kV transformer 2 with a rating of 336 MVA | NPPD | TBD | 45400000
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Rebuild Columbus SE to G19-039-TAP 115 kV | 158601 | Rebuild the existing COL.SE 7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | NPPD | TBD | 4000000
Current Study | DISIS-2018-002 / DISIS-2019-001 | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | ERIS | Rebuild Rising to G19-039-TAP 115 kV | 158603 | Rebuild the existing RISNGCY7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | NPPD | TBD | 5500000
Contingent | DISIS-2018-002 / DISIS-2019-001 | Steady State | 03 CENTRAL | Tranmission Owner Internal Project | ERIS | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade | 158590 | Rebuild the existing CUDAHY 3 to CRKCK 3 115 kV line 1 (9.53 miles) to a standard rating of 135 MVA | SUNC | 36 | 250000
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 02 NEBRASKA | 2021 ITP | ERIS | Columbus East 230/115 kV transformer | 122739 | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | NPPD | 2025-06-01 | 9278651
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 01 NORTH | 2022 ITP | NRIS | Fargo 230 kV Terminal Upgrade | 156282 | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | XEL | 2025-12-31 | 92778
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Farmland - Delaware 138kV GEN-2018-079 Interconnection (TOIF) (AEP) | 156699 | Facilitate the interconnection of GEN-2018-079 | AEPW | 36 | 2087843
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Farmland - Delaware 138kV GEN-2018-079 Interconnection (Non-shared NU) (AEP) | 156700 | Facilitate the interconnection of GEN-2018-079 | AEPW | 36 | 10268478
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Lawton East Side 345kV/138kv GEN-2018-115 Interconnection (TOIF) (AEP) | 156737 | Facilitate the interconnection of GEN-2018-115 | AEPW | 36 | 3377626
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Lawton East Side 345kV/138kv GEN-2018-115 Interconnection (Non-shared NU) (AEP) | 156738 | Facilitate the interconnection of GEN-2018-115 | AEPW | 36 | 5289807
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Longwood 345kV GEN-2018-106 Interconnection (TOIF) (AEP) | 156739 | Facilitate the interconnection of GEN-2018-106 | AEPW | 18 | 246888
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Longwood 345kV GEN-2018-106 Interconnection (Non-shared NU) (AEP) | 156740 | Facilitate the interconnection of GEN-2018-106 | AEPW | 24 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Overton-Northwest Henderson 138kV GEN-2019-065 Interconnection (TOIF) (AEP) | 156757 | Facilitate the interconnection of GEN-2019-065 | AEPW | 36 | 2144327
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Overton-Northwest Henderson 138kV GEN-2019-065 Interconnection (Non-shared NU) (AEP) | 156758 | Facilitate the interconnection of GEN-2019-065 | AEPW | 36 | 12232419
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Pittsburg 345kV GEN-2018-082 Interconnection (TOIF) (AEP) | 156759 | Facilitate the interconnection of GEN-2018-082 | AEPW | 36 | 3485947
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Pittsburg 345kV GEN-2018-082 Interconnection (Non-shared NU) (AEP) | 156760 | Facilitate the interconnection of GEN-2018-082 | AEPW | 36 | 6227138
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Maid 161kV GEN-2019-002 Interconnection (Non-shared NU) (GRDA) | 156745 | Facilitate the interconnection of GEN-2019-002 | GRDA | 18 | 962021
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Maid 161kV GEN-2019-002 Interconnection (TOIF) (GRDA) | 156744 | Facilitate the interconnection of GEN-2019-002 | GRDA | 18 | 1786611
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Tonnece 69kV GEN-2018-064 Interconnection (Non-shared NU) (GRDA) | 156823 | Facilitate the interconnection of GEN-2018-064 | GRDA | 0 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Tonnece 69kV GEN-2018-064 Interconnection (TOIF) (GRDA) | 156822 | Facilitate the interconnection of GEN-2018-064 | GRDA | 18 | 485120
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | DeGrasse 138kV GEN-2019-045 Interconnection (TOIF) (OGE) | 156690 | Facilitate the interconnection of GEN-2019-045 | OKGE | 36 | 1875903
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | DeGrasse 138kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156692 | Facilitate the interconnection of GEN-2019-045 | OKGE | 36 | 1637992
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Ranch Road 345 kV GEN-2018-071 Interconnection (TOIF) (OGE) | 156766 | Facilitate the interconnection of GEN-2018-071 | OKGE | 0 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Ranch Road 345 kV GEN-2018-072 Interconnection (TOIF) (OGE) | 156767 | Facilitate the interconnection of GEN-2018-072 | OKGE | 0 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Ranch Road 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156768 | Facilitate the interconnection of GEN-2018-071, GEN-2018-072 | OKGE | 9 | 60000
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Woodward 345kV GEN-2019-012 Interconnection (Non-shared NU) (OGE) | 156830 | Facilitate the interconnection of GEN-2019-012 | OKGE | 36 | 1969493
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Woodward 345kV GEN-2019-012 Interconnection (TOIF) (OGE) | 156829 | Facilitate the interconnection of GEN-2019-012 | OKGE | 36 | 1671237
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Newhart 230kV GEN-2018-089 Interconnection (Non-shared NU) (SPS) | 156749 | Facilitate the interconnection of GEN-2018-089 | SPS | 36 | 2783494
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Newhart 230kV GEN-2018-089 Interconnection (TOIF) (SPS) | 156748 | Facilitate the interconnection of GEN-2018-089 | SPS | 36 | 2326075
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Roosevelt 230kV GEN-2019-003 Interconnection (TOIF) (SPS) | 156777 | Facilitate the interconnection of GEN-2019-003 | SPS | 36 | 1326193
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Roosevelt 230kV GEN-2019-021 Interconnection (TOIF) (SPS) | 156778 | Facilitate the interconnection of GEN-2019-021 | SPS | 36 | 1326193
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Roosevelt 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156779 | Facilitate the interconnection of GEN-2019-003, GEN-2019-021 | SPS | 36 | 5408411
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Tolk 230kV GEN-2018-099 Interconnection (TOIF) (SPS) | 156817 | Sharing a GEN Tie line with GEN-2017-158 | SPS | 0 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Tolk 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156821 | Facilitate the interconnection of GEN-2018-099 | SPS | 42 | 0
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Yoakum 345kV GEN-2019-011 Interconnection (Non-shared NU) (SPS) | 156832 | Facilitate the interconnection of GEN-2019-011 | SPS | 42 | 8033023
Interconnection | DISIS-2018-002 / DISIS-2019-001 | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Yoakum 345kV GEN-2019-011 Interconnection (TOIF) (SPS) | 156831 | Facilitate the interconnection of GEN-2019-011 | SPS | 42 | 2675954
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | NRIS | Rebuild Columbus SE to G19-039-TAP 115 kV | 158601 | Rebuild the existing COL.SE 7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | NPPD | TBD | 4000000
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | NRIS | Rebuild Rising to G19-039-TAP 115 kV | 158603 | Rebuild the existing RISNGCY7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | NPPD | TBD | 5500000
Contingent | DISIS-2018-002 / DISIS-2019-001 CF | Steady State | 02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | NRIS | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | 170229 | Build a new HOLT.CO3 to ANTELOPE 3 345 kV line 1 (24 miles) to a standard rating of 1792 MVA | NPPD | TBD | 89100000
3864364248.6881

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2018-064 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156823 | ERIS | Tonnece 69kV GEN-2018-064 Interconnection (Non-shared NU) (GRDA) | Interconnection | Facilitate the interconnection of GEN-2018-064 | 0 | 100% | 0 | 1
GEN-2018-064 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156822 | ERIS | Tonnece 69kV GEN-2018-064 Interconnection (TOIF) (GRDA) | Interconnection | Facilitate the interconnection of GEN-2018-064 | 485120 | 100% | 485120 | 1
GEN-2018-067 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170494 | ERIS | Build Strandahl to Black Tail 115 kV line | Current Study | Build a new STRNDAHL-MW7 to BLKTLTAP-MW7 115 kV line 1 (15 miles) to a minimum rating of 239 MVA | 14662500 | 100% | 14662500 | 0.38539
GEN-2018-067 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170493 | ERIS | Rebuild Mont to STRNDAHL Line_115kV | Current Study | Rebuild the existing MONT -MW7 to STRNDAHL-MW7 115 kV line 1 (11.97 miles) to a minimum rating of 220 MVA | 15710000 | 100% | 15710000 | 0.51918
GEN-2018-067 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156804 | ERIS | Strandahl 115kV GEN-2018-067 Interconnection (Non-shared NU) (MWEC) | Interconnection | Facilitate the interconnection of GEN-2018-067 | 2343530 | 100% | 2343530 | 1
GEN-2018-067 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156803 | ERIS | Strandahl 115kV GEN-2018-067 Interconnection (TOIF) (MWEC) | Interconnection | Facilitate the interconnection of GEN-2018-067 | 0 | 100% | 0 | 1
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156826 | ERIS | WAPA-UGP Mingusville 230kV GEN-2018-069 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-069 | 330000 | 100% | 330000 | 1
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156828 | ERIS | WAPA-UGP Mingusville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-069, GEN-2019-023 | 1742021.2766 | 53.19% | 3275000 | 1
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144171 | ERIS | East Fork 345/115 kV Substation | Contingent | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 0 |  | 18251841
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144198 | ERIS | East Fork 345/115 kV Transformer | Contingent | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 0 |  | 6394630
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 156282 | NRIS | Fargo 230 kV Terminal Upgrade | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 0 |  | 92778
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 143714 | ERIS | Finstad - Tande 345 kV New Line | Contingent | Build a 48 mile 345 kV line from Finstad to Tande. | 0 |  | 76991281
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144230 | ERIS | Finstad 345 kV New Substation | Contingent | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 0 |  | 18932308
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144231 | ERIS | Finstad Switched Shunt | Contingent | Install a switched shunt at Finstad. | 0 |  | 404512.6881
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144163 | ERIS | Folvag 115 kV Terminal Equipment | Contingent | Install terminal equipment at Folvag 115 kV sub to accommodate new 115 kV line from NE Williston 115 kV sub. | 0 |  | 500000
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 143588 | ERIS | Kummer Ridge - Round Up 345 kV | Contingent | Build 33.2 mile new 345 kV line from Kummer Ridge to Round Up | 0 |  | 83665874
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 143589 | ERIS | Kummer Ridge 345 kV Terminal Upgrades | Contingent | Install terminal equipment at Kummer Ridge substation 345 kV to support a new 345 kV line from Round Up | 0 |  | 342000
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144236 | ERIS | Leland Olds - Finstad - 345 kV New Line | Contingent | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 0 |  | 215340373
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144237 | ERIS | Leland Olds 345 kV Substation | Contingent | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 0 |  | 9338355
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144177 | ERIS | NE Williston - Folvag 115 kV New Line | Contingent | Build a new 4.5 mile 115 kV line from NE Williston to Folvag. | 0 |  | 8700000
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144178 | ERIS | NE Williston 115 kV Terminal Equipment | Contingent | Install terminal equipment at NE Williston 115 kV sub to accommodate new 115 kV line from Folvag 115 kV sub. | 0 |  | 500000
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170512 | NRIS | NewBranch Dawsonc4 to Wiliston 230 kV | Contingent | Dawson County - Williston 230 kV Ckt 1 New Line | 0 | 43.86% | 157802000 | 0.35184
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 170512 | NRIS | NewBranch Dawsonc4 to Wiliston 230 kV | Contingent | Dawson County - Williston 230 kV Ckt 1 New Line | 0 |  | 157802000
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170000/170003/170006 | NRIS | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV | Contingent | Belfield - Maurine - Underwood - Laramie River 345 kV New Line | 0 | 43.24% | 1114609566 | 0.14577
GEN-2018-069 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 143590 | ERIS | Round Up 345 kV Terminal Upgrades | Contingent | Install terminal equipment at Round Up substation 345 kV to support a new 345 kV line from Kummer Ridge | 0 |  | 342000
GEN-2018-071 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156766 | ERIS | Ranch Road 345 kV GEN-2018-071 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-071 | 0 | 100% | 0 | 1
GEN-2018-071 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156768 | ERIS | Ranch Road 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-071, GEN-2018-072 | 30000 | 50% | 60000 | 1
GEN-2018-071 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 122848, 122849, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 | 20.69% | 128763342 | 0.02999
GEN-2018-071 | DISIS-2018-002 / DISIS-2019-001 CF | 04 SOUTHEAST | 122848, 122849, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 |  | 128763342
GEN-2018-072 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156767 | ERIS | Ranch Road 345 kV GEN-2018-072 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-072 | 0 | 100% | 0 | 1
GEN-2018-072 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156768 | ERIS | Ranch Road 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-071, GEN-2018-072 | 30000 | 50% | 60000 | 1
GEN-2018-072 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 122848, 122849, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 | 20.69% | 128763342 | 0.02999
GEN-2018-072 | DISIS-2018-002 / DISIS-2019-001 CF | 04 SOUTHEAST | 122848, 122849, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 |  | 128763342
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170495 | ERIS | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits | Current Study | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits | 2800000 | 100% | 2800000 | 0.11083
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156696 | ERIS | Denison 230kV GEN-2018-074 Interconnection (Non-shared NU) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-074. *$0 cost contingent upon the successful interconnection of GEN-2017-222 | 0 | 100% | 0 | 1
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156695 | ERIS | Denison 230kV GEN-2018-074 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-074 | 150000 | 100% | 150000 | 1
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170496 | ERIS | Rebuild the circuit from K338 to the new 69 kV tap station | Current Study | Rebuild the K338WTCT-NI8 to NEWTAP 69 kV line 1 (3.98 miles) to a minimum rating of 79 MVA | 1101600 | 100% | 1101600 | 0.06257
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170498, 170499 | ERIS | Rebuild the circuit from WAPA Denison to the new 69 kV tap station | Current Study | Rebuild the DENISON8 to NEWTAP 69 kV line 1 (0.82 miles) to a minimum rating of 135 MVA | 1580500 | 100% | 1580500 | 0.11083
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170620 | ERIS | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1 | Current Study | Rebuild the existing DENISON8 to J6BOYER_-NI8 69 kV line 1 (0.69 miles) to a minimum emergency rating of 125 MVA | 2073600 | 100% | 2073600 | 0.05464
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170497 | ERIS | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line | Current Study | Rebuild the K335AMAI-NI8 to K338WTCT-NI8 69 kV line 1 (0.33 miles) to a minimum rating of 79 MVA | 136800 | 100% | 136800 | 0.05464
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170492 | ERIS | Rebuild the K335AMAI-NI8 to J6BOYER_-NI8 69kV Line 1 | Current Study | Rebuild the existing K335AMAI-NI8 to J6BOYER_-NI8 69 kV line 1 (0.69 miles) to a minimum rating of 70 MVA | 463200 | 100% | 463200 | 0.05464
GEN-2018-074 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 143686 | ERIS | WAPA DENISON8 69 kV Terminal Upgrade | Contingent | Upgrade the WAPA DENISON8 69 kV Terminal Upgrade to a minimum rating of 125 MVA | 0 | 100% | 135000 | 0.05464
GEN-2018-079 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156700 | ERIS | Farmland - Delaware 138kV GEN-2018-079 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-079 | 10268478 | 100% | 10268478 | 1
GEN-2018-079 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156699 | ERIS | Farmland - Delaware 138kV GEN-2018-079 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-079 | 2087843 | 100% | 2087843 | 1
GEN-2018-082 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156760 | ERIS | Pittsburg 345kV GEN-2018-082 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-082 | 6227138 | 100% | 6227138 | 1
GEN-2018-082 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156759 | ERIS | Pittsburg 345kV GEN-2018-082 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-082 | 3485947 | 100% | 3485947 | 1
GEN-2018-083 | DISIS-2018-002 / DISIS-2019-001 CF | 02 NEBRASKA | 122739 | ERIS | Columbus East 230/115 kV transformer | Contingent | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | 0 |  | 9278651
GEN-2018-083 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 170507 | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a new HOSKINS3 to HOSKINS4 345-230 kV transformer 2 with a rating of 336 MVA | 12680866.0949 | 27.93% | 45400000 | 0.03998
GEN-2018-083 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156792 | ERIS | Madison 345kv GEN2018-083 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-083 | 250000 | 100% | 250000 | 1
GEN-2018-083 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156793 | ERIS | Madison 345kv Interconnection (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-083, GEN-2019-069, GEN-2019-070, GEN-2019-073 | 17050000 | 50% | 34100000 | 1
GEN-2018-089 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156749 | ERIS | Newhart 230kV GEN-2018-089 Interconnection (Non-shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-089 | 2783494 | 100% | 2783494 | 1
GEN-2018-089 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156748 | ERIS | Newhart 230kV GEN-2018-089 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-089 | 2326075 | 100% | 2326075 | 1
GEN-2018-099 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156817 | ERIS | Tolk 230kV GEN-2018-099 Interconnection (TOIF) (SPS) | Interconnection | Sharing a GEN Tie line with GEN-2017-158 | 0 | 100% | 0 | 1
GEN-2018-099 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156821 | ERIS | Tolk 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-099 | 0 | 100% | 0 | 1
GEN-2018-106 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156740 | ERIS | Longwood 345kV GEN-2018-106 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-106 | 0 | 100% | 0 | 1
GEN-2018-106 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156739 | ERIS | Longwood 345kV GEN-2018-106 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-106 | 246888 | 100% | 246888 | 1
GEN-2018-108 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156813 | ERIS | Thistle 345kV GEN-2018-108 Interconnection (Non-shared NU) (ITCGP) | Interconnection | Sharing a GEN Tie line with GEN-2018-049 | 0 | 100% | 0 | 1
GEN-2018-108 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156812 | ERIS | Thistle 345kV GEN-2018-108 Interconnection (TOIF) (ITCGP) | Interconnection | Sharing a GEN Tie line with GEN-2018-049 | 0 | 100% | 0 | 1
GEN-2018-115 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156738 | ERIS | Lawton East Side 345kV/138kv GEN-2018-115 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-115 | 5289807 | 100% | 5289807 | 1
GEN-2018-115 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156737 | ERIS | Lawton East Side 345kV/138kv GEN-2018-115 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-115 | 3377626 | 100% | 3377626 | 1
GEN-2018-125 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156709 | ERIS | Gentleman to Sweetwater 345kV GEN-2018-125 Interconnection (Non-shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-125 | 36000000 | 100% | 36000000 | 1
GEN-2018-125 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156708 | ERIS | Gentleman to Sweetwater 345kV GEN-2018-125 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-125 | 1000000 | 100% | 1000000 | 1
GEN-2018-128 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156776 | ERIS | Renfrow-Viola 345 kV GEN-2018-128 Interconnection (Non-shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2018-128 | 29100153 | 100% | 29100153 | 1
GEN-2018-128 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156775 | ERIS | Renfrow-Viola 345 kV GEN-2018-128 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2018-128 | 1861878 | 100% | 1861878 | 1
GEN-2018-131 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 170229 | ERIS | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | Contingent | Build a new HOLT.CO3 to ANTELOPE 3 345 kV line 1 (24 miles) to a standard rating of 1792 MVA | 0 |  | 89100000
GEN-2018-131 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156669 | ERIS | Pierce County 345kV GEN-2018-131 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-131 | 500000 | 100% | 500000 | 1
GEN-2018-131 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156668 | ERIS | Pierce County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-131, GEN-2018-132 | 17952765.9574 | 52.34% | 34300000 | 1
GEN-2018-131 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 170507 | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a new HOSKINS3 to HOSKINS4 345-230 kV transformer 2 with a rating of 336 MVA | 10418388.9759 | 22.95% | 45400000 | 0.03709
GEN-2018-132 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 170229 | ERIS | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | Contingent | Build a new HOLT.CO3 to ANTELOPE 3 345 kV line 1 (24 miles) to a standard rating of 1792 MVA | 0 |  | 89100000
GEN-2018-132 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156670 | ERIS | Pierce County 345kV GEN-2018-132 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-132 | 500000 | 100% | 500000 | 1
GEN-2018-132 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156668 | ERIS | Pierce County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-131, GEN-2018-132 | 16347234.0426 | 47.66% | 34300000 | 1
GEN-2018-132 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 170507 | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a new HOSKINS3 to HOSKINS4 345-230 kV transformer 2 with a rating of 336 MVA | 9486663.1325 | 20.9% | 45400000 | 0.03709
GEN-2019-001 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156815 | ERIS | Buffalo Flats 345kV GEN-2019-001 Interconnection (Non-shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2019-001 | 112911 | 100% | 112911 | 1
GEN-2019-001 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156814 | ERIS | Buffalo Flats 345kV GEN-2019-001 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2019-001 | 0 | 100% | 0 | 1
GEN-2019-002 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156745 | ERIS | Maid 161kV GEN-2019-002 Interconnection (Non-shared NU) (GRDA) | Interconnection | Facilitate the interconnection of GEN-2019-002 | 962021 | 100% | 962021 | 1
GEN-2019-002 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156744 | ERIS | Maid 161kV GEN-2019-002 Interconnection (TOIF) (GRDA) | Interconnection | Facilitate the interconnection of GEN-2019-002 | 1786611 | 100% | 1786611 | 1
GEN-2019-003 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156777 | ERIS | Roosevelt 230kV GEN-2019-003 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-003 | 1326193 | 100% | 1326193 | 1
GEN-2019-003 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156779 | ERIS | Roosevelt 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-003, GEN-2019-021 | 4056308.25 | 75% | 5408411 | 1
GEN-2019-009 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156781 | ERIS | S1263 Brock 161kV GEN-2019-009 Interconnection (Non-shared NU) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2019-009 | 3535000 | 100% | 3535000 | 1
GEN-2019-009 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156780 | ERIS | S1263 Brock 161kV GEN-2019-009 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2019-009 | 5335644 | 100% | 5335644 | 1
GEN-2019-011 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156832 | ERIS | Yoakum 345kV GEN-2019-011 Interconnection (Non-shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-011 | 8033023 | 100% | 8033023 | 1
GEN-2019-011 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156831 | ERIS | Yoakum 345kV GEN-2019-011 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-011 | 2675954 | 100% | 2675954 | 1
GEN-2019-012 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 122848, 122849, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 | 58.62% | 128763342 | 0.06414
GEN-2019-012 | DISIS-2018-002 / DISIS-2019-001 CF | 04 SOUTHEAST | 122848, 122849, 122858, 133085, 133106, 143176, 143257 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 0 |  | 128763342
GEN-2019-012 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156830 | ERIS | Woodward 345kV GEN-2019-012 Interconnection (Non-shared NU) (OGE) | Interconnection | Facilitate the interconnection of GEN-2019-012 | 1969493 | 100% | 1969493 | 1
GEN-2019-012 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156829 | ERIS | Woodward 345kV GEN-2019-012 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2019-012 | 1671237 | 100% | 1671237 | 1
GEN-2019-016 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156689 | ERIS | Dadeville 161kV GEN-2019-016 Interconnection (Non-shared NU) (EDE) | Interconnection | Facilitate the interconnection of GEN-2019-016 | 13073621 | 100% | 13073621 | 1
GEN-2019-016 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156688 | ERIS | Dadeville 161kV GEN-2019-016 Interconnection (TOIF) (EDE) | Interconnection | Facilitate the interconnection of GEN-2019-016 | 2238582 | 100% | 2238582 | 1
GEN-2019-018 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156786 | ERIS | Saxman 115kV Substation GEN-2019-018 Interconnection (Non-shared NU) (MIDW) | Interconnection | Facilitate the interconnection of GEN-2019-018 | 0 | 100% | 0 | 1
GEN-2019-018 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156785 | ERIS | Saxman 115kV Substation GEN-2019-018 Interconnection (TOIF) (MIDW) | Interconnection | Facilitate the interconnection of GEN-2019-018 | 898528 | 100% | 898528 | 1
GEN-2019-019 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 143690 | ERIS | Siouxland 69kV GEN-2019-019 Interconnection (Non-shared NU) (NIPCO) | Interconnection | Facilitate the interconnection of GEN-2019-019 | 1167956 | 100% | 1167956 | 1
GEN-2019-019 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 143689 | ERIS | Siouxland 69kV GEN-2019-019 Interconnection (TOIF) (NIPCO) | Interconnection | Facilitate the interconnection of GEN-2019-019 | 1176290 | 100% | 1176290 | 1
GEN-2019-021 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156778 | ERIS | Roosevelt 230kV GEN-2019-021 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-021 | 1326193 | 100% | 1326193 | 1
GEN-2019-021 | DISIS-2018-002 / DISIS-2019-001 | 05 SOUTHWEST | 156779 | ERIS | Roosevelt 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-003, GEN-2019-021 | 1352102.75 | 25% | 5408411 | 1
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144171 | ERIS | East Fork 345/115 kV Substation | Contingent | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 0 |  | 18251841
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144198 | ERIS | East Fork 345/115 kV Transformer | Contingent | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 0 |  | 6394630
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 156282 | NRIS | Fargo 230 kV Terminal Upgrade | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 0 |  | 92778
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 143714 | ERIS | Finstad - Tande 345 kV New Line | Contingent | Build a 48 mile 345 kV line from Finstad to Tande. | 0 |  | 76991281
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144230 | ERIS | Finstad 345 kV New Substation | Contingent | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 0 |  | 18932308
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144231 | ERIS | Finstad Switched Shunt | Contingent | Install a switched shunt at Finstad. | 0 |  | 404512.6881
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144163 | ERIS | Folvag 115 kV Terminal Equipment | Contingent | Install terminal equipment at Folvag 115 kV sub to accommodate new 115 kV line from NE Williston 115 kV sub. | 0 |  | 500000
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 143588 | ERIS | Kummer Ridge - Round Up 345 kV | Contingent | Build 33.2 mile new 345 kV line from Kummer Ridge to Round Up | 0 |  | 83665874
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 143589 | ERIS | Kummer Ridge 345 kV Terminal Upgrades | Contingent | Install terminal equipment at Kummer Ridge substation 345 kV to support a new 345 kV line from Round Up | 0 |  | 342000
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144236 | ERIS | Leland Olds - Finstad - 345 kV New Line | Contingent | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 0 |  | 215340373
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144237 | ERIS | Leland Olds 345 kV Substation | Contingent | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 0 |  | 9338355
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144177 | ERIS | NE Williston - Folvag 115 kV New Line | Contingent | Build a new 4.5 mile 115 kV line from NE Williston to Folvag. | 0 |  | 8700000
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 144178 | ERIS | NE Williston 115 kV Terminal Equipment | Contingent | Install terminal equipment at NE Williston 115 kV sub to accommodate new 115 kV line from Folvag 115 kV sub. | 0 |  | 500000
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170512 | NRIS | NewBranch Dawsonc4 to Wiliston 230 kV | Contingent | Dawson County - Williston 230 kV Ckt 1 New Line | 0 | 56.14% | 157802000 | 0.35184
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 170512 | NRIS | NewBranch Dawsonc4 to Wiliston 230 kV | Contingent | Dawson County - Williston 230 kV Ckt 1 New Line | 0 |  | 157802000
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 170000/170003/170006 | NRIS | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV | Contingent | Belfield - Maurine - Underwood - Laramie River 345 kV New Line | 0 | 56.76% | 1114609566 | 0.14951
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156827 | ERIS | WAPA-UGP Mingusville 230kV GEN-2019-023 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2019-023 | 150000 | 100% | 150000 | 1
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156828 | ERIS | WAPA-UGP Mingusville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-069, GEN-2019-023 | 1532978.7234 | 46.81% | 3275000 | 1
GEN-2019-023 | DISIS-2018-002 / DISIS-2019-001 CF | 01 NORTH | 143590 | ERIS | Round Up 345 kV Terminal Upgrades | Contingent | Install terminal equipment at Round Up substation 345 kV to support a new 345 kV line from Kummer Ridge | 0 |  | 342000
GEN-2019-030 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156802 | ERIS | Spearville to Clark County 345 kV GEN-2019-030 Interconnection (Non-shared NU) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2019-030 | 17822414 | 100% | 17822414 | 1
GEN-2019-030 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156801 | ERIS | Spearville to Clark County 345 kV GEN-2019-030 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2019-030 | 1268386 | 100% | 1268386 | 1
GEN-2019-037 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156675 | ERIS | Leland Olds 345kV GEN-2019-037 Interconnection (Non-shared NU) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2019-037 | 5916489 | 100% | 5916489 | 1
GEN-2019-037 | DISIS-2018-002 / DISIS-2019-001 | 01 NORTH | 156674 | ERIS | Leland Olds 345kV GEN-2019-037 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2019-037 | 3066936 | 100% | 3066936 | 1
GEN-2019-039 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156685 | ERIS | Columbus Southeast - Rising City 115kV GEN-2019-039 Interconnection (Non-shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-039 | 7100000 | 100% | 7100000 | 1
GEN-2019-039 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156684 | ERIS | Columbus Southeast - Rising City 115kV GEN-2019-039 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-039 | 700000 | 100% | 700000 | 1
GEN-2019-069 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 170507 | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a new HOSKINS3 to HOSKINS4 345-230 kV transformer 2 with a rating of 336 MVA | 5125632.7187 | 11.29% | 45400000 | 0.0404
GEN-2019-070 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 170507 | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a new HOSKINS3 to HOSKINS4 345-230 kV transformer 2 with a rating of 336 MVA | 2562816.3593 | 5.645% | 45400000 | 0.0404
GEN-2019-041 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156747 | ERIS | Monolith 115kV GEN-2019-041 Interconnection (Non-shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-041 | 1500000 | 100% | 1500000 | 1
GEN-2019-041 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156746 | ERIS | Monolith 115kV GEN-2019-041 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-041 | 700000 | 100% | 700000 | 1
GEN-2019-044 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 158590 | ERIS | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade | Contingent | Rebuild the existing CUDAHY 3 to CRKCK 3 115 kV line 1 (9.53 miles) to a standard rating of 135 MVA | 0 |  | 250000
GEN-2019-044 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156751 | ERIS | North Fort Dodge 115kV GEN-2019-044 Interconnection (Non-shared NU) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-044 | 6361713 | 100% | 6361713 | 1
GEN-2019-044 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156750 | ERIS | North Fort Dodge 115kV GEN-2019-044 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-044 | 297327 | 100% | 297327 | 1
GEN-2019-045 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156690 | ERIS | DeGrasse 138kV GEN-2019-045 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2019-045 | 1875903 | 100% | 1875903 | 1
GEN-2019-045 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156692 | ERIS | DeGrasse 138kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-045 | 1637992 | 100% | 1637992 | 1
GEN-2019-053 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156719 | ERIS | Great Bend - Spearville 230kV GEN-2019-053 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-053 | 795429 | 100% | 795429 | 1
GEN-2019-053 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156721 | ERIS | Great Bend - Spearville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-053, GEN-2019-055 | 3680604.75 | 25% | 14722419 | 1
GEN-2019-054 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156717 | ERIS | Great Bend - Circle 230kV GEN-2019-054 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-054 | 802997 | 100% | 802997 | 1
GEN-2019-054 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156718 | ERIS | Great Bend - Circle 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-054, GEN-2019-068 | 10213092.75 | 75% | 13617457 | 1
GEN-2019-055 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156720 | ERIS | Great Bend - Spearville 230kV GEN-2019-055 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-055 | 795429 | 100% | 795429 | 1
GEN-2019-055 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156721 | ERIS | Great Bend - Spearville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-053, GEN-2019-055 | 11041814.25 | 75% | 14722419 | 1
GEN-2019-058 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156681 | ERIS | Clark County 345kV GEN-2019-058 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2019-058 | 634193 | 100% | 634193 | 1
GEN-2019-058 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156683 | ERIS | Clark County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-058, GEN-2019-063 | 1538223 | 75% | 2050964 | 1
GEN-2019-063 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156682 | ERIS | Clark County 345kV GEN-2019-063 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2019-063 | 634193 | 100% | 634193 | 1
GEN-2019-063 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156683 | ERIS | Clark County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-058, GEN-2019-063 | 512741 | 25% | 2050964 | 1
GEN-2019-065 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156758 | ERIS | Overton-Northwest Henderson 138kV GEN-2019-065 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2019-065 | 12232419 | 100% | 12232419 | 1
GEN-2019-065 | DISIS-2018-002 / DISIS-2019-001 | 04 SOUTHEAST | 156757 | ERIS | Overton-Northwest Henderson 138kV GEN-2019-065 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2019-065 | 2144327 | 100% | 2144327 | 1
GEN-2019-068 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156716 | ERIS | Great Bend - Circle 230kV GEN-2019-068 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-068 | 802997 | 100% | 802997 | 1
GEN-2019-068 | DISIS-2018-002 / DISIS-2019-001 | 03 CENTRAL | 156718 | ERIS | Great Bend - Circle 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-054, GEN-2019-068 | 3404364.25 | 25% | 13617457 | 1
GEN-2019-069 | DISIS-2018-002 / DISIS-2019-001 CF | 02 NEBRASKA | 122739 | ERIS | Columbus East 230/115 kV transformer | Contingent | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | 0 |  | 9278651
GEN-2019-073 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 170507 | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a new HOSKINS3 to HOSKINS4 345-230 kV transformer 2 with a rating of 336 MVA | 5125632.7187 | 11.29% | 45400000 | 0.0404
GEN-2019-069 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156789 | ERIS | Madison 345kv GEN-2019-069 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-069 | 250000 | 100% | 250000 | 1
GEN-2019-069 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156793 | ERIS | Madison 345kv Interconnection (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-083, GEN-2019-069, GEN-2019-070, GEN-2019-073 | 6820000 | 20% | 34100000 | 1
GEN-2019-070 | DISIS-2018-002 / DISIS-2019-001 CF | 02 NEBRASKA | 122739 | ERIS | Columbus East 230/115 kV transformer | Contingent | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | 0 |  | 9278651
GEN-2019-039 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 158601 | ERIS | Rebuild Columbus SE to G19-039-TAP 115 kV | Current Study | Rebuild the existing COL.SE 7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | 4000000 | 100% | 4000000 | 0.82132
GEN-2019-070 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156790 | ERIS | Madison 345kv GEN-2019-070 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-070 | 250000 | 100% | 250000 | 1
GEN-2019-070 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156793 | ERIS | Madison 345kv Interconnection (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-083, GEN-2019-069, GEN-2019-070, GEN-2019-073 | 3410000 | 10% | 34100000 | 1
GEN-2019-073 | DISIS-2018-002 / DISIS-2019-001 CF | 02 NEBRASKA | 122739 | ERIS | Columbus East 230/115 kV transformer | Contingent | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | 0 |  | 9278651
GEN-2019-039 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 158603 | ERIS | Rebuild Rising to G19-039-TAP 115 kV | Current Study | Rebuild the existing RISNGCY7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | 5500000 | 100% | 5500000 | 0.17868
GEN-2019-073 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156791 | ERIS | Madison 345kv GEN-2019-073 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-073 | 250000 | 100% | 250000 | 1
GEN-2019-073 | DISIS-2018-002 / DISIS-2019-001 | 02 NEBRASKA | 156793 | ERIS | Madison 345kv Interconnection (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-083, GEN-2019-069, GEN-2019-070, GEN-2019-073 | 6820000 | 20% | 34100000 | 1
GEN-2019-039 | DISIS-2018-002 / DISIS-2019-001 CF | 02 NEBRASKA | 158601 | NRIS | Rebuild Columbus SE to G19-039-TAP 115 kV | Contingent | Rebuild the existing COL.SE 7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | 0 |  | 4000000
GEN-2019-039 | DISIS-2018-002 / DISIS-2019-001 CF | 02 NEBRASKA | 158603 | NRIS | Rebuild Rising to G19-039-TAP 115 kV | Contingent | Rebuild the existing RISNGCY7 to G19-039-TAP 115 kV line 1 (6.76 miles) to a standard rating of 180 MVA | 0 |  | 5500000
GEN-2018-131 | DISIS-2018-002 / DISIS-2019-001 CF | 02 NEBRASKA | 170229 | NRIS | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | Contingent | Build a new HOLT.CO3 to ANTELOPE 3 345 kV line 1 (24 miles) to a standard rating of 1792 MVA | 0 |  | 89100000
GEN-2018-132 | DISIS-2018-002 / DISIS-2019-001 CF | 02 NEBRASKA | 170229 | NRIS | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP) | Contingent | Build a new HOLT.CO3 to ANTELOPE 3 345 kV line 1 (24 miles) to a standard rating of 1792 MVA | 0 |  | 89100000
424854829

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 23SP, 26SP | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 93.06 | 107.06 |  |  |  | Sweetwater to Chisholm 230 kV Line Rebuild
04ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 23SP, 26SP | P42:345:OKGE:SB_BVTY7315_PRE19S | 349 | 395 | 116.94 | 132.44 |  |  |  | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
04ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 26SP | P42:345:OKGE:SB_BVTY7315_PRE19S | 535 | 535 | <90% | 102.22 |  |  |  | Multi - Border - Woodward 345 kV Tap
00NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | 514898 CIMARON4 138 997969 CIMARON1 _1 138 1 | 23SP | P13:138-345:OKGE:BKRBKR_3W021:::: | 478 | 478 | 93.05 | 100.8 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 514898 CIMARON4 138 997969 CIMARON1 _1 138 1 | 23SP | P13:138-345:OKGE:BKRBKR_3W021:::: | 478 | 478 | 94.08 | 101.72 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | 514901 CIMARON7 345 997969 CIMARON1 _1 138 1 | 23SP | P13:138-345:OKGE:BKRBKR_3W021:::: | 478 | 478 | 96.64 | 104.67 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 514901 CIMARON7 345 997969 CIMARON1 _1 138 1 | 23SP | P13:138-345:OKGE:BKRBKR_3W021:::: | 478 | 478 | 97.75 | 105.65 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
04ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 23SP, 26SP | P42:345:OKGE:SB_BVTY7315_PRE19S | 353 | 353 | 130.87 | 148.23 |  |  |  | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
04ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 26SP | P42:345:OKGE:SB_BVTY7315_PRE19S | 535 | 535 | <90% | 102.22 |  |  |  | Multi - Border - Woodward 345 kV Tap
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | 532782 BUFFALO7 345 | 23SP, 26SP, 26WP | PROXY_P4_345kV_POI 532782_5 |  |  |  |  | 0.916 | 0.95 | 1.05 | Switch Out Thistle Line Reactor Circuit 1
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | 532783 KINGMAN7 345 | 26WP | PROXY_P4_345kV_POI 532782_5 |  |  |  |  | 0.9499 | 0.95 | 1.05 | Switch Out Thistle Line Reactor Circuit 1
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 | 23SP, 26SP | System Intact | 119.5 | 148.2 | <90% | 103.34 |  |  |  | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | 539801 THISTLE7 345 | 23SP, 26SP, 26WP | PROXY_P4_345kV_POI 532782_5 |  |  |  |  | 0.9091 | 0.95 | 1.05 | Switch Out Thistle Line Reactor Circuit 1
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 26WP | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | 342 | 342 | 93.92 | 106.34 |  |  |  | Fargo 230 kV Terminal Upgrade
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 23SP, 26SP, 26WP | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 140 | 140 | <90% | 122.27 |  |  |  | Rebuild Columbus SE to G19-039-TAP 115 kV
02ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 640126 E.COL. 4 230 997070 COL.EAST T3 115 1 | 26WP | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | 187 | 187 | <90% | 122.27 |  |  |  | Columbus East 230/115 kV transformer
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 26WP | P13:230-345:NPPD:HOSKINS3:T2:::: | 336 | 336 | <90% | 107.13 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 26WP | P13:230-345:NPPD:NUCOR-1::::: | 336 | 336 | <90% | 107.13 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 26WP | P13:115-345:NPPD:HOSKINS3:T4:::: | 336 | 336 | <90% | 109.81 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 26WP | P13:115-345:NPPD:NUCOR-2::::: | 336 | 336 | <90% | 109.81 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 26SP | P13:230-345:NPPD:HOSKINS3:T2:::: | 336 | 336 | <90% | 107.65 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 26SP | P13:230-345:NPPD:NUCOR-1::::: | 336 | 336 | <90% | 107.65 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 23SP | P13:230-345:NPPD:HOSKINS3:T2:::: | 336 | 336 | <90% | 107.19 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 23SP | P13:230-345:NPPD:NUCOR-1::::: | 336 | 336 | <90% | 107.19 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 26SP | P13:115-345:NPPD:HOSKINS3:T4:::: | 336 | 336 | <90% | 108.98 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 26SP | P13:115-345:NPPD:NUCOR-2::::: | 336 | 336 | <90% | 108.98 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 23SP | P13:115-345:NPPD:HOSKINS3:T4:::: | 336 | 336 | <90% | 108.07 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 23SP | P13:115-345:NPPD:NUCOR-2::::: | 336 | 336 | <90% | 108.07 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 26WP | P13:230-345:NPPD:HOSKINS3:T2:::: | 336 | 336 | <90% | 105.87 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 26WP | P13:230-345:NPPD:NUCOR-1::::: | 336 | 336 | <90% | 105.87 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 26SP | P13:230-345:NPPD:HOSKINS3:T2:::: | 336 | 336 | <90% | 106.84 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 26SP | P13:230-345:NPPD:NUCOR-1::::: | 336 | 336 | <90% | 106.84 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640228 HOSKINS7 115 997023 HOSKN T4 _1 115 1 | 23SP | P13:230-345:NPPD:HOSKINS3:T2:::: | 336 | 336 | <90% | 106.19 |  |  |  | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 23SP, 26SP, 26WP | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 140 | 140 | <90% | 125.72 |  |  |  | Rebuild Rising to G19-039-TAP 115 kV
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 23SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 121 | 121 | 95.05 | 100.91 |  |  |  | NewBranch Dawsonc4 to Wiliston 230 kV
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26WP, 26SP | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | 117 | 117 | 108.42 | 121.4 |  |  |  | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26WP, 26SP | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | 117 | 117 | 108.42 | 121.4 |  |  |  | Rebuild the circuit from K338 to the new 69 kV tap station
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26WP, 26SP | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | 117 | 117 | 108.42 | 121.4 |  |  |  | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26WP, 26SP | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | 117 | 117 | 108.42 | 121.4 |  |  |  | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26WP, 26SP | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | 117 | 117 | 108.42 | 121.4 |  |  |  | WAPA DENISON8 69 kV Terminal Upgrade
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26WP, 26SP | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W/O A FAULT (EXI-AT TAP):HV: | 117 | 117 | 108.42 | 121.4 |  |  |  | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 23SP, 26L, 26WP, 26SP | 655931 BLKTLTAP-MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | <90% | 173.54 |  |  |  | Rebuild Mont to STRNDAHL Line_115kV
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | East Fork 345/115 kV Substation
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | East Fork 345/115 kV Transformer
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Finstad - Tande 345 kV New Line
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Finstad 345 kV New Substation
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Finstad Switched Shunt
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Folvag 115 kV Terminal Equipment
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Leland Olds - Finstad - 345 kV New Line
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Leland Olds 345 kV Substation
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | NE Williston - Folvag 115 kV New Line
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | NE Williston 115 kV Terminal Equipment
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Kummer Ridge - Round Up 345 kV
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Kummer Ridge 345 kV Terminal Upgrades
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | 127 | 127 | <90% | 101.24 |  |  |  | Round Up 345 kV Terminal Upgrades
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 26WP | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | 127 | 127 | <90% | 102.31 |  |  |  | NewBranch Dawsonc4 to Wiliston 230 kV
00NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 23SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 121 | 121 | 93.38 | 100.81 |  |  |  | NewBranch Dawsonc4 to Wiliston 230 kV
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 23SP, 26SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 121 | 121 | 96.28 | 102.14 |  |  |  | NewBranch Dawsonc4 to Wiliston 230 kV
00NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 26WP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 120 | 132 | 97.81 | 104.46 |  |  |  | NewBranch Dawsonc4 to Wiliston 230 kV
00NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 26WP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 120 | 132 | 97.81 | 104.46 |  |  |  | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 26WP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 120 | 132 | 103.59 | 107.83 |  |  |  | NewBranch Dawsonc4 to Wiliston 230 kV
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 26WP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 120 | 132 | 103.59 | 107.83 |  |  |  | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 659854 K335AMAI-NI8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP | Base Case | 34.8 | 45.5 | <90% | 103.54 |  |  |  | Rebuild the K335AMAI-NI8 to J6BOYER_-NI8 69kV Line 1
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | 760284 GEN-2017-220 345 | 23SP, 26SP, 26WP | PROXY_P4_345kV_POI 532782_5 |  |  |  |  | 0.9161 | 0.95 | 1.05 | Switch Out Thistle Line Reactor Circuit 1
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP | P21:115:UMZB:# 2613 #: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU | [7 empty] | Build Strandahl to Black Tail 115 kV line
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 | 23SP, 26SP, 26WP | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | 417 | 417 | <90% | 101.06 |  |  |  | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
01NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
01NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | None | 26L | None | [7 empty] | None
01NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Voltage | None | 26L | None | [7 empty] | None
01NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
01NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
01NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Non-Converge | None | 23SP, 26L, 26WP, 26SP | None | [7 empty] | None
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | None | 23SP, 26SP, 26L | None | [7 empty] | None
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
01ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Voltage | None | 23SP, 26SP, 26WP, 26L | None | [7 empty] | None
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | None | 26L | None | [7 empty] | None
03NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | None | 26L | None | [7 empty] | None
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | None | 26L | None | [7 empty] | None
03NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Voltage | None | 26L | None | [7 empty] | None
03ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | None | 26L | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Non-Converge | None | 26L | None | [7 empty] | None
02NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | None | 26L | None | [7 empty] | None
02NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Voltage | None | 26L | None | [7 empty] | None
02NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | None | 23SP, 26L, 26SP | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
02NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None
02NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
03ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | None | 23SP, 26L, 26SP | None | [7 empty] | None
03ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
03ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
03NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None
03NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
00ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
05ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Thermal | None | 26L, 26WP | None | [7 empty] | None
04ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
04ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | None | 26L | None | [7 empty] | None
04NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Voltage | None | 26L | None | [7 empty] | None
04NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
05NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | None | 26L | None | [7 empty] | None
05NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Voltage | None | 26L | None | [7 empty] | None
05NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
05ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
05ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | None | 23SP, 26L, 26WP | None | [7 empty] | None
04ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
04ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
00NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Thermal | None | 26SP | None | [7 empty] | None
00NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | DISIS-2018-002 / DISIS-2019-001 | NRIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00ALL | DISIS-2018-002 / DISIS-2019-001 CF | ERIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
04NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
04NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None
04NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
05NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | None | 26L | None | [7 empty] | None
05NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Voltage | None | 26L | None | [7 empty] | None
05NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
01ALL | DISIS-2018-002 / DISIS-2019-001 | ERIS | Stability | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. | 25SP, 25WP | GROUP1_P1_LOCAL_FAULT_134 | [7 empty] | Build Strandahl to Black Tail 115 kV line
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 23SP, 26SP, 26WP | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 140 | 140 | <90% | 122.3 |  |  |  | Rebuild Columbus SE to G19-039-TAP 115 kV
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 23SP, 26SP, 26WP | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 140 | 140 | <90% | 125.68 |  |  |  | Rebuild Rising to G19-039-TAP 115 kV
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 | 23SP | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | 417 | 417 | <90% | 101.02 |  |  |  | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 640521 ANTELOPE 7 115 996909 ANTELOPE T1 115 1 | 26SP | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | 417 | 417 | <90% | 100.82 |  |  |  | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
00NR | DISIS-2018-002 / DISIS-2019-001 CF | NRIS | Thermal | 640521 ANTELOPE 7 115 996907 ANTELOPE T1 115 1 | 26WP | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | 417 | 417 | <90% | 100.35 |  |  |  | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 26L and 26SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2018-115 | 04 SOUTHEAST | NRIS | 220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Yes | Yes | 0.0449 | 2025-05-30 | 24000 | 0
GEN-2018-063 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06881 | TBD (Delayed) | 3415129 | 0
GEN-2018-064 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0711 | TBD (Delayed) | 3415129 | 0
GEN-2018-071 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.14118 | TBD (Delayed) | 3415129 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.1235 | TBD (Delayed) | 3415129 | 0
GEN-2018-072 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.14118 | TBD (Delayed) | 3415129 | 0
GEN-2018-072 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.1235 | TBD (Delayed) | 3415129 | 0
GEN-2018-079 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08889 | TBD (Delayed) | 3415129 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05297 | TBD (Delayed) | 3415129 | 0
GEN-2018-106 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03053 | TBD (Delayed) | 3415129 | 0
GEN-2018-108 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.15835 | TBD (Delayed) | 3415129 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0407 | TBD (Delayed) | 3415129 | 0
GEN-2018-128 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08572 | TBD (Delayed) | 3415129 | 0
GEN-2018-128 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.13629 | TBD (Delayed) | 3415129 | 0
GEN-2019-001 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.22693 | TBD (Delayed) | 3415129 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07295 | TBD (Delayed) | 3415129 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04202 | TBD (Delayed) | 3415129 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03932 | TBD (Delayed) | 3415129 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06068 | TBD (Delayed) | 3415129 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07835 | TBD (Delayed) | 3415129 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03355 | TBD (Delayed) | 3415129 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07332 | TBD (Delayed) | 3415129 | 0
GEN-2019-016 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07166 | TBD (Delayed) | 3415129 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04202 | TBD (Delayed) | 3415129 | 0
GEN-2019-030 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.10389 | TBD (Delayed) | 3415129 | 0
GEN-2019-035 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06962 | TBD (Delayed) | 3415129 | 0
GEN-2019-044 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11929 | TBD (Delayed) | 3415129 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08746 | TBD (Delayed) | 3415129 | 0
GEN-2019-053 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.12066 | TBD (Delayed) | 3415129 | 0
GEN-2019-054 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.12537 | TBD (Delayed) | 3415129 | 0
GEN-2019-055 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.12066 | TBD (Delayed) | 3415129 | 0
GEN-2019-058 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.13159 | TBD (Delayed) | 3415129 | 0
GEN-2019-063 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.13159 | TBD (Delayed) | 3415129 | 0
GEN-2019-068 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.12537 | TBD (Delayed) | 3415129 | 0
GEN-2018-063 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07807 | 2025-07-15 | 87298154 | 0
GEN-2018-064 | 04 SOUTHEAST | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07134 | 2025-07-15 | 87298154 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0319 | 2025-07-15 | 87298154 | 0
GEN-2018-072 | 04 SOUTHEAST | NRIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0319 | 2025-07-15 | 87298154 | 0
GEN-2018-079 | 04 SOUTHEAST | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.04605 | 2025-07-15 | 87298154 | 0
GEN-2018-108 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0344 | 2025-07-15 | 87298154 | 0
GEN-2019-001 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0398 | 2025-07-15 | 87298154 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07231 | 2025-07-15 | 87298154 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03429 | 2025-07-15 | 87298154 | 0
GEN-2019-016 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0866 | 2025-07-15 | 87298154 | 0
GEN-2019-035 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07045 | 2025-07-15 | 87298154 | 0
GEN-2019-053 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0315 | 2025-07-15 | 87298154 | 0
GEN-2019-054 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03512 | 2025-07-15 | 87298154 | 0
GEN-2019-055 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0315 | 2025-07-15 | 87298154 | 0
GEN-2019-058 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03106 | 2025-07-15 | 87298154 | 0
GEN-2019-063 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03106 | 2025-07-15 | 87298154 | 0
GEN-2019-068 | 03 CENTRAL | ERIS | 210626 | 122598 | Line - Wolf Creek - Blackberry 345 kV | Blackberry - Wolf Creek 345 kV | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03512 | 2025-07-15 | 87298154 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.16286 | 2025-03-31 | 23239179 | 0
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.17776 | 2025-03-31 | 23239179 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.1802 | 2025-03-31 | 23239179 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.21312 | 2025-03-31 | 23239179 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.04611 | 2025-03-31 | 23239179 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.06291 | 2025-03-31 | 23239179 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.04231 | 2025-03-31 | 23239179 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.1802 | 2025-03-31 | 23239179 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.05152 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2018-088 | 04 SOUTHEAST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.03407 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.16286 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.17776 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2018-108 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.07241 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.09078 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.07807 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-001 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.03515 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.1802 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.21312 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-011 | 05 SOUTHWEST | NRIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.04611 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.13698 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.1336 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.06291 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.33006 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.1802 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-030 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.04677 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-044 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.05602 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.08669 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-053 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.05266 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-054 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.04706 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-055 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.05266 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-058 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.06128 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-063 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.06128 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2019-068 | 03 CENTRAL | ERIS | 210609 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border and Beckham 345kV Capacitive Reactive Support | Install +39 MVAR Capacitor Bank(s) at Border 345 kV and +39 MVAR Capacitor Bank(s) at Beckham County 345 kV | DISIS-2016-002 | Yes | Yes | 0.04706 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2018-067 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.12603 | 2029-09-12 | 9455440 | 0
GEN-2018-069 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.11055 | 2029-09-12 | 9455440 | 0
GEN-2019-023 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.11055 | 2029-09-12 | 9455440 | 0
GEN-2019-037 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.12953 | 2029-09-12 | 9455440 | 0
GEN-2018-067 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.12603 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2018-069 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.11055 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2018-069 | 01 NORTH | NRIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.16089 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2019-023 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.11055 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2019-023 | 01 NORTH | NRIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.16089 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2019-037 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.12953 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2019-037 | 01 NORTH | NRIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.05365 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2018-125 | 02 NEBRASKA | NRIS | TBD | 170229 | Antelope - Holt County 345 kV Ckt 1 New Line | Build new Antelope - Holt County 345 kV Ckt 1 Line (2024 ITP) | Build new Antelope - Holt County 345 kV Ckt 1 Line to a standard rating of 1792 MVA (2024 ITP) | 2024 ITP | No | Yes | 0.17238 | TBD | 40886805 | 0
GEN-2018-131 | 02 NEBRASKA | NRIS | TBD | 170229 | Antelope - Holt County 345 kV Ckt 1 New Line | Build new Antelope - Holt County 345 kV Ckt 1 Line (2024 ITP) | Build new Antelope - Holt County 345 kV Ckt 1 Line to a standard rating of 1792 MVA (2024 ITP) | 2024 ITP | No | Yes | 0.39924 | TBD | 40886805 | 0
GEN-2018-132 | 02 NEBRASKA | NRIS | TBD | 170229 | Antelope - Holt County 345 kV Ckt 1 New Line | Build new Antelope - Holt County 345 kV Ckt 1 Line (2024 ITP) | Build new Antelope - Holt County 345 kV Ckt 1 Line to a standard rating of 1792 MVA (2024 ITP) | 2024 ITP | No | Yes | 0.39924 | TBD | 40886805 | 0
GEN-2019-019 | 01 NORTH | NRIS | TBD | 170229 | Antelope - Holt County 345 kV Ckt 1 New Line | Build new Antelope - Holt County 345 kV Ckt 1 Line (2024 ITP) | Build new Antelope - Holt County 345 kV Ckt 1 Line to a standard rating of 1792 MVA (2024 ITP) | 2024 ITP | No | Yes | 0.08769 | TBD | 40886805 | 0
GEN-2019-039 | 02 NEBRASKA | NRIS | TBD | 170229 | Antelope - Holt County 345 kV Ckt 1 New Line | Build new Antelope - Holt County 345 kV Ckt 1 Line (2024 ITP) | Build new Antelope - Holt County 345 kV Ckt 1 Line to a standard rating of 1792 MVA (2024 ITP) | 2024 ITP | No | Yes | 0.14657 | TBD | 40886805 | 0
GEN-2019-041 | 02 NEBRASKA | NRIS | TBD | 170229 | Antelope - Holt County 345 kV Ckt 1 New Line | Build new Antelope - Holt County 345 kV Ckt 1 Line (2024 ITP) | Build new Antelope - Holt County 345 kV Ckt 1 Line to a standard rating of 1792 MVA (2024 ITP) | 2024 ITP | No | Yes | 0.0749 | TBD | 40886805 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.11369 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2018-099 | 05 SOUTHWEST | ERIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.25437 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2019-003 | 05 SOUTHWEST | ERIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.23078 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2019-003 | 05 SOUTHWEST | NRIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.1062 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2019-011 | 05 SOUTHWEST | ERIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.21985 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2019-011 | 05 SOUTHWEST | NRIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.09583 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2019-021 | 05 SOUTHWEST | ERIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.23078 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2019-021 | 05 SOUTHWEST | NRIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.1062 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2019-044 | 03 CENTRAL | ERIS | TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Yes | Yes | 0.03039 | TBD (36 month lead time) | 180684436 | 180684436
GEN-2018-067 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0396 | 2026-12-31 | 224639813 | 0
GEN-2018-069 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03676 | 2026-12-31 | 224639813 | 0
GEN-2018-125 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.1036 | 2026-12-31 | 224639813 | 0
GEN-2018-125 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.15007 | 2026-12-31 | 224639813 | 0
GEN-2018-131 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03168 | 2026-12-31 | 224639813 | 0
GEN-2018-131 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.10053 | 2026-12-31 | 224639813 | 0
GEN-2018-132 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03168 | 2026-12-31 | 224639813 | 0
GEN-2018-132 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.10053 | 2026-12-31 | 224639813 | 0
GEN-2019-023 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03676 | 2026-12-31 | 224639813 | 0
GEN-2019-037 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04946 | 2026-12-31 | 224639813 | 0
GEN-2019-039 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09466 | 2026-12-31 | 224639813 | 0
GEN-2019-041 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.08629 | 2026-12-31 | 224639813 | 0
GEN-2018-067 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03735 | 2026-12-31 | 254838000 | 0
GEN-2018-069 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03389 | 2026-12-31 | 254838000 | 0
GEN-2018-125 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.08821 | 2026-12-31 | 254838000 | 0
GEN-2018-125 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.10989 | 2026-12-31 | 254838000 | 0
GEN-2018-131 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09205 | 2026-12-31 | 254838000 | 0
GEN-2018-132 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09205 | 2026-12-31 | 254838000 | 0
GEN-2019-023 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03389 | 2026-12-31 | 254838000 | 0
GEN-2019-037 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0459 | 2026-12-31 | 254838000 | 0
GEN-2019-039 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09287 | 2026-12-31 | 254838000 | 0
GEN-2019-041 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.08943 | 2026-12-31 | 254838000 | 0
GEN-2018-067 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0396 | 2026-12-31 | 16186000 | 0
GEN-2018-069 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03676 | 2026-12-31 | 16186000 | 0
GEN-2018-125 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.1036 | 2026-12-31 | 16186000 | 0
GEN-2018-125 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.15007 | 2026-12-31 | 16186000 | 0
GEN-2018-131 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03168 | 2026-12-31 | 16186000 | 0
GEN-2018-131 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.10053 | 2026-12-31 | 16186000 | 0
GEN-2018-132 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03168 | 2026-12-31 | 16186000 | 0
GEN-2018-132 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.10053 | 2026-12-31 | 16186000 | 0
GEN-2019-023 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03676 | 2026-12-31 | 16186000 | 0
GEN-2019-037 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04946 | 2026-12-31 | 16186000 | 0
GEN-2019-039 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09466 | 2026-12-31 | 16186000 | 0
GEN-2019-041 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.08629 | 2026-12-31 | 16186000 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05152 | 2024-05-24 | 9331684 | 0
GEN-2018-088 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03407 | 2024-05-24 | 9331684 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05176 | 2024-05-24 | 9331684 | 0
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06384 | 2024-05-24 | 9331684 | 0
GEN-2018-108 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05057 | 2024-05-24 | 9331684 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.09078 | 2024-05-24 | 9331684 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05868 | 2024-05-24 | 9331684 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.07114 | 2024-05-24 | 9331684 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.08846 | 2024-05-24 | 9331684 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.1083 | 2024-05-24 | 9331684 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.12688 | 2024-05-24 | 9331684 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.36249 | 2024-05-24 | 9331684 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.33006 | 2024-05-24 | 9331684 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.07114 | 2024-05-24 | 9331684 | 0
GEN-2019-030 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03223 | 2024-05-24 | 9331684 | 0
GEN-2019-044 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04301 | 2024-05-24 | 9331684 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06067 | 2024-05-24 | 9331684 | 0
GEN-2019-053 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03739 | 2024-05-24 | 9331684 | 0
GEN-2019-054 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03015 | 2024-05-24 | 9331684 | 0
GEN-2019-055 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03739 | 2024-05-24 | 9331684 | 0
GEN-2019-058 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04471 | 2024-05-24 | 9331684 | 0
GEN-2019-063 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04471 | 2024-05-24 | 9331684 | 0
GEN-2019-068 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03015 | 2024-05-24 | 9331684 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05152 | 2026-05-01 | 8323241 | 0
GEN-2018-088 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03407 | 2026-05-01 | 8323241 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05176 | 2026-05-01 | 8323241 | 0
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06384 | 2026-05-01 | 8323241 | 0
GEN-2018-108 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05057 | 2026-05-01 | 8323241 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09078 | 2026-05-01 | 8323241 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05868 | 2026-05-01 | 8323241 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07114 | 2026-05-01 | 8323241 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08846 | 2026-05-01 | 8323241 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.1083 | 2026-05-01 | 8323241 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.12688 | 2026-05-01 | 8323241 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.36249 | 2026-05-01 | 8323241 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.33006 | 2026-05-01 | 8323241 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07114 | 2026-05-01 | 8323241 | 0
GEN-2019-030 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03223 | 2026-05-01 | 8323241 | 0
GEN-2019-044 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04301 | 2026-05-01 | 8323241 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06067 | 2026-05-01 | 8323241 | 0
GEN-2019-053 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03739 | 2026-05-01 | 8323241 | 0
GEN-2019-054 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03015 | 2026-05-01 | 8323241 | 0
GEN-2019-055 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03739 | 2026-05-01 | 8323241 | 0
GEN-2019-058 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04471 | 2026-05-01 | 8323241 | 0
GEN-2019-063 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04471 | 2026-05-01 | 8323241 | 0
GEN-2019-068 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03015 | 2026-05-01 | 8323241 | 0
GEN-2018-071 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.04015 | 2025-01-01 | 647852 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.06032 | 2025-01-01 | 647852 | 0
GEN-2018-072 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.04015 | 2025-01-01 | 647852 | 0
GEN-2018-072 | 04 SOUTHEAST | NRIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.06032 | 2025-01-01 | 647852 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.12553 | 2025-01-01 | 647852 | 0
GEN-2018-088 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.06202 | 2025-01-01 | 647852 | 0
GEN-2018-106 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.0453 | 2025-01-01 | 647852 | 0
GEN-2018-108 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.04475 | 2025-01-01 | 647852 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03352 | 2025-01-01 | 647852 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.06253 | 2025-01-01 | 647852 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.08263 | 2025-01-01 | 647852 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.04973 | 2025-01-01 | 647852 | 0
GEN-2019-044 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03828 | 2025-01-01 | 647852 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.05252 | 2025-01-01 | 647852 | 0
GEN-2019-053 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03571 | 2025-01-01 | 647852 | 0
GEN-2019-054 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03295 | 2025-01-01 | 647852 | 0
GEN-2019-055 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03571 | 2025-01-01 | 647852 | 0
GEN-2019-058 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03985 | 2025-01-01 | 647852 | 0
GEN-2019-063 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03985 | 2025-01-01 | 647852 | 0
GEN-2019-065 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.04865 | 2025-01-01 | 647852 | 0
GEN-2019-068 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03295 | 2025-01-01 | 647852 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA STUDIES | Yes | Yes | 0.03655 | 2027-02-28 | 12224000 | 12224000
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA STUDIES | Yes | Yes | 0.03087 | 2027-02-28 | 9932652 | 9932652
GEN-2019-039 | 02 NEBRASKA | ERIS | 210645 | 122739 | XFR - Columbus 230/115 | Columbus East 230/115 kV transformer | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | 2021 ITP | Yes | Yes | 0.19071 | 2025-06-01 | 9278651 | 0
GEN-2019-039 | 02 NEBRASKA | NRIS | 210645 | 122739 | Columbus East 230/115 kV transformer | Columbus East 230/115 kV transformer | Replace the 230/115 kV transformer and any necessary terminal equipment at Columbus East. | 2021 ITP | Yes | Yes | 0.20067 | 2025-06-01 | 9278651 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.10467 | 2026-05-15 | 196135074 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.092 | 2026-05-15 | 196135074 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.10467 | 2025-05-15 | 15910202 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.092 | 2025-05-15 | 15910202 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | TBD | 122645 | Curry - Deafsmith 115 kV Ckt 1 Rebuild (DISIS-2016-002) | Curry - Deafsmith 115 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA. | DISIS-2016-002 | Yes | Yes | 0.10657 | 12/15/2021 (delayed) | 4852215 | 4852215
GEN-2019-021 | 05 SOUTHWEST | ERIS | TBD | 122645 | Curry - Deafsmith 115 kV Ckt 1 Rebuild (DISIS-2016-002) | Curry - Deafsmith 115 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA. | DISIS-2016-002 | Yes | Yes | 0.10657 | 12/15/2021 (delayed) | 4852215 | 4852215
GEN-2019-012 | 04 SOUTHEAST | NRIS | 220739 | 122761 | Czech Hall 138 kV Terminal Upgrade | Czech Hall 138 kV Terminal Upgrade | UPGRADE TERMINAL EQUIPMENT AT CZECH HALL AND CIMARRON 138KV FOR 387/444 MVA RATING | 2023 ITP | Yes | Yes | 0.03221 | 2025-12-01 | 154916 | 0
GEN-2018-069 | 01 NORTH | ERIS | 220748 | 157280 | Device Dawson County-Fort Peck 230 kV 40 MVAR Line Reactor | Dawson County-Fort Peck 230 kV Line Reactor | Install 40 MVAR reactor on the Dawson County-Fort Peck 230 kV Line | 2023 ITP | Yes | Yes | 0.04961 | 2030-09-01 | 7300684 | 0
GEN-2018-069 | 01 NORTH | NRIS | 220748 | 157280 | Device Dawson County-Fort Peck 230 kV 40 MVAR Line Reactor | Dawson County-Fort Peck 230 kV Line Reactor | Install 40 MVAR reactor on the Dawson County-Fort Peck 230 kV Line | 2023 ITP | Yes | Yes | 0.0495 | 2030-09-01 | 7300684 | 0
GEN-2019-023 | 01 NORTH | ERIS | 220748 | 157280 | Device Dawson County-Fort Peck 230 kV 40 MVAR Line Reactor | Dawson County-Fort Peck 230 kV Line Reactor | Install 40 MVAR reactor on the Dawson County-Fort Peck 230 kV Line | 2023 ITP | Yes | Yes | 0.04961 | 2030-09-01 | 7300684 | 0
GEN-2019-023 | 01 NORTH | NRIS | 220748 | 157280 | Device Dawson County-Fort Peck 230 kV 40 MVAR Line Reactor | Dawson County-Fort Peck 230 kV Line Reactor | Install 40 MVAR reactor on the Dawson County-Fort Peck 230 kV Line | 2023 ITP | Yes | Yes | 0.0495 | 2030-09-01 | 7300684 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.0331 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2018-099 | 05 SOUTHWEST | ERIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.10753 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2019-003 | 05 SOUTHWEST | ERIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.05999 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2019-011 | 05 SOUTHWEST | ERIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.07338 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2019-011 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.03645 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2019-021 | 05 SOUTHWEST | ERIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum system emergency rating of 430 MVA. | DISIS-2016-002 | Yes | Yes | 0.05999 | 12/17/2021 (delayed) | 4578401 | 4578401
GEN-2018-089 | 05 SOUTHWEST | ERIS | TBD | 122648 | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Deaf Smith 115 kV substation. | DISIS-2016-002 | Yes | Yes | 0.04378 | 11/2021 (Delayed) | 3318137 | 3318137
GEN-2019-003 | 05 SOUTHWEST | ERIS | TBD | 122648 | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Deaf Smith 115 kV substation. | DISIS-2016-002 | Yes | Yes | 0.03353 | 11/2021 (Delayed) | 3318137 | 3318137
GEN-2019-003 | 05 SOUTHWEST | NRIS | TBD | 122648 | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Deaf Smith 115 kV substation. | DISIS-2016-002 | Yes | Yes | 0.03198 | 11/2021 (Delayed) | 3318137 | 3318137
GEN-2019-021 | 05 SOUTHWEST | ERIS | TBD | 122648 | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Deaf Smith 115 kV substation. | DISIS-2016-002 | Yes | Yes | 0.03353 | 11/2021 (Delayed) | 3318137 | 3318137
GEN-2019-021 | 05 SOUTHWEST | NRIS | TBD | 122648 | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Deafsmith 115 kV Capacitive Reactive Power Support (DISIS-2016-002) | Build 100 MVAR at Deaf Smith 115 kV substation. | DISIS-2016-002 | Yes | Yes | 0.03198 | 11/2021 (Delayed) | 3318137 | 3318137
GEN-2019-045 | 04 SOUTHEAST | ERIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.13375 | 2027-10-30 | 1200000 | 0
GEN-2018-074 | 01 NORTH | ERIS | TBD | 143686 | Denison to Boyer 69kV Terminal Upgrade | Denison to Boyer 69kV Terminal Upgrade | Upgrade terminal equipment at Denison 69kV to achieve a minimum rating of 117 MVA | DISIS-2017-002 | Yes | Yes | 0.18751 | TBD (36 month lead time) | 135000 | 135000
GEN-2018-072 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03191 | 2025-01-01 | 16516041 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.1007 | 2025-01-01 | 16516041 | 0
GEN-2018-088 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04512 | 2025-01-01 | 16516041 | 0
GEN-2018-106 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03554 | 2025-01-01 | 16516041 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03311 | 2025-01-01 | 16516041 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05423 | 2025-01-01 | 16516041 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04085 | 2025-01-01 | 16516041 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04093 | 2025-01-01 | 16516041 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04389 | 2025-01-01 | 16516041 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05794 | 2025-01-01 | 16516041 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04692 | 2025-01-01 | 16516041 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06844 | 2025-01-01 | 16516041 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04085 | 2025-01-01 | 16516041 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03496 | 2025-01-01 | 16516041 | 0
GEN-2019-065 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03744 | 2025-01-01 | 16516041 | 0
GEN-2018-072 | 04 SOUTHEAST | NRIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03191 | 2025-01-01 | 7099303 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.1007 | 2025-01-01 | 7099303 | 0
GEN-2018-088 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04512 | 2025-01-01 | 7099303 | 0
GEN-2018-106 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03554 | 2025-01-01 | 7099303 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03311 | 2025-01-01 | 7099303 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.05423 | 2025-01-01 | 7099303 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04085 | 2025-01-01 | 7099303 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04093 | 2025-01-01 | 7099303 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04389 | 2025-01-01 | 7099303 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.05794 | 2025-01-01 | 7099303 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04692 | 2025-01-01 | 7099303 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.06844 | 2025-01-01 | 7099303 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04085 | 2025-01-01 | 7099303 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03496 | 2025-01-01 | 7099303 | 0
GEN-2019-065 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03744 | 2025-01-01 | 7099303 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 200397 | 51526 | Driftwood 138 kV Substation | Driftwood 138 kV Substation | Tap the 138 kV line from Byron to Cherokee City to construct new Driftwood substation. Install any required 138 kV terminal upgrades required to install 138/69 kV transformer. | 2016 ITPNT | Yes | Yes | 0.09661 | 2023-07-31 | 600000 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.20125 | 2024-11-30 | 18251841 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.09409 | 2024-11-30 | 18251841 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.08651 | 2024-11-30 | 18251841 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.09409 | 2024-11-30 | 18251841 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.08674 | 2024-11-30 | 18251841 | 0
GEN-2019-037 | 01 NORTH | NRIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.03813 | 2024-11-30 | 18251841 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.34582 | 2024-11-30 | 6394630 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.03513 | 2024-11-30 | 6394630 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.03616 | 2024-11-30 | 6394630 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.03513 | 2024-11-30 | 6394630 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.03616 | 2024-11-30 | 6394630 | 0
GEN-2019-018 | 03 CENTRAL | NRIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase rating to 106/113.9 MVA | 2023 ITP | Yes | Yes | 0.07926 | 2028-01-01 | 750000 | 0
GEN-2019-053 | 03 CENTRAL | NRIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase rating to 106/113.9 MVA | 2023 ITP | Yes | Yes | 0.03259 | 2028-01-01 | 750000 | 0
GEN-2019-054 | 03 CENTRAL | NRIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase rating to 106/113.9 MVA | 2023 ITP | Yes | Yes | 0.03977 | 2028-01-01 | 750000 | 0
GEN-2019-055 | 03 CENTRAL | NRIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase rating to 106/113.9 MVA | 2023 ITP | Yes | Yes | 0.03259 | 2028-01-01 | 750000 | 0
GEN-2019-068 | 03 CENTRAL | NRIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase rating to 106/113.9 MVA | 2023 ITP | Yes | Yes | 0.03977 | 2028-01-01 | 750000 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne. Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo. | 2022 ITP | Yes | Yes | 0.04478 | 2025-12-31 | 92778 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne. Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo. | 2022 ITP | Yes | Yes | 0.04212 | 2025-12-31 | 92778 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne. Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo. | 2022 ITP | Yes | Yes | 0.0315 | 2025-12-31 | 92778 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne. Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo. | 2022 ITP | Yes | Yes | 0.03297 | 2025-12-31 | 92778 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne. Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo. | 2022 ITP | Yes | Yes | 0.04212 | 2025-12-31 | 92778 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne. Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo. | 2022 ITP | Yes | Yes | 0.03204 | 2025-12-31 | 92778 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne. Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo. | 2022 ITP | Yes | Yes | 0.05091 | 2025-12-31 | 92778 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.20427 | 2026-11-30 | 76991281 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.07538 | 2026-11-30 | 76991281 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.08848 | 2026-11-30 | 76991281 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.03379 | 2026-11-30 | 76991281 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.07538 | 2026-11-30 | 76991281 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.08848 | 2026-11-30 | 76991281 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.03122 | 2026-11-30 | 76991281 | 0
GEN-2019-037 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.06043 | 2026-11-30 | 76991281 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.20692 | 2026-11-30 | 18932308 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.0714 | 2026-11-30 | 18932308 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.08832 | 2026-11-30 | 18932308 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.03061 | 2026-11-30 | 18932308 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.0714 | 2026-11-30 | 18932308 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.08832 | 2026-11-30 | 18932308 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.05145 | 2026-11-30 | 18932308 | 0
GEN-2019-037 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.07701 | 2026-11-30 | 18932308 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.20692 | 2026-11-30 | 385021 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.0714 | 2026-11-30 | 385021 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.08832 | 2026-11-30 | 385021 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.03061 | 2026-11-30 | 385021 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.0714 | 2026-11-30 | 385021 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.08832 | 2026-11-30 | 385021 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.05145 | 2026-11-30 | 385021 | 0
GEN-2019-037 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.07701 | 2026-11-30 | 385021 | 0
GEN-2019-009 | 02 NEBRASKA | ERIS | 210538 | 112404 | Sub - Firth 115kV | Firth 115 kV Substation Expansion | Expand the existing Firth 115 kV substation to accommodate a new 15 MVAR capacitor bank. | 2019 ITP | Yes | Yes | 0.04604 | 2024-06-01 | 3036560 | 0
GEN-2019-009 | 02 NEBRASKA | ERIS | 210538 | 112403 | Sub - Firth 115kV | Firth Cap Bank 115kV Ckt 1 | Install new 15 MVAR capacitor bank at Firth 115 kV substation. | 2019 ITP | Yes | Yes | 0.04604 | 2024-06-01 | 608900 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210663 | 144163 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | Folvag 115 kV Terminal Equipment | Install terminal equipment at Folvag 115 kV sub to accommodate new 115 kV line from NE Williston 115 kV sub. | 2021 ITP | Yes | Yes | 0.06265 | 2024-11-01 | 500000 | 0
GEN-2018-131 | 02 NEBRASKA | ERIS | 220748 | 157946 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point - Yankton Junction 115 kV Ckt 1 Rebuild (WAPA) | Rebuild 4 miles of 115 kV Ckt 1 line from Gavins Point 115 kV substation to Yankton Junction 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.03456 | 2027-04-01 | 2539625 | 0
GEN-2018-132 | 02 NEBRASKA | ERIS | 220748 | 157946 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point - Yankton Junction 115 kV Ckt 1 Rebuild (WAPA) | Rebuild 4 miles of 115 kV Ckt 1 line from Gavins Point 115 kV substation to Yankton Junction 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.03456 | 2027-04-01 | 2539625 | 0
GEN-2019-023 | 01 NORTH | NRIS | 220748 | 157946 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point - Yankton Junction 115 kV Ckt 1 Rebuild (WAPA) | Rebuild 4 miles of 115 kV Ckt 1 line from Gavins Point 115 kV substation to Yankton Junction 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.0666 | 2027-04-01 | 2539625 | 0
GEN-2018-131 | 02 NEBRASKA | ERIS | 220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.03456 | 0 | 264000 | 0
GEN-2018-132 | 02 NEBRASKA | ERIS | 220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.03456 | 0 | 264000 | 0
GEN-2019-023 | 01 NORTH | NRIS | 220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.0666 | 0 | 264000 | 0
GEN-2019-019 | 01 NORTH | NRIS | 220743 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.03103 | 2026-01-01 | 1600000 | 0
GEN-2018-064 | 04 SOUTHEAST | NRIS | 210578 | 122718 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 161 kV Terminal Upgrades Transformer Ckt 1 | Upgrade terminal equipment at GRDA1 161 kV Ckt 1 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Yes | Yes | 0.07582 | 2023-05-01 | 453000 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 210578 | 122718 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 161 kV Terminal Upgrades Transformer Ckt 1 | Upgrade terminal equipment at GRDA1 161 kV Ckt 1 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Yes | Yes | 0.16959 | 2023-05-01 | 453000 | 0
GEN-2018-064 | 04 SOUTHEAST | NRIS | 210578 | 122802 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 161 kV Terminal Upgrades Transformer Ckt 2 | Upgrade terminal equipment at GRDA1 161 kV Ckt 2 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Yes | Yes | 0.07648 | 2023-05-01 | 453000 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 210578 | 122802 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 161 kV Terminal Upgrades Transformer Ckt 2 | Upgrade terminal equipment at GRDA1 161 kV Ckt 2 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Yes | Yes | 0.17108 | 2023-05-01 | 453000 | 0
GEN-2018-064 | 04 SOUTHEAST | NRIS | 210578 | 122717 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 345 kV Terminal Upgrades Transformer Ckt 1 | Upgrade terminal equipment at GRDA1 345 kV Ckt 1 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Yes | Yes | 0.07582 | 2023-05-01 | 374400 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 210578 | 122717 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 345 kV Terminal Upgrades Transformer Ckt 1 | Upgrade terminal equipment at GRDA1 345 kV Ckt 1 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Yes | Yes | 0.16959 | 2023-05-01 | 374400 | 0
GEN-2018-064 | 04 SOUTHEAST | NRIS | 210578 | 122801 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 345 kV Terminal Upgrades Transformer Ckt 2 | Upgrade terminal equipment at GRDA1 345 kV Ckt 2 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Yes | Yes | 0.07648 | 2023-05-01 | 312000 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 210578 | 122801 | Sub - GRDA1 345/161 kV Ckt 1 and Ckt 2 | GRDA1 345 kV Terminal Upgrades Transformer Ckt 2 | Upgrade terminal equipment at GRDA1 345 kV Ckt 2 to achieve a summer emergency rating of 558 MVA | 2020 ITP | Yes | Yes | 0.17108 | 2023-05-01 | 312000 | 0
GEN-2018-067 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.12036 | 2029-09-12 | 9263038 | 0
GEN-2018-069 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.10218 | 2029-09-12 | 9263038 | 0
GEN-2018-069 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.12248 | 2029-09-12 | 9263038 | 0
GEN-2019-019 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.07396 | 2029-09-12 | 9263038 | 0
GEN-2019-023 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.10218 | 2029-09-12 | 9263038 | 0
GEN-2019-023 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.12248 | 2029-09-12 | 9263038 | 0
GEN-2019-037 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.15214 | 2029-09-12 | 9263038 | 0
GEN-2019-037 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.09042 | 2029-09-12 | 9263038 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.10467 | 2025-05-15 | 18628957 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.092 | 2025-05-15 | 18628957 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03735 | 2026-12-31 | 842000 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03389 | 2026-12-31 | 842000 | 0
GEN-2018-125 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.08821 | 2026-12-31 | 842000 | 0
GEN-2018-125 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.10989 | 2026-12-31 | 842000 | 0
GEN-2018-131 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.09205 | 2026-12-31 | 842000 | 0
GEN-2018-132 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.09205 | 2026-12-31 | 842000 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03389 | 2026-12-31 | 842000 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.0459 | 2026-12-31 | 842000 | 0
GEN-2019-039 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.09287 | 2026-12-31 | 842000 | 0
GEN-2019-041 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.08943 | 2026-12-31 | 842000 | 0
GEN-2018-069 | 01 NORTH | NRIS | 220742 | 157892 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron - Huron 'B' Tap 115 kV Ckt 1 Rebuild (NWE) | Rebuild 0.2 mile Ckt 1 line from Huron 115 kV substation to Huron 'B' Tap 115 kV substation | 2023 ITP | Yes | Yes | 0.10147 | 0 | 207080 | 0
GEN-2019-023 | 01 NORTH | NRIS | 220742 | 157892 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron - Huron 'B' Tap 115 kV Ckt 1 Rebuild (NWE) | Rebuild 0.2 mile Ckt 1 line from Huron 115 kV substation to Huron 'B' Tap 115 kV substation | 2023 ITP | Yes | Yes | 0.10147 | 0 | 207080 | 0
GEN-2018-069 | 01 NORTH | NRIS | 220742 | 157891 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron - Huron West Park 115 kV Ckt 1 Rebuild (NWE) | Rebuild 10.4 mile Ckt 1 line from Huron 115 kV substation to Huron West Park 115 kV substation | 2023 ITP | Yes | Yes | 0.07225 | 0 | 11554745 | 0
GEN-2019-023 | 01 NORTH | NRIS | 220742 | 157891 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron - Huron West Park 115 kV Ckt 1 Rebuild (NWE) | Rebuild 10.4 mile Ckt 1 line from Huron 115 kV substation to Huron West Park 115 kV substation | 2023 ITP | Yes | Yes | 0.07225 | 0 | 11554745 | 0
GEN-2018-069 | 01 NORTH | NRIS | 220742 | 157724 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron B Tap 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Huron B Tap 115 kV substation on the Huron B Tap to Huron 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.10147 | 0 | 393298 | 0
GEN-2019-023 | 01 NORTH | NRIS | 220742 | 157724 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron B Tap 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Huron B Tap 115 kV substation on the Huron B Tap to Huron 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.10147 | 0 | 393298 | 0
GEN-2018-069 | 01 NORTH | NRIS | 220742 | 157721 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron West Park 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Huron West Park 115 kV substation on the Huron West Park to Huron 'B' Tap 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.07225 | 0 | 393298 | 0
GEN-2019-023 | 01 NORTH | NRIS | 220742 | 157721 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron West Park 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Huron West Park 115 kV substation on the Huron West Park to Huron 'B' Tap 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.07225 | 0 | 393298 | 0
GEN-2019-048 | 03 CENTRAL | ERIS | TBD | 159068 | Install a second 650 MVA TX at Nashua | Install a second 650 MVA TX at Nashua | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650 MVA | DISIS-2017-002 | Yes | Yes | 0.03753 | TBD (48 month lead time) | 22759204 | 22759204
GEN-2018-064 | 04 SOUTHEAST | ERIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05214 | 2026-12-31 | 730200 | 0
GEN-2018-064 | 04 SOUTHEAST | NRIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.06951 | 2026-12-31 | 730200 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05193 | 2026-12-31 | 730200 | 0
GEN-2018-064 | 04 SOUTHEAST | ERIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line (CKT 2) from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05214 | 0 | 730200 | 0
GEN-2018-064 | 04 SOUTHEAST | NRIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line (CKT 2) from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.06951 | 0 | 730200 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line (CKT 2) from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05193 | 0 | 730200 | 0
GEN-2018-064 | 04 SOUTHEAST | ERIS | 220741 | 156301/156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | KERR-MAID 161 KV CKT 1 AND 2 REBUILD | Rebuild 5.5 miles of 161 kV Ckt 1 and Ckt 2 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05214 | 2026-12-31 | 9846500 | 0
GEN-2018-064 | 04 SOUTHEAST | NRIS | 220741 | 156301/156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | KERR-MAID 161 KV CKT 1 AND 2 REBUILD | Rebuild 5.5 miles of 161 kV Ckt 1 and Ckt 2 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.06951 | 2026-12-31 | 9846500 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.20692 | 2026-11-30 | 215340373 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.0714 | 2026-11-30 | 215340373 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.08832 | 2026-11-30 | 215340373 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.03061 | 2026-11-30 | 215340373 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.0714 | 2026-11-30 | 215340373 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.08832 | 2026-11-30 | 215340373 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.05145 | 2026-11-30 | 215340373 | 0
GEN-2019-037 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.07701 | 2026-11-30 | 215340373 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.20692 | 2026-11-30 | 9338355 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.0714 | 2026-11-30 | 9338355 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.08832 | 2026-11-30 | 9338355 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.03061 | 2026-11-30 | 9338355 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.0714 | 2026-11-30 | 9338355 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.08832 | 2026-11-30 | 9338355 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.05145 | 2026-11-30 | 9338355 | 0
GEN-2019-037 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.07701 | 2026-11-30 | 9338355 | 0
GEN-2019-003 | 05 SOUTHWEST | NRIS | 210642 | 112401 | Sub - Lubbock South - Jones 230 kV Ckt 1 & 2 Terminal Upgrades | Lubbock South - Jones 230kV Ckt 2 Terminal Upgrades | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station | 2021 ITP | Yes | Yes | 0.03634 | TBD (Delayed) | 0 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 210642 | 112401 | Sub - Lubbock South - Jones 230 kV Ckt 1 & 2 Terminal Upgrades | Lubbock South - Jones 230kV Ckt 2 Terminal Upgrades | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station | 2021 ITP | Yes | Yes | 0.04026 | TBD (Delayed) | 0 | 0
GEN-2019-021 | 05 SOUTHWEST | NRIS | 210642 | 112401 | Sub - Lubbock South - Jones 230 kV Ckt 1 & 2 Terminal Upgrades | Lubbock South - Jones 230kV Ckt 2 Terminal Upgrades | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station | 2021 ITP | Yes | Yes | 0.03634 | TBD (Delayed) | 0 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210496 | 92151 | XFR - McDowell 230/115 kV Ckt 1 | McDowell Creek 230/115kV Substation | Tap Moore-Potter 230kV and tap Exell-Fain 115kV and tie into a new substation at McDowell Creek. | 2018 ITPNT | Yes | Yes | 0.07952 | 2024-11-22 | 15533553 | 0
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210496 | 92151 | XFR - McDowell 230/115 kV Ckt 1 | McDowell Creek 230/115kV Substation | Tap Moore-Potter 230kV and tap Exell-Fain 115kV and tie into a new substation at McDowell Creek. | 2018 ITPNT | Yes | Yes | 0.07055 | 2024-11-22 | 15533553 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210496 | 92151 | XFR - McDowell 230/115 kV Ckt 1 | McDowell Creek 230/115kV Substation | Tap Moore-Potter 230kV and tap Exell-Fain 115kV and tie into a new substation at McDowell Creek. | 2018 ITPNT | Yes | Yes | 0.07007 | 2024-11-22 | 15533553 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210496 | 92151 | XFR - McDowell 230/115 kV Ckt 1 | McDowell Creek 230/115kV Substation | Tap Moore-Potter 230kV and tap Exell-Fain 115kV and tie into a new substation at McDowell Creek. | 2018 ITPNT | Yes | Yes | 0.06169 | 2024-11-22 | 15533553 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210496 | 92151 | XFR - McDowell 230/115 kV Ckt 1 | McDowell Creek 230/115kV Substation | Tap Moore-Potter 230kV and tap Exell-Fain 115kV and tie into a new substation at McDowell Creek. | 2018 ITPNT | Yes | Yes | 0.07007 | 2024-11-22 | 15533553 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.06299 | 2025-01-01 | 38537430 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.05136 | 2025-01-01 | 38537430 | 0
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.05239 | 2025-01-01 | 38537430 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.11259 | 2025-01-01 | 38537430 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.1235 | 2025-01-01 | 38537430 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.07137 | 2025-01-01 | 38537430 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.07493 | 2025-01-01 | 38537430 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.03744 | 2025-01-01 | 38537430 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.06409 | 2025-01-01 | 38537430 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.08594 | 2025-01-01 | 38537430 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.09706 | 2025-01-01 | 38537430 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.07137 | 2025-01-01 | 38537430 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06299 | 2025-01-01 | 5170350 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05136 | 2025-01-01 | 5170350 | 0
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05239 | 2025-01-01 | 5170350 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.11259 | 2025-01-01 | 5170350 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.1235 | 2025-01-01 | 5170350 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07137 | 2025-01-01 | 5170350 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07493 | 2025-01-01 | 5170350 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03744 | 2025-01-01 | 5170350 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06409 | 2025-01-01 | 5170350 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08594 | 2025-01-01 | 5170350 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09706 | 2025-01-01 | 5170350 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07137 | 2025-01-01 | 5170350 | 0
GEN-2018-125 | 02 NEBRASKA | NRIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA STUDIES | Yes | Yes | 0.03979 | 2025-10-01 | 18617823 | 18617823
GEN-2018-131 | 02 NEBRASKA | NRIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA STUDIES | Yes | Yes | 0.03613 | 2025-10-01 | 18617823 | 18617823
GEN-2018-132 | 02 NEBRASKA | NRIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA STUDIES | Yes | Yes | 0.03613 | 2025-10-01 | 18617823 | 18617823
GEN-2019-009 | 02 NEBRASKA | ERIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA STUDIES | Yes | Yes | 0.04604 | 2025-10-01 | 18617823 | 18617823
GEN-2019-041 | 02 NEBRASKA | ERIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA STUDIES | Yes | Yes | 0.23149 | 2025-10-01 | 18617823 | 18617823
GEN-2019-041 | 02 NEBRASKA | NRIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA STUDIES | Yes | Yes | 0.26702 | 2025-10-01 | 18617823 | 18617823
GEN-2018-067 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04229 | 2025-10-01 | 24319368 | 24319368
GEN-2018-069 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04414 | 2025-10-01 | 24319368 | 24319368
GEN-2018-083 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.08648 | 2025-10-01 | 24319368 | 24319368
GEN-2018-125 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.11908 | 2025-10-01 | 24319368 | 24319368
GEN-2018-125 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.08933 | 2025-10-01 | 24319368 | 24319368
GEN-2018-131 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.08839 | 2025-10-01 | 24319368 | 24319368
GEN-2018-131 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03238 | 2025-10-01 | 24319368 | 24319368
GEN-2018-132 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.08839 | 2025-10-01 | 24319368 | 24319368
GEN-2018-132 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03238 | 2025-10-01 | 24319368 | 24319368
GEN-2019-009 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.09561 | 2025-10-01 | 24319368 | 24319368
GEN-2019-023 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04414 | 2025-10-01 | 24319368 | 24319368
GEN-2019-037 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.0548 | 2025-10-01 | 24319368 | 24319368
GEN-2019-039 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.1091 | 2025-10-01 | 24319368 | 24319368
GEN-2019-039 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.05303 | 2025-10-01 | 24319368 | 24319368
GEN-2019-041 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.31498 | 2025-10-01 | 24319368 | 24319368
GEN-2019-041 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.37089 | 2025-10-01 | 24319368 | 24319368
GEN-2019-048 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04427 | 2025-10-01 | 24319368 | 24319368
GEN-2019-069 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.09896 | 2025-10-01 | 24319368 | 24319368
GEN-2019-070 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.09896 | 2025-10-01 | 24319368 | 24319368
GEN-2019-073 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.09896 | 2025-10-01 | 24319368 | 24319368
GEN-2018-125 | 02 NEBRASKA | NRIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.03972 | 2024-10-01 | 5468352 | 5468352
GEN-2018-131 | 02 NEBRASKA | NRIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.03407 | 2024-10-01 | 5468352 | 5468352
GEN-2018-132 | 02 NEBRASKA | NRIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.03407 | 2024-10-01 | 5468352 | 5468352
GEN-2019-041 | 02 NEBRASKA | ERIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.25669 | 2024-10-01 | 5468352 | 5468352
GEN-2019-041 | 02 NEBRASKA | NRIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.22468 | 2024-10-01 | 5468352 | 5468352
GEN-2018-125 | 02 NEBRASKA | NRIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.03972 | 2025-10-01 | 5468352 | 5468352
GEN-2018-131 | 02 NEBRASKA | NRIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.03407 | 2025-10-01 | 5468352 | 5468352
GEN-2018-132 | 02 NEBRASKA | NRIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.03407 | 2025-10-01 | 5468352 | 5468352
GEN-2019-041 | 02 NEBRASKA | ERIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.25669 | 2025-10-01 | 5468352 | 5468352
GEN-2019-041 | 02 NEBRASKA | NRIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA STUDIES | Yes | Yes | 0.22468 | 2025-10-01 | 5468352 | 5468352
GEN-2018-069 | 01 NORTH | NRIS | 210585 | 143159 | Device - Moorehead 230 kV | Moorehead 230 kV Reactor | Install 2x40 MVAR reactors at Moorehead to control voltage on the 115 kV and 230 kV transmission systems | 2020 ITP | Yes | Yes | 0.03072 | 2024-12-31 | 6601822 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210585 | 143159 | Device - Moorehead 230 kV | Moorehead 230 kV Reactor | Install 2x40 MVAR reactors at Moorehead to control voltage on the 115 kV and 230 kV transmission systems | 2020 ITP | Yes | Yes | 0.03072 | 2024-12-31 | 6601822 | 0
GEN-2019-048 | 03 CENTRAL | ERIS | TBD | 50772 | Nashua 345/161 kV Transformer Upgrade Ckt11 | Nashua 345/161 kV Transformer Upgrade Ckt11 | Increase rating of Nashua transformer to 650/715 MVA. | 2023 ITP | Yes | Yes | 0.03753 | TBD (48 month lead time) | 8306343 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210663 | 144177 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | NE Williston - Folvag 115 kV New Line | Build a new 4.5 mile 115 kV line from NE Williston to Folvag. | 2021 ITP | Yes | Yes | 0.06265 | 2024-11-01 | 8700000 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210663 | 144178 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | NE Williston 115 kV Terminal Equipment | Install terminal equipment at NE Williston 115 kV sub to accommodate new 115 kV line from Folvag 115 kV sub. | 2021 ITP | Yes | Yes | 0.06265 | 2024-12-31 | 500000 | 0
GEN-2018-063 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.11403 | 0 | 3415129 | 0
GEN-2018-064 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.08096 | 0 | 3415129 | 0
GEN-2018-079 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.13412 | 0 | 3415129 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.08084 | 0 | 3415129 | 0
GEN-2019-016 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.14295 | 0 | 3415129 | 0
GEN-2019-035 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.072 | 0 | 3415129 | 0
GEN-2019-035 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.13148 | 0 | 3415129 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum emergency rating of 456 MVA. | DISIS-2016-002 | Yes | Yes | 0.27329 | 12/31/2020 (delayed) | 697514 | 697514
GEN-2019-003 | 05 SOUTHWEST | ERIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum emergency rating of 456 MVA. | DISIS-2016-002 | Yes | Yes | 0.10756 | 12/31/2020 (delayed) | 697514 | 697514
GEN-2019-011 | 05 SOUTHWEST | ERIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum emergency rating of 456 MVA. | DISIS-2016-002 | Yes | Yes | 0.07178 | 12/31/2020 (delayed) | 697514 | 697514
GEN-2019-021 | 05 SOUTHWEST | ERIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Newhart - Plant X 230 kV Ckt 1 Rebuild (DISIS-2016-002) | Rebuild line to achieve minimum emergency rating of 456 MVA. | DISIS-2016-002 | Yes | Yes | 0.10756 | 12/31/2020 (delayed) | 697514 | 697514
GEN-2018-067 | 01 NORTH | ERIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.04707 | 2025-01-01 | 561800 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.04259 | 2025-01-01 | 561800 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.0668 | 2025-01-01 | 561800 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.04174 | 2025-01-01 | 561800 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.04259 | 2025-01-01 | 561800 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.07057 | 2025-01-01 | 561800 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.05205 | 2025-01-01 | 561800 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.03191 | 2025-01-01 | 28449977 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.10759 | 2025-01-01 | 28449977 | 0
GEN-2018-088 | 04 SOUTHEAST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.04821 | 2025-01-01 | 28449977 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.05136 | 2025-01-01 | 28449977 | 0
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.05239 | 2025-01-01 | 28449977 | 0
GEN-2018-106 | 04 SOUTHEAST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.03797 | 2025-01-01 | 28449977 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.11259 | 2025-01-01 | 28449977 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.1235 | 2025-01-01 | 28449977 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.07137 | 2025-01-01 | 28449977 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.07493 | 2025-01-01 | 28449977 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.0469 | 2025-01-01 | 28449977 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.06409 | 2025-01-01 | 28449977 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.08594 | 2025-01-01 | 28449977 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.09706 | 2025-01-01 | 28449977 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.07137 | 2025-01-01 | 28449977 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.03735 | 2025-01-01 | 28449977 | 0
GEN-2019-065 | 04 SOUTHEAST | ERIS | 210616 | 143257 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (138 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | 2020 ITP | Yes | Yes | 0.04 | 2025-01-01 | 28449977 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.03191 | 2025-01-01 | 32342389 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.10759 | 2025-01-01 | 32342389 | 0
GEN-2018-088 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.04821 | 2025-01-01 | 32342389 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.05136 | 2025-01-01 | 32342389 | 0
GEN-2018-099 | 05 SOUTHWEST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.05239 | 2025-01-01 | 32342389 | 0
GEN-2018-106 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.03797 | 2025-01-01 | 32342389 | 0
GEN-2018-115 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.11259 | 2025-01-01 | 32342389 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.1235 | 2025-01-01 | 32342389 | 0
GEN-2019-003 | 05 SOUTHWEST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.07137 | 2025-01-01 | 32342389 | 0
GEN-2019-011 | 05 SOUTHWEST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.07493 | 2025-01-01 | 32342389 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.03744 | 2025-01-01 | 32342389 | 0
GEN-2019-012 | 04 SOUTHEAST | NRIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.06409 | 2025-01-01 | 32342389 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.08594 | 2025-01-01 | 32342389 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.09706 | 2025-01-01 | 32342389 | 0
GEN-2019-021 | 05 SOUTHWEST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.07137 | 2025-01-01 | 32342389 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.03735 | 2025-01-01 | 32342389 | 0
GEN-2019-065 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.04 | 2025-01-01 | 32342389 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.07295 | 0 | 10545000 | 0
GEN-2019-003 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03059 | 0 | 10545000 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03786 | 0 | 10545000 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03635 | 0 | 10545000 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03853 | 0 | 10545000 | 0
GEN-2019-021 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03059 | 0 | 10545000 | 0
GEN-2019-003 | 05 SOUTHWEST | NRIS | 220780 | 158631 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 | Replace existing 345/230 kV transformer at Potter County substation ckt 1 | 2023 ITP | Yes | Yes | 0.03059 | 0 | 10187000 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 220780 | 158631 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 | Replace existing 345/230 kV transformer at Potter County substation ckt 1 | 2023 ITP | Yes | Yes | 0.03786 | 0 | 10187000 | 0
GEN-2019-021 | 05 SOUTHWEST | NRIS | 220780 | 158631 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 | Replace existing 345/230 kV transformer at Potter County substation ckt 1 | 2023 ITP | Yes | Yes | 0.03059 | 0 | 10187000 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.07295 | 0 | 5577000 | 0
GEN-2019-003 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03059 | 0 | 5577000 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03786 | 0 | 5577000 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03635 | 0 | 5577000 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03853 | 0 | 5577000 | 0
GEN-2019-021 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03059 | 0 | 5577000 | 0
GEN-2018-089 | 05 SOUTHWEST | ERIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.07295 | 0 | 9642000 | 0
GEN-2019-003 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.03059 | 0 | 9642000 | 0
GEN-2019-011 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.03786 | 0 | 9642000 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.03635 | 0 | 9642000 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.03853 | 0 | 9642000 | 0
GEN-2019-021 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.03059 | 0 | 9642000 | 0
GEN-2019-039 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild Columbus SE to G19-039-TAP 115 kV | Rebuild Columbus SE to G19-039-TAP 115 kV | Rebuild approximately 6.76 miles of 115kV line from Columbus southeast to G16-039-TAP | DISIS-2018-002/2019-001 | No | Yes | 0.82257 | TBD | 4000000 | 4000000
GEN-2019-039 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild Rising to G19-039-TAP 115 kV | Rebuild Rising to G19-039-TAP 115 kV | Rebuild approximately 6.76 miles of 115kV line from Rising to G19-039-TAP | DISIS-2018-002/2019-001 | No | Yes | 0.17743 | TBD | 5500000 | 5500000
GEN-2018-125 | 02 NEBRASKA | NRIS | TBD | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | Yes | Yes | 0.0376 | TBD (36 month lead time) | 8300000 | 8300000
GEN-2018-131 | 02 NEBRASKA | NRIS | TBD | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | Yes | Yes | 0.03202 | TBD (36 month lead time) | 8300000 | 8300000
GEN-2018-132 | 02 NEBRASKA | NRIS | TBD | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | Yes | Yes | 0.03202 | TBD (36 month lead time) | 8300000 | 8300000
GEN-2019-018 | 03 CENTRAL | NRIS | 210719 | 122803 | Device - Russell 115 kV | Russell 115 kV Capacitor Bank | Add new 24 MVAR capacitor bank at Russell 115 kV | 2020 ITP | Yes | Yes | 0.02996 | 2024-04-01 | 7172538 | 0
GEN-2019-053 | 03 CENTRAL | NRIS | 210719 | 122803 | Device - Russell 115 kV | Russell 115 kV Capacitor Bank | Add new 24 MVAR capacitor bank at Russell 115 kV | 2020 ITP | Yes | Yes | 0.0355 | 2024-04-01 | 7172538 | 0
GEN-2019-054 | 03 CENTRAL | NRIS | 210719 | 122803 | Device - Russell 115 kV | Russell 115 kV Capacitor Bank | Add new 24 MVAR capacitor bank at Russell 115 kV | 2020 ITP | Yes | Yes | 0.0447 | 2024-04-01 | 7172538 | 0
GEN-2019-055 | 03 CENTRAL | NRIS | 210719 | 122803 | Device - Russell 115 kV | Russell 115 kV Capacitor Bank | Add new 24 MVAR capacitor bank at Russell 115 kV | 2020 ITP | Yes | Yes | 0.0355 | 2024-04-01 | 7172538 | 0
GEN-2019-068 | 03 CENTRAL | NRIS | 210719 | 122803 | Device - Russell 115 kV | Russell 115 kV Capacitor Bank | Add new 24 MVAR capacitor bank at Russell 115 kV | 2020 ITP | Yes | Yes | 0.0447 | 2024-04-01 | 7172538 | 0
GEN-2018-083 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03204 | 2026-12-31 | 64071687 | 0
GEN-2018-131 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03743 | 2026-12-31 | 64071687 | 0
GEN-2018-132 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03743 | 2026-12-31 | 64071687 | 0
GEN-2019-039 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03462 | 2026-12-31 | 64071687 | 0
GEN-2019-069 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03697 | 2026-12-31 | 64071687 | 0
GEN-2019-070 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03697 | 2026-12-31 | 64071687 | 0
GEN-2019-073 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03697 | 2026-12-31 | 64071687 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04435 | 2026-12-31 | 2070042 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04307 | 2026-12-31 | 2070042 | 0
GEN-2018-074 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06144 | 2026-12-31 | 2070042 | 0
GEN-2018-083 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04261 | 2026-12-31 | 2070042 | 0
GEN-2018-125 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.0802 | 2026-12-31 | 2070042 | 0
GEN-2018-131 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05741 | 2026-12-31 | 2070042 | 0
GEN-2018-131 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.07009 | 2026-12-31 | 2070042 | 0
GEN-2018-132 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05741 | 2026-12-31 | 2070042 | 0
GEN-2018-132 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.07009 | 2026-12-31 | 2070042 | 0
GEN-2019-009 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03636 | 2026-12-31 | 2070042 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03829 | 2026-12-31 | 2070042 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04307 | 2026-12-31 | 2070042 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05002 | 2026-12-31 | 2070042 | 0
GEN-2019-039 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.09376 | 2026-12-31 | 2070042 | 0
GEN-2019-041 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.16921 | 2026-12-31 | 2070042 | 0
GEN-2019-041 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.08031 | 2026-12-31 | 2070042 | 0
GEN-2019-069 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.0503 | 2026-12-31 | 2070042 | 0
GEN-2019-070 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.0503 | 2026-12-31 | 2070042 | 0
GEN-2019-073 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.0503 | 2026-12-31 | 2070042 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.04871 | 2024-06-28 | 100000 | 100000
GEN-2018-069 | 01 NORTH | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.04776 | 2024-06-28 | 100000 | 100000
GEN-2018-074 | 01 NORTH | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.0762 | 2024-06-28 | 100000 | 100000
GEN-2018-083 | 02 NEBRASKA | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.04885 | 2024-06-28 | 100000 | 100000
GEN-2018-131 | 02 NEBRASKA | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.06265 | 2024-06-28 | 100000 | 100000
GEN-2018-131 | 02 NEBRASKA | NRIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.04565 | 2024-06-28 | 100000 | 100000
GEN-2018-132 | 02 NEBRASKA | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.06265 | 2024-06-28 | 100000 | 100000
GEN-2018-132 | 02 NEBRASKA | NRIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.04565 | 2024-06-28 | 100000 | 100000
GEN-2019-023 | 01 NORTH | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.04776 | 2024-06-28 | 100000 | 100000
GEN-2019-037 | 01 NORTH | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.0571 | 2024-06-28 | 100000 | 100000
GEN-2019-039 | 02 NEBRASKA | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.03962 | 2024-06-28 | 100000 | 100000
GEN-2019-069 | 02 NEBRASKA | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.05678 | 2024-06-28 | 100000 | 100000
GEN-2019-070 | 02 NEBRASKA | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.05678 | 2024-06-28 | 100000 | 100000
GEN-2019-073 | 02 NEBRASKA | ERIS | 210600 | 143178 | Multi - S3456 - S3458 345 kV, S3455 - S3740 345 kV, S1260 - S1362 161 kV | S3456 to S3458 345 kV Ckt 1 Terminal Upgrades | The upgrade disconnect switch and associated jumpers on S3456 to S3458 345 kV line to achieve at least a 981 MVA summer emergency rating. | DPA STUDIES | Yes | Yes | 0.05678 | 2024-06-28 | 100000 | 100000
GEN-2018-083 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03204 | 2026-12-31 | 1786830 | 0
GEN-2018-131 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03743 | 2026-12-31 | 1786830 | 0
GEN-2018-132 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03743 | 2026-12-31 | 1786830 | 0
GEN-2019-039 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03462 | 2026-12-31 | 1786830 | 0
GEN-2019-069 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03697 | 2026-12-31 | 1786830 | 0
GEN-2019-070 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03697 | 2026-12-31 | 1786830 | 0
GEN-2019-073 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03697 | 2026-12-31 | 1786830 | 0
GEN-2018-125 | 02 NEBRASKA | NRIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA STUDIES | Yes | Yes | 0.03979 | 2025-10-01 | 1173160 | 1173160
GEN-2018-131 | 02 NEBRASKA | NRIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA STUDIES | Yes | Yes | 0.03613 | 2025-10-01 | 1173160 | 1173160
GEN-2018-132 | 02 NEBRASKA | NRIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA STUDIES | Yes | Yes | 0.03613 | 2025-10-01 | 1173160 | 1173160
GEN-2019-041 | 02 NEBRASKA | ERIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA STUDIES | Yes | Yes | 0.23149 | 2025-10-01 | 1173160 | 1173160
GEN-2019-041 | 02 NEBRASKA | NRIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA STUDIES | Yes | Yes | 0.26702 | 2025-10-01 | 1173160 | 1173160
GEN-2018-125 | 02 NEBRASKA | NRIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA STUDIES | Yes | Yes | 0.03979 | 2025-10-01 | 5928037 | 5928037
GEN-2018-131 | 02 NEBRASKA | NRIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA STUDIES | Yes | Yes | 0.03613 | 2025-10-01 | 5928037 | 5928037
GEN-2018-132 | 02 NEBRASKA | NRIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA STUDIES | Yes | Yes | 0.03613 | 2025-10-01 | 5928037 | 5928037
GEN-2019-041 | 02 NEBRASKA | ERIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA STUDIES | Yes | Yes | 0.23149 | 2025-10-01 | 5928037 | 5928037
GEN-2019-041 | 02 NEBRASKA | NRIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA STUDIES | Yes | Yes | 0.26702 | 2025-10-01 | 5928037 | 5928037
GEN-2018-063 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0348 | 2026-01-01 | 121709542 | 0
GEN-2018-064 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05906 | 2026-01-01 | 121709542 | 0
GEN-2018-071 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.12514 | 2026-01-01 | 121709542 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.10711 | 2026-01-01 | 121709542 | 0
GEN-2018-072 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.12514 | 2026-01-01 | 121709542 | 0
GEN-2018-072 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.10711 | 2026-01-01 | 121709542 | 0
GEN-2018-079 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05388 | 2026-01-01 | 121709542 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03612 | 2026-01-01 | 121709542 | 0
GEN-2018-108 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03509 | 2026-01-01 | 121709542 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06703 | 2026-01-01 | 121709542 | 0
GEN-2018-128 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03392 | 2026-01-01 | 121709542 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06359 | 2026-01-01 | 121709542 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03676 | 2026-01-01 | 121709542 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03058 | 2026-01-01 | 121709542 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07852 | 2026-01-01 | 121709542 | 0
GEN-2019-016 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03243 | 2026-01-01 | 121709542 | 0
GEN-2019-035 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03705 | 2026-01-01 | 121709542 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.04016 | 2026-01-01 | 121709542 | 0
GEN-2018-063 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0348 | 2025-05-01 | 5915803 | 0
GEN-2018-064 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05906 | 2025-05-01 | 5915803 | 0
GEN-2018-071 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.12514 | 2025-05-01 | 5915803 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.10711 | 2025-05-01 | 5915803 | 0
GEN-2018-072 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.12514 | 2025-05-01 | 5915803 | 0
GEN-2018-072 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.10711 | 2025-05-01 | 5915803 | 0
GEN-2018-079 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05388 | 2025-05-01 | 5915803 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03612 | 2025-05-01 | 5915803 | 0
GEN-2018-108 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03509 | 2025-05-01 | 5915803 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06703 | 2025-05-01 | 5915803 | 0
GEN-2018-128 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03392 | 2025-05-01 | 5915803 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06359 | 2025-05-01 | 5915803 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03676 | 2025-05-01 | 5915803 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03058 | 2025-05-01 | 5915803 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07852 | 2025-05-01 | 5915803 | 0
GEN-2019-016 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03243 | 2025-05-01 | 5915803 | 0
GEN-2019-035 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03705 | 2025-05-01 | 5915803 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04016 | 2025-05-01 | 5915803 | 0
GEN-2018-063 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0348 | 2025-10-01 | 3909824 | 0
GEN-2018-064 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05906 | 2025-10-01 | 3909824 | 0
GEN-2018-071 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.12514 | 2025-10-01 | 3909824 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.10711 | 2025-10-01 | 3909824 | 0
GEN-2018-072 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.12514 | 2025-10-01 | 3909824 | 0
GEN-2018-072 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.10711 | 2025-10-01 | 3909824 | 0
GEN-2018-079 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05388 | 2025-10-01 | 3909824 | 0
GEN-2018-082 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03612 | 2025-10-01 | 3909824 | 0
GEN-2018-108 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03509 | 2025-10-01 | 3909824 | 0
GEN-2018-115 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06703 | 2025-10-01 | 3909824 | 0
GEN-2018-128 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03392 | 2025-10-01 | 3909824 | 0
GEN-2019-002 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06359 | 2025-10-01 | 3909824 | 0
GEN-2019-012 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03676 | 2025-10-01 | 3909824 | 0
GEN-2019-013 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03058 | 2025-10-01 | 3909824 | 0
GEN-2019-013 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07852 | 2025-10-01 | 3909824 | 0
GEN-2019-016 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03243 | 2025-10-01 | 3909824 | 0
GEN-2019-035 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03705 | 2025-10-01 | 3909824 | 0
GEN-2019-045 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04016 | 2025-10-01 | 3909824 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.04707 | 2025-01-01 | 562397 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.04259 | 2025-01-01 | 562397 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.0668 | 2025-01-01 | 562397 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.04259 | 2025-01-01 | 562397 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.07057 | 2025-01-01 | 562397 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.05205 | 2025-01-01 | 562397 | 0
GEN-2018-067 | 01 NORTH | ERIS | 210639 | 122735 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes 230 kV Terminal Upgrades | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 2021 ITP | Yes | Yes | 0.04707 | 2023-12-01 | 627400 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210639 | 122735 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes 230 kV Terminal Upgrades | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 2021 ITP | Yes | Yes | 0.04259 | 2023-12-01 | 627400 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210639 | 122735 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes 230 kV Terminal Upgrades | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 2021 ITP | Yes | Yes | 0.0668 | 2023-12-01 | 627400 | 0
GEN-2019-019 | 01 NORTH | NRIS | 210639 | 122735 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes 230 kV Terminal Upgrades | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 2021 ITP | Yes | Yes | 0.04174 | 2023-12-01 | 627400 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210639 | 122735 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes 230 kV Terminal Upgrades | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 2021 ITP | Yes | Yes | 0.04259 | 2023-12-01 | 627400 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210639 | 122735 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes 230 kV Terminal Upgrades | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 2021 ITP | Yes | Yes | 0.07057 | 2023-12-01 | 627400 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210639 | 122735 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes 230 kV Terminal Upgrades | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 2021 ITP | Yes | Yes | 0.05205 | 2023-12-01 | 627400 | 0
GEN-2018-071 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04502 | N/A | N/A | N/A
GEN-2018-072 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04502 | N/A | N/A | N/A
GEN-2018-115 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.03188 | N/A | N/A | N/A
GEN-2019-012 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.07758 | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06304 | N/A | N/A | N/A
GEN-2019-018 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.0508 | N/A | N/A | N/A
GEN-2019-030 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.05201 | N/A | N/A | N/A
GEN-2019-054 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04836 | N/A | N/A | N/A
GEN-2019-058 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06595 | N/A | N/A | N/A
GEN-2019-063 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06595 | N/A | N/A | N/A
GEN-2019-068 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 1 | Switch Out Buffalo Line Reactor Circuit 1 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04836 | N/A | N/A | N/A
GEN-2018-071 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04502 | N/A | N/A | N/A
GEN-2018-072 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04502 | N/A | N/A | N/A
GEN-2018-115 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.03188 | N/A | N/A | N/A
GEN-2019-012 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.07758 | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06304 | N/A | N/A | N/A
GEN-2019-018 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.0508 | N/A | N/A | N/A
GEN-2019-030 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.05201 | N/A | N/A | N/A
GEN-2019-054 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04836 | N/A | N/A | N/A
GEN-2019-058 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06595 | N/A | N/A | N/A
GEN-2019-063 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06595 | N/A | N/A | N/A
GEN-2019-068 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Buffalo Line Reactor Circuit 2 | Switch Out Buffalo Line Reactor Circuit 2 | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04836 | N/A | N/A | N/A
GEN-2019-018 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 1 | Switch Out Thistle Line Reactor Circuit 1 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.05459 | N/A | N/A | N/A
GEN-2019-030 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 1 | Switch Out Thistle Line Reactor Circuit 1 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.12432 | N/A | N/A | N/A
GEN-2019-053 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 1 | Switch Out Thistle Line Reactor Circuit 1 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04478 | N/A | N/A | N/A
GEN-2019-055 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 1 | Switch Out Thistle Line Reactor Circuit 1 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04478 | N/A | N/A | N/A
GEN-2019-058 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 1 | Switch Out Thistle Line Reactor Circuit 1 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.15356 | N/A | N/A | N/A
GEN-2019-063 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 1 | Switch Out Thistle Line Reactor Circuit 1 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.15356 | N/A | N/A | N/A
GEN-2019-018 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 2 | Switch Out Thistle Line Reactor Circuit 2 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.05459 | N/A | N/A | N/A
GEN-2019-030 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 2 | Switch Out Thistle Line Reactor Circuit 2 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.12432 | N/A | N/A | N/A
GEN-2019-053 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 2 | Switch Out Thistle Line Reactor Circuit 2 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04478 | N/A | N/A | N/A
GEN-2019-055 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 2 | Switch Out Thistle Line Reactor Circuit 2 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04478 | N/A | N/A | N/A
GEN-2019-058 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 2 | Switch Out Thistle Line Reactor Circuit 2 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.15356 | N/A | N/A | N/A
GEN-2019-063 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Thistle Line Reactor Circuit 2 | Switch Out Thistle Line Reactor Circuit 2 | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.15356 | N/A | N/A | N/A
GEN-2018-071 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04502 | N/A | N/A | N/A
GEN-2018-072 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04502 | N/A | N/A | N/A
GEN-2018-115 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.03188 | N/A | N/A | N/A
GEN-2019-012 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.07758 | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06304 | N/A | N/A | N/A
GEN-2019-018 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.0508 | N/A | N/A | N/A
GEN-2019-030 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.05201 | N/A | N/A | N/A
GEN-2019-054 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04836 | N/A | N/A | N/A
GEN-2019-058 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06595 | N/A | N/A | N/A
GEN-2019-063 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06595 | N/A | N/A | N/A
GEN-2019-068 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 1 | Switch Out Wichita Line Reactor Circuit 1 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04836 | N/A | N/A | N/A
GEN-2018-071 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.03188 | N/A | N/A | N/A
GEN-2018-072 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06304 | N/A | N/A | N/A
GEN-2018-115 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.0508 | N/A | N/A | N/A
GEN-2019-012 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04502 | N/A | N/A | N/A
GEN-2019-013 | 04 SOUTHEAST | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.07758 | N/A | N/A | N/A
GEN-2019-018 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.0348 | N/A | N/A | N/A
GEN-2019-030 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.05201 | N/A | N/A | N/A
GEN-2019-054 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04836 | N/A | N/A | N/A
GEN-2019-058 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06595 | N/A | N/A | N/A
GEN-2019-063 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.06595 | N/A | N/A | N/A
GEN-2019-068 | 03 CENTRAL | NRIS | TBD | TBD | Switch Out Wichita Line Reactor Circuit 2 | Switch Out Wichita Line Reactor Circuit 2 | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | DISIS-2018-002/2019-001 | No | Yes | 0.04836 | N/A | N/A | N/A
GEN-2018-125 | 02 NEBRASKA | NRIS | 200277 | 51002 | XFR - Thedford 345/115 kV | Thedford 345 kV Terminal Upgrades | Install any necessary 345 kV terminal equipment at Thedford associated with new 345/115 kV transformer. | HPILS | Yes | Yes | 0.04923 | 2026-12-31 | 1326679 | 0
GEN-2018-125 | 02 NEBRASKA | NRIS | 200277 | 50889 | XFR - Thedford 345/115 kV | Thedford 345/115 kV Transformer | Install new 345/115 kV 400 MVA transformer at Thedford substation. Install any necessary 115 kV terminal equipment. | HPILS | Yes | Yes | 0.04923 | 2026-12-31 | 9928833 | 0
GEN-2019-003 | 05 SOUTHWEST | NRIS | TBD | 122647 | Tuco 230 kV Capacitive Reactive Power Support | Tuco 230 kV Capacitive Reactive Power Support | Build 100 MVAR at Tuco 230 kV Substation. | DISIS-2016-002 | Yes | Yes | 0.09116 | 12/31/2020 (Delayed) | 5943138 | 5943138
GEN-2019-011 | 05 SOUTHWEST | NRIS | TBD | 122647 | Tuco 230 kV Capacitive Reactive Power Support | Tuco 230 kV Capacitive Reactive Power Support | Build 100 MVAR at Tuco 230 kV Substation. | DISIS-2016-002 | Yes | Yes | 0.05096 | 12/31/2020 (Delayed) | 5943138 | 5943138
GEN-2019-021 | 05 SOUTHWEST | NRIS | TBD | 122647 | Tuco 230 kV Capacitive Reactive Power Support | Tuco 230 kV Capacitive Reactive Power Support | Build 100 MVAR at Tuco 230 kV Substation. | DISIS-2016-002 | Yes | Yes | 0.09116 | 12/31/2020 (Delayed) | 5943138 | 5943138
GEN-2018-088 | 04 SOUTHEAST | ERIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.03741 | 2026-03-01 | 5250000 | 0
GEN-2018-128 | 03 CENTRAL | NRIS | TBD | 122792 | Viola 345/138 kV Transformer CKT 2 | Viola 345/138 kV Transformer CKT 2 (DISIS-2016-002-2) | Install a new 345 kV terminal on a new rung consisting of two (2) breakers, four (4) switches, and two (2) control panels. Install a new 138 kV terminal on an existing rung consisting of one (1) breaker, three (3) switches, three (3) PTs, and one (1) 400/440 MVA 345-138 kV transformer with LTCs. | DISIS-2016-002 | Yes | Yes | 0.06247 | TBD | 11450023 | 11450023
GEN-2018-067 | 01 NORTH | ERIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.04707 | 2025-01-01 | 2734578 | 0
GEN-2018-069 | 01 NORTH | ERIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.04259 | 2025-01-01 | 2734578 | 0
GEN-2018-069 | 01 NORTH | NRIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.0668 | 2025-01-01 | 2734578 | 0
GEN-2019-023 | 01 NORTH | ERIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.04259 | 2025-01-01 | 2734578 | 0
GEN-2019-023 | 01 NORTH | NRIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.07057 | 2025-01-01 | 2734578 | 0
GEN-2019-037 | 01 NORTH | ERIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.05205 | 2025-01-01 | 2734578 | 0

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | TO->FROM | 659854 K335AMAI-NI8 69.0 659912 J6BOYER_-NI8 69.0 1 | 34.8 | 45.5 | 0.05396 | 103.54 | Base Case | TDF Impact | Rebuild the K335AMAI-NI8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82698 | 173.54 | 655931 BLKTLTAP-MW7 115 655941 STRNDAHL-MW7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82689 | 173.46 | P12:115:UMZB:# 7139 #:: ZAH IN ND. ZAHL - TYRONE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82689 | 173.31 | P12:115:UMZ:# 5692 #: PROPER N-1 (LINE) FOR 655931-655955-1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 118.02 | P12:115:UMZB:# 2535 #:: SLN IN ND. PIONEER - STATELINE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 118.02 | P21:115:UMZB:# 2538 #:: SLN IN ND. OPENING OF LINE SECTION WITHOUT FAULT SLN-SBT:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.63729 | 115.01 | 655931 BLKTLTAP-MW7 115 655956 TYRONE -MW7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.63729 | 110.19 | P12:115:UMZB:# 7142 #:: TYO IN ND. TYRONE - EAST FORK:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 101.22 | P21:115:UMZB:# 2614 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-BTE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 101.22 | P12:115:UMZB:# 2612 #:: STR IN ND. STRANDAHL - BARR BUTTE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 101.22 | P21:115:UMZB:# 2628 #: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 101.22 | P21:115:UMZB:# 2628 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.85 | P12:115:UMZB:# 2625 #:: BTE IN ND. BARR BUTTE - GRENORA:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.85 | P21:115:UMZB:# 2813 #: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.85 | P21:115:UMZB:# 2813 #:: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.85 | P21:115:UMZB:# 2627 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-GRN:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82719 | 165.43 | 655931 BLKTLTAP-MW7 115 655941 STRNDAHL-MW7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.8271 | 165.36 | P12:115:UMZB:# 7139 #:: ZAH IN ND. ZAHL - TYRONE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.8271 | 165.21 | P12:115:UMZ:# 5692 #: PROPER N-1 (LINE) FOR 655931-655955-1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.63687 | 118.68 | 655931 BLKTLTAP-MW7 115 655956 TYRONE -MW7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 118.22 | P21:115:UMZB:# 2628 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 118.22 | P21:115:UMZB:# 2614 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-BTE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 118.22 | P12:115:UMZB:# 2612 #:: STR IN ND. STRANDAHL - BARR BUTTE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 118.22 | P21:115:UMZB:# 2628 #: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 117.77 | P12:115:UMZB:# 2625 #:: BTE IN ND. BARR BUTTE - GRENORA:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 117.77 | P21:115:UMZB:# 2813 #:: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 117.77 | P21:115:UMZB:# 2813 #: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 117.77 | P21:115:UMZB:# 2627 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-GRN:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.63687 | 112.46 | P12:115:UMZB:# 7142 #:: TYO IN ND. TYRONE - EAST FORK:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 108.76 | P21:115:UMZB:# 2815 #:: GRN IN ND. GRENORA TO SNAKE BUTTE TAP LINE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 108.42 | P12:115:UMZ:# 5800 #: PROPER N-1 (LINE) FOR 659145-655778-1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 108.42 | P12:115:UMZB:# 2810 #:: SBT IN ND. LOSS OF SNAKE BUTTE TAP:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 106.2 | 655778 SNAKEBTT-SH7 115 659430 PIONEER2-BE7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 106.1 | P21:115:UMZB:# 2538 #:: SLN IN ND. OPENING OF LINE SECTION WITHOUT FAULT SLN-SBT:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55681 | 106.1 | P12:115:UMZB:# 2535 #:: SLN IN ND. PIONEER - STATELINE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.51448 | 104.04 | 655931 BLKTLTAP-MW7 115 655955 ZAHL -MW7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82697 | 172.66 | 655931 BLKTLTAP-MW7 115 655941 STRNDAHL-MW7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82689 | 172.57 | P12:115:UMZB:# 7139 #:: ZAH IN ND. ZAHL - TYRONE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82689 | 172.42 | P12:115:UMZ:# 5692 #: PROPER N-1 (LINE) FOR 655931-655955-1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 117.08 | P21:115:UMZB:# 2538 #:: SLN IN ND. OPENING OF LINE SECTION WITHOUT FAULT SLN-SBT:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 117.08 | P12:115:UMZB:# 2535 #:: SLN IN ND. PIONEER - STATELINE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.63729 | 111.71 | 655931 BLKTLTAP-MW7 115 655956 TYRONE -MW7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.63729 | 104.76 | P12:115:UMZB:# 7142 #:: TYO IN ND. TYRONE - EAST FORK:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.63 | P12:115:UMZB:# 2612 #:: STR IN ND. STRANDAHL - BARR BUTTE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.63 | P21:115:UMZB:# 2614 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-BTE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.63 | P21:115:UMZB:# 2628 #: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.63 | P21:115:UMZB:# 2628 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.15 | P21:115:UMZB:# 2627 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-GRN:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.15 | P12:115:UMZB:# 2625 #:: BTE IN ND. BARR BUTTE - GRENORA:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.15 | P21:115:UMZB:# 2813 #: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.55743 | 100.15 | P21:115:UMZB:# 2813 #:: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82694 | 117.5 | 655931 BLKTLTAP-MW7 115 655941 STRNDAHL-MW7 115 1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82685 | 117.42 | P12:115:UMZB:# 7139 #:: ZAH IN ND. ZAHL - TYRONE:HV: | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-067 | TO->FROM | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 115 | 115 | 0.82685 | 117.32 | P12:115:UMZ:# 5692 #: PROPER N-1 (LINE) FOR 655931-655955-1 | TDF Impact | Rebuild Mont to STRNDAHL Line_115kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24307 | 114.02 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24354 | 107.76 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.86 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.85 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24208 | 104.92 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24341 | 108.22 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the DENISON8 to J6BOYER_-NI8 69kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24307 | 114.02 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24354 | 107.76 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.86 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.85 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24208 | 104.92 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24341 | 108.22 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | WAPA DENISON8 69 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24307 | 114.02 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24354 | 107.76 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.86 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.85 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24208 | 104.92 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24341 | 108.22 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Build a new 69 kV tap station cutting off DENISON8 - MANNINGTAP 8 and K338 - K318 circuits
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24307 | 114.02 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24354 | 107.76 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.86 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.85 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24208 | 104.92 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24341 | 108.22 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the circuit from K338 to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24307 | 114.02 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24354 | 107.76 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.86 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.85 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24208 | 104.92 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24341 | 108.22 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 121.4 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24265 | 121.26 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.12 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24204 | 116.02 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24215 | 115.92 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24307 | 114.02 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24254 | 110.51 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24354 | 107.76 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.86 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.85 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24111 | 107.8 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24101 | 107.75 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24208 | 104.92 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P12:161:WAPA:DENISON-EXIRA:1 | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 111 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24241 | 110.92 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24252 | 110.76 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1 | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 117 | 117 | 0.24341 | 108.22 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | TDF Impact | Rebuild the circuit from WAPA Denison to the new 69 kV tap station
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 23SP | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2613 #: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 23SP | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P12:115:UMZB:# 2578 #:: MNU IN ND. MONT - STRANDAHL:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 23SP | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2582 #:: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULT MNU-STR:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 23SP | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2613 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26L | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2613 #: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26L | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P12:115:UMZB:# 2578 #:: MNU IN ND. MONT - STRANDAHL:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26L | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2582 #:: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULT MNU-STR:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26L | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2613 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26SP | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2613 #: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26SP | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P12:115:UMZB:# 2578 #:: MNU IN ND. MONT - STRANDAHL:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26SP | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2582 #:: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULT MNU-STR:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26SP | GEN-2018-067 |  | Non-Converge |  |  | 0.38539 |  | P21:115:UMZB:# 2613 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU:HV: |  | Build Strandahl to Black Tail 115 kV line
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | East Fork 345/115 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | East Fork 345/115 kV Transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Finstad - Tande 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Finstad 345 kV New Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Finstad Switched Shunt
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Folvag 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Leland Olds - Finstad - 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Leland Olds 345 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | NE Williston - Folvag 115 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | NE Williston 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Kummer Ridge - Round Up 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Kummer Ridge 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Round Up 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | East Fork 345/115 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | East Fork 345/115 kV Transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Finstad - Tande 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Finstad 345 kV New Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Finstad Switched Shunt
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Folvag 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Leland Olds - Finstad - 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Leland Olds 345 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | NE Williston - Folvag 115 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | NE Williston 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Kummer Ridge - Round Up 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Kummer Ridge 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Round Up 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | East Fork 345/115 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | East Fork 345/115 kV Transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Finstad - Tande 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Finstad 345 kV New Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Finstad Switched Shunt
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Folvag 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Leland Olds - Finstad - 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Leland Olds 345 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | NE Williston - Folvag 115 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | NE Williston 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Kummer Ridge - Round Up 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Kummer Ridge 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2018-069 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Round Up 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | East Fork 345/115 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | East Fork 345/115 kV Transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Finstad - Tande 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Finstad 345 kV New Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Finstad Switched Shunt
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Folvag 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Leland Olds - Finstad - 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Leland Olds 345 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | NE Williston - Folvag 115 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | NE Williston 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Kummer Ridge - Round Up 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Kummer Ridge 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | Round Up 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | East Fork 345/115 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | East Fork 345/115 kV Transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Finstad - Tande 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Finstad 345 kV New Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Finstad Switched Shunt
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Folvag 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Leland Olds - Finstad - 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Leland Olds 345 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | NE Williston - Folvag 115 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | NE Williston 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Kummer Ridge - Round Up 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Kummer Ridge 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.24 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | Round Up 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | East Fork 345/115 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | East Fork 345/115 kV Transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Finstad - Tande 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Finstad 345 kV New Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Finstad Switched Shunt
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Folvag 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Leland Olds - Finstad - 345 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Leland Olds 345 kV Substation
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | NE Williston - Folvag 115 kV New Line
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | NE Williston 115 kV Terminal Equipment
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Kummer Ridge - Round Up 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Kummer Ridge 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 1 | 26WP | GEN-2019-023 | TO->FROM | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27819 | 101.04 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | Round Up 345 kV Terminal Upgrades
Thermal | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 1 | 23SP | GEN-2019-044 | TO->FROM | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 | 119.5 | 148.2 | 0.11881 | 103.34 | System Intact | TDF Impact | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 1 | 26SP | GEN-2019-044 | TO->FROM | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 | 119.5 | 148.2 | 0.11885 | 101.03 | System Intact | TDF Impact | CUDAHY 3 to CRKCK 3 115kV Line 1 Terminal Upgrade
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 00NR | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 00NR | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 00NR | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 0 | 23SP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 0 | 26L | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 0 | 26SP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 0 | 26WP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 0 | 23SP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 0 | 26L | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 0 | 26SP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 0 | 26WP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-039 | TO->FROM | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 122.26 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | Cumulative Impact | Rebuild Columbus SE to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 107.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10168 | 107.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10168 | 107.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 107.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 107.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 107.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 107.19 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10168 | 107.19 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10168 | 107.19 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 107.19 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 107.19 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 107.19 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 108.07 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1163 | 108.07 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1163 | 108.07 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 108.07 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 108.07 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 108.07 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 108.07 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1163 | 108.07 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1163 | 108.07 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 108.07 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 108.07 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 108.07 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-083 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 107.22 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1163 | 107.22 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1163 | 107.22 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-069 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 107.22 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-070 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 107.22 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-073 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 107.22 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-083 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 107.22 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1163 | 107.22 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1163 | 107.22 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-069 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 107.22 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-070 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 107.22 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-073 | TO->FROM | 640227 HOSKINS4 230 997025 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11365 | 107.22 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-083 | TO->FROM | 640228 HOSKINS7 115 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 106.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | TO->FROM | 640228 HOSKINS7 115 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10168 | 106.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | TO->FROM | 640228 HOSKINS7 115 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10168 | 106.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-069 | TO->FROM | 640228 HOSKINS7 115 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 106.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-070 | TO->FROM | 640228 HOSKINS7 115 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 106.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-073 | TO->FROM | 640228 HOSKINS7 115 997023 HOSKN T4 _1 115 1 | 336 | 336 | 0.10301 | 106.19 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2019-039 | TO->FROM | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 125.64 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Cumulative Impact | Rebuild Rising to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.06 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.06 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.06 | POI 640226_1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.06 | POI 640226_1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.05 | POI 640226_5 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.05 | POI 640226_5 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.05 | POI 640226_3 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 23SP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.05 | POI 640226_3 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26L | N/A |  | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-039 | TO->FROM | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 122.26 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | Cumulative Impact | Rebuild Columbus SE to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 107.65 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 107.65 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10209 | 107.65 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10209 | 107.65 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10209 | 107.65 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10209 | 107.65 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 107.65 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 107.65 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 107.65 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 107.65 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 107.65 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 107.65 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.98 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.98 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11666 | 108.98 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11666 | 108.98 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11666 | 108.98 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11666 | 108.98 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.98 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.98 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.98 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.98 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.98 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.98 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-083 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.23 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-083 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.23 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11666 | 108.23 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11666 | 108.23 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11666 | 108.23 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11666 | 108.23 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-069 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.23 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-069 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.23 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-070 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.23 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-070 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.23 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-073 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.23 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-073 | TO->FROM | 640227 HOSKINS4 230 997024 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11398 | 108.23 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-083 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 106.84 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-083 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 106.84 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10209 | 106.84 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10209 | 106.84 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10209 | 106.84 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10209 | 106.84 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-069 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 106.84 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-069 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 106.84 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-070 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 106.84 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-070 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 106.84 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-073 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 106.84 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-073 | TO->FROM | 640228 HOSKINS7 115 997022 HOSKN T4 _1 115 1 | 336 | 336 | 0.10337 | 106.84 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2019-039 | TO->FROM | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 125.72 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Cumulative Impact | Rebuild Rising to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.33 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.33 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.34 | POI 640226_1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.34 | POI 640226_1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.17 | POI 640226_5 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.17 | POI 640226_5 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.17 | POI 640226_3 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.17 | POI 640226_3 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.03 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.03 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.04 | POI 640226_1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.04 | POI 640226_1 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.02 | POI 640226_5 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.02 | POI 640226_5 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-131 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.99 | POI 640226_3 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26SP | GEN-2018-132 | TO->FROM | 640521 ANTELOPE 7 115 996915 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.99 | POI 640226_3 | Cumulative Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-039 | TO->FROM | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 122.27 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | Cumulative Impact | Rebuild Columbus SE to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 1 | 26WP | GEN-2018-083 | FROM->TO | 640126 E.COL. 4 230 997070 COL.EAST T3 115 1 | 187 | 187 | 0.07514 | 101.59 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | Cumulative Impact | Columbus East 230/115 kV transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 1 | 26WP | GEN-2019-069 | FROM->TO | 640126 E.COL. 4 230 997070 COL.EAST T3 115 1 | 187 | 187 | 0.07514 | 101.59 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | Cumulative Impact | Columbus East 230/115 kV transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 1 | 26WP | GEN-2019-070 | FROM->TO | 640126 E.COL. 4 230 997070 COL.EAST T3 115 1 | 187 | 187 | 0.07514 | 101.59 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | Cumulative Impact | Columbus East 230/115 kV transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 1 | 26WP | GEN-2019-073 | FROM->TO | 640126 E.COL. 4 230 997070 COL.EAST T3 115 1 | 187 | 187 | 0.07514 | 101.59 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1 | Cumulative Impact | Columbus East 230/115 kV transformer
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 107.13 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 107.13 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.1026 | 107.13 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.1026 | 107.13 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.1026 | 107.13 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.1026 | 107.13 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 107.13 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 107.13 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 107.13 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 107.13 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 107.13 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 107.13 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 109.81 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 109.81 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1171 | 109.81 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1171 | 109.81 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1171 | 109.81 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1171 | 109.81 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 109.81 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 109.81 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 109.81 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 109.81 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 109.81 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 109.81 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-083 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 108.96 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-083 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 108.96 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1171 | 108.96 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1171 | 108.96 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1171 | 108.96 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.1171 | 108.96 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-069 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 108.96 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-069 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 108.96 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-070 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 108.96 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-070 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 108.96 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-073 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 108.96 | P13:115-345:NPPD:HOSKINS3:T4:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-073 | TO->FROM | 640227 HOSKINS4 230 997022 HOSKINS T2 _ 230 1 | 336 | 336 | 0.11441 | 108.96 | P13:115-345:NPPD:NUCOR-2::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-083 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 105.87 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-083 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 105.87 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.1026 | 105.87 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-131 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.1026 | 105.87 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 0 | 26WP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 0 | 23SP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 0 | 26L | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 0 | 26SP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 0 | 26WP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 01NR | 0 | 26L | N/A |  | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 01NR | 1 | 26L | N/A |  | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 01NR | 0 | 26L | N/A |  | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.1026 | 105.87 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2018-132 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.1026 | 105.87 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-069 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 105.87 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-069 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 105.87 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-070 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 105.87 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-070 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 105.87 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-073 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 105.87 | P13:230-345:NPPD:HOSKINS3:T2:::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-073 | TO->FROM | 640228 HOSKINS7 115 997020 HOSKN T4 _1 115 1 | 336 | 336 | 0.10387 | 105.87 | P13:230-345:NPPD:NUCOR-1::::: | Cumulative Impact | Build a Second 345-230 kV Transformer at Hoskins_345kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 1 | 26WP | GEN-2019-039 | TO->FROM | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 125.06 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | Cumulative Impact | Rebuild Rising to G19-039-TAP 115 kV
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 02NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 02NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 0 | 23SP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 0 | 26SP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 0 | 26L | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 0 | 26WP | N/A |  | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 03NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 03NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 1 | 106.48 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 1 | 106.49 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 1 | 106.49 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.27871 | 101.58 | Potential P4 Event - POI 523961_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.27876 | 100.34 | Potential P4 Event - POI 523097_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.27876 | 100.34 | Potential P4 Event - POI 523097_9 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.28771 | 100.8 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 104.22 | Potential P4 Event - POI 511468_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.18 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.18 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.18 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.18 | Potential P4 Event - POI 511456_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.18 | Potential P4 Event - POI 511456_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.18 | Potential P4 Event - POI 511456_5 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.18 | Potential P4 Event - POI 762467_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.19 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.19 | Potential P4 Event - POI 511456_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.2 | Potential P4 Event - POI 511456_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.32 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.32 | Potential P4 Event - POI 762467_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.33 | Potential P4 Event - POI 762467_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.34 | Potential P4 Event - POI 762216_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.38 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.39 | Potential P4 Event - POI 762216_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29071 | 107.41 | Potential P4 Event - POI 762216_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29592 | 107.41 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29592 | 107.41 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.29592 | 107.41 | Potential P4 Event - POI 511468_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2752 | 108.58 | Potential P4 Event - POI 523097_18 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.27695 | 106.68 | Potential P4 Event - POI 523961_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.27871 | 113.68 | Potential P4 Event - POI 523961_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.27876 | 112.29 | Potential P4 Event - POI 523097_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.27876 | 112.29 | Potential P4 Event - POI 523097_9 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2791 | 110.36 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2791 | 110.36 | Potential P4 Event - POI 523097_13 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2791 | 110.36 | Potential P4 Event - POI 523097_16 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2791 | 110.36 | Potential P4 Event - POI 523097_20 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28484 | 108.77 | Potential P4 Event - POI 515375_50 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28484 | 108.78 | Potential P4 Event - POI 515375_47 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28577 | 105.1 | Potential P4 Event - POI 515375_32 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28577 | 105.1 | Potential P4 Event - POI 515375_38 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28585 | 107.53 | Potential P4 Event - POI 515375_43 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28613 | 105.59 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28613 | 105.63 | 515458 BORDER 7 345 755000 WWDBORDT 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28613 | 105.64 | 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28613 | 105.66 | P42:345:OKGE:SB_BVTY7387:::: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28613 | 106.45 | Potential P4 Event - POI 515375_54 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28613 | 107.04 | Potential P4 Event - POI 515375_52 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28631 | 105.92 | Potential P4 Event - POI 515375_8 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28631 | 105.93 | Potential P4 Event - POI 515375_17 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28768 | 105.43 | 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28771 | 112.81 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28785 | 111.38 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28805 | 110.23 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28807 | 109.64 | 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28811 | 109.51 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2884 | 101.69 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2884 | 101.69 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2885 | 100.87 | 525481 PLANT_X 6 230 525494 PLANT_X4 1 20.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28854 | 104.65 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28861 | 100.75 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28861 | 111.22 | P43:345:SPS:TUCO:SLG::EHV: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2887 | 105.02 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28871 | 102.83 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28882 | 103.04 | P11:115:SPS:HOBBS1&3:145MW:::: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28889 | 101.59 | P11:115:SPS:MUSTANG1&3:153MW:::: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28903 | 100.28 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28908 | 101.65 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28908 | 101.65 | Potential P4 Event - POI 526936_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28908 | 102.47 | Potential P4 Event - POI 526936_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28908 | 102.49 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 116.63 | Potential P4 Event - POI 511468_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.94 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.94 | Potential P4 Event - POI 511456_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.95 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.95 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.95 | Potential P4 Event - POI 511456_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.95 | Potential P4 Event - POI 511456_5 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.95 | Potential P4 Event - POI 762467_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.96 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.96 | Potential P4 Event - POI 511456_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 119.96 | Potential P4 Event - POI 511456_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 120.1 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 120.1 | Potential P4 Event - POI 762467_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 120.11 | Potential P4 Event - POI 762467_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 120.12 | Potential P4 Event - POI 762216_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 120.17 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 120.18 | Potential P4 Event - POI 762216_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29071 | 120.2 | Potential P4 Event - POI 762216_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29413 | 102 | Potential P4 Event - POI 511468_3 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29592 | 120.2 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29592 | 120.2 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29592 | 120.2 | Potential P4 Event - POI 511468_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29612 | 100.2 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29612 | 100.2 | P12:345:OKGE-AEPW:BKRBKR366:::: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.29612 | 100.2 | Potential P4 Event - POI 511468_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.35255 | 103.69 | P13:138-230:AEPW:ELKCTY-4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.35255 | 103.7 | P12:230:AEPW:ELKCITY6:CHISHOLM6 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.48343 | 102.92 | Potential P4 Event - POI 515800_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.48386 | 102.6 | P12:345:OKGE-AEPW:BKRBKR371:::: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.48386 | 102.6 | Potential P4 Event - POI 515800_3 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.48572 | 101.74 | Potential P4 Event - POI 515800_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 1 | 106.68 | P12:230:AEPW:SWEETWT6:CHISHOLM6 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 1 | 107.05 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 1 | 107.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 1 | 107.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6 | TDF Impact | Sweetwater to Chisholm 230 kV Line Rebuild
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.20324 | 102.41 | Potential P4 Event - POI 523961_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.20352 | 101.72 | Potential P4 Event - POI 523097_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.20352 | 101.72 | Potential P4 Event - POI 523097_9 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.22628 | 103.91 | 515458 BORDER 7 345 755000 WWDBORDT 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.22628 | 103.95 | 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.22628 | 103.96 | P42:345:OKGE:SB_BVTY7387:::: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2 | 109.3 | Potential P4 Event - POI 523097_18 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20199 | 106.3 | Potential P4 Event - POI 523961_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20324 | 114.6 | Potential P4 Event - POI 523961_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20352 | 113.83 | Potential P4 Event - POI 523097_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20352 | 113.83 | Potential P4 Event - POI 523097_9 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20363 | 111.39 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20363 | 111.39 | Potential P4 Event - POI 523097_13 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20363 | 111.39 | Potential P4 Event - POI 523097_20 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20363 | 111.4 | Potential P4 Event - POI 523097_16 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 108.05 | Potential P4 Event - POI 511468_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.41 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.41 | Potential P4 Event - POI 511456_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.42 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.42 | P23:345:AEPW:OKLAUNION CB 3401A NBTB | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.42 | Potential P4 Event - POI 511456_4 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.42 | Potential P4 Event - POI 511456_5 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.42 | Potential P4 Event - POI 762467_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.43 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.43 | Potential P4 Event - POI 511456_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.43 | Potential P4 Event - POI 511456_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.55 | Potential P4 Event - POI 762467_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.56 | Potential P4 Event - POI 762216_2 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.56 | Potential P4 Event - POI 762467_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.59 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.6 | Potential P4 Event - POI 762216_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20844 | 109.61 | Potential P4 Event - POI 762216_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20936 | 109.16 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20936 | 109.16 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.20936 | 109.16 | Potential P4 Event - POI 511468_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21196 | 103.82 | 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21217 | 109.8 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.2123 | 108.75 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21233 | 108.04 | 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21237 | 107.92 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21237 | 108.06 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21287 | 101.38 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21297 | 100.36 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21297 | 102.23 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21308 | 100.62 | P11:115:SPS:HOBBS1&3:145MW:::: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21328 | 108.91 | P43:345:SPS:TUCO:SLG::EHV: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21365 | 101.51 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21365 | 101.51 | Potential P4 Event - POI 526936_1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21365 | 102 | Potential P4 Event - POI 526936_0 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.21365 | 102.02 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.22628 | 116.29 | 515458 BORDER 7 345 755000 WWDBORDT 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.22628 | 116.33 | 515458 BORDER 7 345 525832 TUCO_INT 7 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.22628 | 116.34 | P42:345:OKGE:SB_BVTY7387:::: | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.28652 | 105.11 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 1 | 106.59 | P12:230:AEPW:SWEETWT6:CHISHOLM6 | TDF Impact | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 23SP | GEN-2018-071 | FROM->TO | 514901 CIMARON7 345 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.0308 | 104.67 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 23SP | GEN-2018-072 | FROM->TO | 514901 CIMARON7 345 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.0308 | 104.67 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 23SP | GEN-2019-012 | FROM->TO | 514901 CIMARON7 345 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.03706 | 104.67 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03525 | 100.81 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03525 | 100.81 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03525 | 100.81 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03525 | 100.81 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03522 | 104.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03522 | 104.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03522 | 104.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03522 | 104.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03522 | 104.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03522 | 104.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03522 | 104.46 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03522 | 104.46 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-071 | FROM->TO | 514898 CIMARON4 138 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.03059 | 101.72 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-071 | FROM->TO | 514901 CIMARON7 345 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.03059 | 105.65 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-072 | FROM->TO | 514898 CIMARON4 138 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.03059 | 101.72 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-072 | FROM->TO | 514901 CIMARON7 345 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.03059 | 105.65 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2019-012 | FROM->TO | 514898 CIMARON4 138 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.03688 | 101.72 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2019-012 | FROM->TO | 514901 CIMARON7 345 997969 CIMARON1 _1 138 1 | 478 | 478 | 0.03688 | 105.65 | P13:138-345:OKGE:BKRBKR_3W021:::: | TDF Impact | Multi - Minco - Pleasant Valley - Draper 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 100.91 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 100.91 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 102.14 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 102.14 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 100.91 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 100.91 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 102.14 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 102.14 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 100.62 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 100.62 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 100.62 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 121 | 121 | 0.03605 | 100.62 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27784 | 102.1 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27784 | 102.31 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27784 | 102.31 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03603 | 107.83 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03603 | 107.83 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27784 | 102.1 | 652616 MINGUSVILLE4 230 659247 MEDORA__-UM4 230 1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27784 | 102.31 | P12:230:UMZ:# 5531 #: PROPER N-1 (LINE) FOR 659247-652425-1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659151 RICHLAND-BE7 115 661056 LEWIS 7 115 1 | 127 | 127 | 0.27784 | 102.31 | P12:230:UMZB:# 2938 #:: MDR IN ND. LOSS OF MEDORA TAP:HV: | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03603 | 107.83 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03603 | 107.83 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Dawsonc4 to Wiliston 230 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.063 | 106.12 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.06315 | 106.34 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.06315 | 106.34 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.063 | 106.12 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.06315 | 106.34 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.06315 | 106.34 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03603 | 107.83 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03603 | 107.83 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03603 | 107.83 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 120 | 132 | 0.03603 | 107.83 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | TDF Impact | NewBranch Laramervr to Underwood to Maurine to Belfeild 345 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 04NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 04NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 04NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 0 | 23SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 0 | 26SP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 0 | 26WP | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 | 05NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 | 05NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Non-Converge | DISIS-2018-002 / DISIS-2019-001 CF | 05NR | 0 | 26L | N/A | " | Non-Converge |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 05NR | 1 | 26L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.22 | Potential P4 Event - POI 762216_1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.22 | Potential P4 Event - POI 762216_1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.2 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.2 | Potential P4 Event - POI 762216_0 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.2 | Potential P4 Event - POI 762467_0 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.2 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.2 | Potential P4 Event - POI 762216_0 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.2 | Potential P4 Event - POI 762467_0 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.19 | Potential P4 Event - POI 762216_2 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.19 | Potential P4 Event - POI 762216_2 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.18 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.18 | Potential P4 Event - POI 762467_2 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.18 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.18 | Potential P4 Event - POI 762467_2 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.12 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.12 | Potential P4 Event - POI 511456_1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.12 | Potential P4 Event - POI 511456_2 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.12 | Potential P4 Event - POI 511456_5 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.12 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.12 | Potential P4 Event - POI 511456_1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.12 | Potential P4 Event - POI 511456_2 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.12 | Potential P4 Event - POI 511456_5 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | Potential P4 Event - POI 511456_0 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | Potential P4 Event - POI 511456_4 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | Potential P4 Event - POI 762467_1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | P12:345:AEPW:O.K.U.-7:L.E.S.-7 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | P23:345:AEPW:OKLAUNION CB 3401A NBTB |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | Potential P4 Event - POI 511456_0 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | Potential P4 Event - POI 511456_4 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.2771 | 102.11 | Potential P4 Event - POI 762467_1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.28288 | 101.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.28288 | 101.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.28288 | 101.97 | Potential P4 Event - POI 511468_1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.28288 | 101.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.28288 | 101.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.28288 | 101.97 | Potential P4 Event - POI 511468_1 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.26556 | 101.94 | Potential P4 Event - POI 515375_45 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.26556 | 101.94 | Potential P4 Event - POI 560071_0 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.26556 | 101.94 | Potential P4 Event - POI 515375_45 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 459 | 459 | 0.26556 | 101.94 | Potential P4 Event - POI 560071_0 |  | Multi - Border - Woodward 345 kV Tap
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2019-039 | FROM->TO | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 125.49 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | TDF Impact | Rebuild Rising to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26SP | GEN-2019-039 | FROM->TO | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 125.68 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | TDF Impact | Rebuild Rising to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-039 | FROM->TO | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 124.95 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | TDF Impact | Rebuild Rising to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2019-039 | FROM->TO | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 122.26 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | TDF Impact | Rebuild Columbus SE to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26SP | GEN-2019-039 | FROM->TO | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 122.26 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | TDF Impact | Rebuild Columbus SE to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2019-039 | FROM->TO | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 140 | 140 | 1 | 122.3 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | TDF Impact | Rebuild Columbus SE to G19-039-TAP 115 kV
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.02 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 23SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996912 ANTELOPE T1 115 1 | 417 | 417 | 1 | 101.02 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996909 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.82 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996909 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.82 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996907 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.35 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)
Thermal | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 1 | 26WP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996907 ANTELOPE T1 115 1 | 417 | 417 | 1 | 100.35 | 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | Antelope - Holt County 345 kV Ckt 1 New Line (2024 ITP)

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 01ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 01NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 01ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 01NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2018-108 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.20331 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2018-116 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.03931 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-001 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.353 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-030 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.12698 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-044 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.11129 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-051 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.03931 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-053 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.07982 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-055 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.07982 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-058 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.14088 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-063 | 539801 THISTLE7 345 | 0.9719 | 0.9244 | -0.048873 |  | 0.95 | 1.05 | 0.14088 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2018-108 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.20331 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2018-116 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.03931 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-001 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.353 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-030 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.12698 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-044 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.11129 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-051 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.03931 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-053 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.07982 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-055 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.07982 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-058 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.14088 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-063 | 532782 BUFFALO7 345 | 0.9774 | 0.9343 | -0.044097 |  | 0.95 | 1.05 | 0.14088 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2018-108 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.20331 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2018-116 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.03931 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-001 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.353 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-030 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.12698 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-044 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.11129 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-051 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.03931 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-053 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.07982 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-055 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.07982 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-058 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.14088 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 23SP | GEN-2019-063 | 760284 GEN-2017-220 345 | 0.9775 | 0.9344 | -0.044092 |  | 0.95 | 1.05 | 0.14088 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2018-108 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.20183 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2018-116 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.03866 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-001 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.35366 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-030 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.1255 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-044 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.10976 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-051 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.03866 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-053 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.07872 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-055 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.07872 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-058 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.1394 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-063 | 539801 THISTLE7 345 | 0.9753 | 0.94 | -0.036194 |  | 0.95 | 1.05 | 0.1394 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2018-108 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.20183 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2018-116 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.03866 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-001 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.35366 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-030 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.1255 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-044 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.10976 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-051 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.03866 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-053 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.07872 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-055 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.07872 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-058 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.1394 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-063 | 532782 BUFFALO7 345 | 0.9791 | 0.9497 | -0.030028 |  | 0.95 | 1.05 | 0.1394 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2018-108 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.20183 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2018-116 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.03866 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-001 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.35366 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-030 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.1255 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-044 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.10976 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-051 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.03866 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-053 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.07872 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-055 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.07872 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-058 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.1394 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26SP | GEN-2019-063 | 760284 GEN-2017-220 345 | 0.9792 | 0.9498 | -0.030025 |  | 0.95 | 1.05 | 0.1394 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2018-108 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.20065 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2018-116 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.03748 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-001 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.35248 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-030 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.12432 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-044 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.10858 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-051 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.03748 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-053 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.07754 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-055 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.07754 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-058 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.13822 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-063 | 539801 THISTLE7 345 | 0.9695 | 0.9091 | -0.0623 |  | 0.95 | 1.05 | 0.13822 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2018-108 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.20065 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2018-116 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.03748 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-001 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.35248 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-030 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.12432 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-044 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.10858 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-051 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.03748 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-053 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.07754 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-055 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.07754 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-058 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.13822 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-063 | 532782 BUFFALO7 345 | 0.9762 | 0.916 | -0.061668 |  | 0.95 | 1.05 | 0.13822 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2018-108 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.20065 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2018-116 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.03748 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-001 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.35248 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-030 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.12432 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-044 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.10858 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-051 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.03748 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-053 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.07754 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-055 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.07754 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-058 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.13822 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-063 | 760284 GEN-2017-220 345 | 0.9763 | 0.9161 | -0.061661 |  | 0.95 | 1.05 | 0.13822 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2018-108 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.20065 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2018-116 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.03748 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-001 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.35248 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-030 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.12432 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-044 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.10858 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-051 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.03748 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-053 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.07754 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-055 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.07754 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-058 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.13822 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26WP | GEN-2019-063 | 532783 KINGMAN7 345 | 1.005 | 0.9499 | -0.054826 |  | 0.95 | 1.05 | 0.13822 | PROXY_P4_345kV_POI 532782_5 | Switch Out Thistle Line Reactor Circuit 1
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 03NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 02ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 02NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 03ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 03NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 02ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 02NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 04ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 04NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 04ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 04NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 05ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 05NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 05ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 05NR | 2 | 26L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 00ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 00ALL | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 00NR | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 00NR | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 | 00NR | 2 | 26WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 2 | 23SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2018-002 / DISIS-2019-001 CF | 00NR | 2 | 26WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips OAKTREE WIND (660013). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_019 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on PLNTYWD7 115.00 (661077) 115 kV Bus a. Apply fault at the PLNTYWD7 115.00 (661077) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLNTYWD7 (661077) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on LTL SIOUX 5 161.00 (635360) 161 kV Bus a. Apply fault at the LTL SIOUX 5 161.00 (635360) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.2. CLIPPER5 (635350) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.3. LTL SIOUX 5 (635360) 161.0 kV to LTL SIOUX 8 (635361) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON1AG (608891), BISON 4G (608894), BISON5BG (608895), BISON1BG (608897) and BISON5AG (608898). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G287 NOB4G W (600114) and G287 NOB2G W (600112). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on LKFLDXL3 345.00 (601029) 345 kV Bus a. Apply fault at the LKFLDXL3 345.00 (601029) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LKFLDXL3 (601029) 345.0 kV to CRANDAL 3 (601074) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on TERRY TAP 115.00 (652394) 115 kV Bus a. Apply fault at the TERRY TAP 115.00 (652394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.3. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on ABERDN JCT 7115.00 (660000) 115 kV Bus a. Apply fault at the ABERDN JCT 7115.00 (660000) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_129 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_130 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | No | Yes | No | No | Simulation crashes due to oscillations from PS_RCP.B-BEG (659432 and 659431). Disabling the dynamic controller model allows the simulation to reach the end following which oscilations are observed at GEN-2018-067 (763024 and 763027) generating site. The following CQ unit was determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_132 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_133 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | No | Yes | No | Yes | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. The following CQ unit were determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_135 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_136 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_137 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_138 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_139 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_140 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_141 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_142 | 3 Phase fault on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_143 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN-LNX3 (652829) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_144 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_145 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_146 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_147 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_148 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_149 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_150 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_151 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_152 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_153 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_154 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_155 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_156 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_157 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_158 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_161 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_162 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_166 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_167 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_168 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_169 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_170 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_171 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_172 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_173 | 3 Phase fault on LOGANPK8 69.000 (635245) 69 kV Bus a. Apply fault at the LOGANPK8 69.000 (635245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGANPK8 (635245) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_174 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_175 | 3 Phase fault on LEMARS S 8 69.000 (635262) 69 kV Bus a. Apply fault at the LEMARS S 8 69.000 (635262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARS S 8 (635262) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_176 | 3 Phase fault on MERRIL 8 69.000 (635393) 69 kV Bus a. Apply fault at the MERRIL 8 69.000 (635393) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIL 8 (635393) 69.0 kV to MERRILN8 (635394) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_178 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_179 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_180 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_181 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_182 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_183 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_184 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_185 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_186 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_187 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_188 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to FERNEY-ER8 (655256) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_189 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON-ER8 (655267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_190 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_191 | 3 Phase fault on GROTON2 869.000 (652253) 69 kV Bus a. Apply fault at the GROTON2 869.000 (652253) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON (660430) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_192 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_193 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_194 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_195 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_196 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_197 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_198 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_199 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_200 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_201 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_202 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_203 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_204 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_205 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_206 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_207 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_208 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_209 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_210 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_211 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_212 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_213 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_214 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_215 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_216 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_217 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_218 | 3 Phase fault on SUMMIT-7 115.00 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 115.00 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_219 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_220 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_221 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_222 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_223 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_224 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_225 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_226 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_227 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_228 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_229 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_230 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_231 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_233 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_234 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_235 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_236 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_237 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_238 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_239 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_240 | 3 Phase fault on MOS-RDFL-ER869.000 (655054) 69 kV Bus a. Apply fault at the MOS-RDFL-ER869.000 (655054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RDFL-ER8 (655054) 69.0 kV to REDFELD-ER8 (655482) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_241 | 3 Phase fault on MOS-ASHT-ER869.000 (655059) 69 kV Bus a. Apply fault at the MOS-ASHT-ER869.000 (655059) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ASHT-ER8 (655059) 69.0 kV to REDFELD-ER8 (655482) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_242 | 3 Phase fault on MOS-CLRM-ER869.000 (655082) 69 kV Bus a. Apply fault at the MOS-CLRM-ER869.000 (655082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CLRM-ER8 (655082) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_243 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_244 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_245 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_246 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_247 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_248 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_249 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_250 | 3 Phase fault on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_251 | 3 Phase fault on BATH-ER8 69.000 (655269) 69 kV Bus a. Apply fault at the BATH-ER8 69.000 (655269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATH-ER8 (655269) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_252 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_253 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_254 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_255 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_256 | 3 Phase fault on MARLEY -LY7115.00 (655793) 115 kV Bus a. Apply fault at the MARLEY -LY7115.00 (655793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLEY -LY7 (655793) 115.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_257 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_258 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_259 | 3 Phase fault on OAKDALE -MK7115.00 (655836) 115 kV Bus a. Apply fault at the OAKDALE -MK7115.00 (655836) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKDALE -MK7 (655836) 115.0 kV to BEARCREK-MK7 (655853) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_260 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_261 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_262 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_263 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_264 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_265 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_266 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_267 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_268 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_269 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_270 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_271 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_272 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_273 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_274 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_275 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_276 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_277 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_278 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_279 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_280 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_281 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_282 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_283 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_284 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to 32STREET-RR7 (659442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_285 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to PRNGHORN-RR7 (659544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_286 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_287 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_288 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_289 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_290 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_291 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_292 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_293 | 3 Phase fault on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_294 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_295 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_296 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_297 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_298 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_299 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_300 | 3 Phase fault on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_301 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_302 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_303 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_304 | 3 Phase fault on J12_____-NI869.000 (659918) 69 kV Bus a. Apply fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J12_____-NI8 (659918) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_305 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_306 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_307 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_308 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_309 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_310 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_311 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_312 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_313 | 3 Phase fault on FALLON 7 115.00 (652407) 115 kV Bus a. Apply fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_314 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_315 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_316 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_317 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_318 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_319 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_320 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_321 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_322 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_323 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_324 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_325 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_326 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_327 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_328 | 3 Phase fault on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_329 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_330 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_331 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_332 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_333 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_334 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_335 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_336 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_337 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_338 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_339 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_340 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_341 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_342 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_343 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_344 | 3 Phase fault on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_345 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_346 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_347 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_348 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_349 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_350 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_351 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_352 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_353 | 3 Phase fault on BEAVRHIL-GW4230.00 (659535) 230 kV Bus a. Apply fault at the BEAVRHIL-GW4230.00 (659535) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVRHIL-GW4 (659535) 230.0 kV to BEAVRHIL-GW7 (659536) 115.0 kV to BEAVRHIL-GW9 (659537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_354 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_355 | 3 Phase fault on BAKER 4 230.00 (661004) 230 kV Bus a. Apply fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_356 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_357 | 3 Phase fault on MI CTYW4 230.00 (652402) 230 kV Bus a. Apply fault at the MI CTYW4 230.00 (652402) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYW4 (652402) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_358 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_359 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_360 | 3 Phase fault on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE7 (652412) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_361 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_362 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_363 | 3 Phase fault on REDFELD-ER8 69.000 (655482) 69 kV Bus a. Apply fault at the REDFELD-ER8 69.000 (655482) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER8 (655482) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_364 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_365 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_366 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.3. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply Fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.5. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.6. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LEWIS 7 115.00 (661056) 115 kV Bus a. Apply Fault at the LEWIS 7 115.00 (661056) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.2. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.3. LEWIS 7 (661056) 115.0 kV to LEWIS71G (661055) 13.8 kV Two Winding #1 b.4. LEWIS 7 (661056) 115.0 kV to LEWIS72G (661104) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z b.5. BEULAH 7 (661008) 115.0 kV to COYOTE 7 (661018) 115.0 kV Transmission Circuit #1 b.6. BEULAH 7 (661008) 115.0 kV to COYOTETAP 7 (661057) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply Fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 b.3. GLENDCT7 (661032) 115.0 kV to Load #Y0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 b.3. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.4. GLENDCT7 (661032) 115.0 kV to GLNDCT1G (661100) 13.8 kV Two Winding #1 b.5. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply Fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.4. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.5. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.6. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.7. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.8. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.9. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.10. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.4. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply Fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on GU CTR 5 161.00 (631072) 161 kV Bus a. Apply Fault at the GU CTR 5 161.00 (631072) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.3. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #1 b.4. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #2 b.5. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.6. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.7. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.8. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.9. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.10. SCRANTN5 (631071) 161.0 kV to SCRANTN9 (629111) 34.5 kV Two Winding #1 b.11. SCRANTN5 (631071) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.12. SCRANTN5 (631071) 161.0 kV to GR JCT 5 (631074) 161.0 kV Transmission Circuit #1 b.13. GU CTR 5 (631072) 161.0 kV to GU CTR 9 (629113) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply Fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.3. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to None Three Winding #1 b.4. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 b.5. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 b.3. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.4. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.5. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply Fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.4. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.5. EDGELEY 19 (652328) 13.2 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.2. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.3. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.4. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.5. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.6. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.6. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7 115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7 115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to Load #BB b.6. GARRISN7 (652442) 115.0 kV to Load #BW b.7. GARRISN7 (652442) 115.0 kV to Load #R0 b.8. GARRISN7 (652442) 115.0 kV to Load #W0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. EXIRA 5 (652603) 161.0 kV to EXIRA 2G (658001) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.11. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 b.7. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply Fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | No | Yes | No | Yes | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. The following CQ unit were determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | No | Yes | No | Yes | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. The following CQ unit were determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on FORTUNA -SH7115.00 (655777) 115 kV Bus a. Apply Fault at the FORTUNA -SH7115.00 (655777) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 b.2. FORTUNA -SH7 (655777) 115.0 kV to AMBROSE -BD7 (655784) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.5. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.7. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.8. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.9. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply Fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 b.4. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. BROOKS 5 (635037) 161.0 kV to ADAMS 5 (635056) 161.0 kV Transmission Circuit #1 b.5. ADAMS 5 (635056) 161.0 kV to ADAMS B1 9 (635057) 34.5 kV Two Winding #1 b.6. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.7. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. NBCS_10_-PPR (659278) 12.5 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.3. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 b.3. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.9. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 b.10. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.10. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on HOSPERS8 69.000 (635371) 69 kV Bus a. Apply Fault at the HOSPERS8 69.000 (635371) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSPERS8 (635371) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 b.2. HOSPERS8 (635371) 69.0 kV to SHELDON8 (635370) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply Fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCKVALY8 (635380) 69.0 kV to DOONTAP8 (635377) 69.0 kV Transmission Circuit #1 b.2. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on RKVALTT8 69.000 (635381) 69 kV Bus a. Apply Fault at the RKVALTT8 69.000 (635381) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RKVALTT8 (635381) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 b.2. RKVALTT8 (635381) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on INWOODT8 69.000 (635383) 69 kV Bus a. Apply Fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 b.2. INWOODT8 (635383) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply Fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. HUDSON 8 (635385) 69.0 kV to INWOODT8 (635383) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on IRETONT8 69.000 (635391) 69 kV Bus a. Apply Fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. IRETONT8 (635391) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z2 b.2. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. DENISON8 (652583) 69.0 kV to DENISON4 (652567) 230.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply Fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply Fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply Fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 b.2. TEMPLTON8 (656247) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on DENISONWEST869.000 (658030) 69 kV Bus a. Apply Fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on L6OC E MUNI869.000 (658904) 69 kV Bus a. Apply Fault at the L6OC E MUNI869.000 (658904) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L6OC E MUNI8 (658904) 69.0 kV to L7OC W MUNI8 (658906) 69.0 kV Transmission Circuit #1 b.2. L6OC E MUNI8 (658904) 69.0 kV to L14OCINDMUN8 (658903) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on L7OC W MUNI869.000 (658906) 69 kV Bus a. Apply Fault at the L7OC W MUNI869.000 (658906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L7OC W MUNI8 (658906) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 b.2. L7OC W MUNI8 (658906) 69.0 kV to L6OC E MUNI8 (658904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply Fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 b.2. K125DUNL-NI8 (659853) 69.0 kV to K126MEC -NI8 (659852) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply Fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply Fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 b.2. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply Fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply Fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K307DENI-NI8 (659862) 69.0 kV Transmission Circuit #1 b.2. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply Fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on K228WSTB-NI869.000 (659896) 69 kV Bus a. Apply Fault at the K228WSTB-NI869.000 (659896) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K228WSTB-NI8 (659896) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 b.2. K228WSTB-NI8 (659896) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to EAGLE___-NI4 (659900) 230.0 kV Two Winding #2 b.2. EAGLE___-NI8 (659901) 69.0 kV to EAGLE___-NI4 (659900) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on L1______-NI869.000 (659902) 69 kV Bus a. Apply Fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on L3______-NI869.000 (659904) 69 kV Bus a. Apply Fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L3______-NI8 (659904) 69.0 kV to K228WSTB-NI8 (659896) 69.0 kV Transmission Circuit #1 b.2. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on L8______-NI869.000 (659905) 69 kV Bus a. Apply Fault at the L8______-NI869.000 (659905) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L8______-NI8 (659905) 69.0 kV to L7OC W MUNI8 (658906) 69.0 kV Transmission Circuit #1 b.2. L8______-NI8 (659905) 69.0 kV to K228WSTB-NI8 (659896) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. J6BOYER_-NI8 (659912) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on J12_____-NI869.000 (659918) 69 kV Bus a. Apply Fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J12_____-NI8 (659918) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. J12_____-NI8 (659918) 69.0 kV to K125DUNL-NI8 (659853) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J15_____-NI8 (659921) 69.0 kV to L4SXCTNMUNI8 (658900) 69.0 kV Transmission Circuit #1 b.2. J15_____-NI8 (659921) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on K202PRES-NI869.000 (659944) 69 kV Bus a. Apply Fault at the K202PRES-NI869.000 (659944) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K202PRES-NI8 (659944) 69.0 kV to K226MERR-NI8 (659945) 69.0 kV Transmission Circuit #1 b.2. K202PRES-NI8 (659944) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on K214____-NI869.000 (659948) 69 kV Bus a. Apply Fault at the K214____-NI869.000 (659948) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K214____-NI8 (659948) 69.0 kV to K211SENY-NI8 (659949) 69.0 kV Transmission Circuit #1 b.2. K214____-NI8 (659948) 69.0 kV to K221ALTO-NI8 (659947) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply Fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 b.2. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.2. FTTHOM2-LNX3 (652807) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply Fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.2. AV.LS-BD-BE3 (659420) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply Fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #1 b.2. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND-BE3 (659120) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply Fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 b.2. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on K213HOSP-NI869.000 (659955) 69 kV Bus a. Apply Fault at the K213HOSP-NI869.000 (659955) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K213HOSP-NI8 (659955) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 b.2. K213HOSP-NI8 (659955) 69.0 kV to HOSPERS8 (635371) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on K218ROCK-NI869.000 (659977) 69 kV Bus a. Apply Fault at the K218ROCK-NI869.000 (659977) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K218ROCK-NI8 (659977) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. K218ROCK-NI8 (659977) 69.0 kV to RKVALTT8 (635381) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTON__-BE3 (659160) 345.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on MANNINGTAP 869.000 (656267) 69 kV Bus a. Apply Fault at the MANNINGTAP 869.000 (656267) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANNINGTAP 8 (656267) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. MANNINGTAP 8 (656267) 69.0 kV to TEMPLTON8 (656247) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on DENSOUMAIN8 69.000 (658031) 69 kV Bus a. Apply Fault at the DENSOUMAIN8 69.000 (658031) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENSOUMAIN8 (658031) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENSOUMAIN8 (658031) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply Fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSBORN -MW7 (655919) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.2. OSBORN -MW7 (655919) 115.0 kV to E.NEWTWN-MW7 (655907) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on K338WTCT-NI869.000 (659897) 69 kV Bus a. Apply Fault at the K338WTCT-NI869.000 (659897) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K338WTCT-NI8 (659897) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 b.2. K338WTCT-NI8 (659897) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on K308EARL-NI869.000 (659856) 69 kV Bus a. Apply Fault at the K308EARL-NI869.000 (659856) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K308EARL-NI8 (659856) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 b.2. K308EARL-NI8 (659856) 69.0 kV to K321MEC -NI8 (659857) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on K317MANN-NI869.000 (659906) 69 kV Bus a. Apply Fault at the K317MANN-NI869.000 (659906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K317MANN-NI8 (659906) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 b.2. K317MANN-NI8 (659906) 69.0 kV to K330MANM-NI8 (659864) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on K326OTTE-NI869.000 (659886) 69 kV Bus a. Apply Fault at the K326OTTE-NI869.000 (659886) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K326OTTE-NI8 (659886) 69.0 kV to K306SCHL-NI8 (659885) 69.0 kV Transmission Circuit #1 b.2. K326OTTE-NI8 (659886) 69.0 kV to K333SCHL-NI8 (659887) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on K217HWDN-NI869.000 (659942) 69 kV Bus a. Apply Fault at the K217HWDN-NI869.000 (659942) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K217HWDN-NI8 (659942) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. K217HWDN-NI8 (659942) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply Fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K222HULL-NI8 (659941) 69.0 kV to L4SXCTNMUNI8 (658900) 69.0 kV Transmission Circuit #1 b.2. K222HULL-NI8 (659941) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on K207OC N-NI869.000 (659943) 69 kV Bus a. Apply Fault at the K207OC N-NI869.000 (659943) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K207OC N-NI8 (659943) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 b.2. K207OC N-NI8 (659943) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply Fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K223SIOU-NI8 (659940) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. K223SIOU-NI8 (659940) 69.0 kV to L5SXCTWMUNI8 (658902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on K106CHAR-NI869.000 (659999) 69 kV Bus a. Apply Fault at the K106CHAR-NI869.000 (659999) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K106CHAR-NI8 (659999) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 b.2. K106CHAR-NI8 (659999) 69.0 kV to K105UTE_-NI8 (659998) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on K226MERR-NI869.000 (659945) 69 kV Bus a. Apply Fault at the K226MERR-NI869.000 (659945) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K226MERR-NI8 (659945) 69.0 kV to K225ADAV-NI8 (659899) 69.0 kV Transmission Circuit #1 b.2. K226MERR-NI8 (659945) 69.0 kV to K202PRES-NI8 (659944) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MONT -MW7 115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7 115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to remove bus # | P4 | No | Yes | Yes | No | Yes | No | Yes | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. The following CQ unit were determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7 115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7 115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply Fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on DENISON8 69.00 (652583) 69 kV Bus a. Apply Fault at the DENISON8 69.00 (652583) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI8 69.00 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI8 69.00 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on EAGLE___-NI8 69.00 (659901) 69 kV Bus a. Apply Fault at the EAGLE___-NI8 69.00 (659901) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on J1CENTER-NI8 69.00 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI8 69.00 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on L1______-NI8 69.00 (659902) 69 kV Bus a. Apply Fault at the L1______-NI8 69.00 (659902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L1______-NI8 (659902) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3 345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3 345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BROWNSV4 230.00 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 230.00 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on ASTORIA 3 345.00 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 345.00 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #1 b.2. ASTORIA 3 (620483) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_001 | Single Phase Fault with Stuck Breaker on AVS 345 (659420) 345 kV Bus a. Apply Fault at the AVS 345 (659420) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to remove bus #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to Load #BB b.3. COTEAU_1-RR8 (659222) 69.0 kV to Load #BW b.4. DGC UREA-BE8 (659236) 69.0 kV to Load #BG b.5. COTEAU 1-RR9 (659219) 13.8 kV to remove bus # b.6. COTEAU 2-RR9 (659231) 13.8 kV to remove bus # b.7. COTEAU_1-RR8 (659222) 69.0 kV to remove bus # b.8. COTEAU__-RR3 (659218) 345.0 kV to remove bus # b.9. DGC UREA-BE8 (659236) 69.0 kV to remove bus # b.10. AV.LS-BD-BE3 (659420) 345.0 kV to remove bus # b.11. AV.LS-BD-BE3 (659420) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_002 | Single Phase Fault with Stuck Breaker on LOS 345 (659424) 345 kV Bus a. Apply Fault at the LOS 345 (659424) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #Z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to Switched Shunt Device # b.3. CC.LS-LO-BE3 (659428) 345.0 kV to Switched Shunt Device # b.4. LELAND_2-BEG (659111) 20.0 kV to Load #S0 b.5. LELAND_2-BEG (659111) 20.0 kV to Generator #2 b.6. LELAND_2-BEG (659111) 20.0 kV to remove bus # b.7. CC.LS-LO-BE3 (659428) 345.0 kV to remove bus # b.8. LO.LS-FT-BE3 (659424) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_003 | Single Phase Fault with Stuck Breaker on LOS 345 (659422) 345 kV Bus a. Apply Fault at the LOS 345 (659422) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #Z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to Switched Shunt Device # b.3. LO.LS-GR-BE3 (659422) 345.0 kV to Switched Shunt Device # b.4. LO.KU1A_-BE9 (659201) 13.8 kV to Switched Shunt Device # b.5. LO.LS-GR-BE3 (659422) 345.0 kV to remove bus # b.6. GR.LS-LO-BE3 (659423) 345.0 kV to remove bus # b.7. LO.KU1A_-BE9 (659201) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_004 | Single Phase Fault with Stuck Breaker on LOS 230 (659106) 230 kV Bus a. Apply Fault at the LOS 230 (659106) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to Load #BB b.3. BASIN___-BE7 (659109) 115.0 kV to Load #BW b.4. BASIN___-BE7 (659109) 115.0 kV to Load #W0 b.5. LELAND_1-BEG (659110) 22.0 kV to Load #S0 b.6. LELAND_1-BEG (659110) 22.0 kV to Generator #1 b.7. NEWSALEM-MG7 (655748) 115.0 kV to Load #BB b.8. NEWSALEM-MG7 (655748) 115.0 kV to Load #BW b.9. ROUGHRDR-MG7 (655750) 115.0 kV to Load #BB b.10. ROUGHRDR-MG7 (655750) 115.0 kV to Load #BW b.11. NRWSTMDN-MG7 (655751) 115.0 kV to Load #BB b.12. NRWSTMDN-MG7 (655751) 115.0 kV to Load #BW b.13. DEVAUL -MG8 (655746) 69.0 kV to Load #W0 b.14. CANNON -MG8 (655740) 69.0 kV to Load #BB b.15. CANNON -MG8 (655740) 69.0 kV to Load #BW b.16. CEDAR -MG8 (655741) 69.0 kV to Load #BB b.17. CEDAR -MG8 (655741) 69.0 kV to Load #BW b.18. GRANT -MG8 (655742) 69.0 kV to Load #BB b.19. GRANT -MG8 (655742) 69.0 kV to Load #BW b.20. FLASHER -MG8 (655732) 69.0 kV to Load #BB b.21. FLASHER -MG8 (655732) 69.0 kV to Load #BW b.22. LO.KU1A_-BE9 (659201) 13.8 kV to remove bus # b.23. LO.KVA2_-BE9 (659202) 13.8 kV to remove bus # b.24. BAL.KY1A-BE9 (659200) 13.8 kV to remove bus # b.25. LELAND_O-BE4 (659106) 230.0 kV to remove bus # b.26. BASIN___-BE7 (659109) 115.0 kV to remove bus # b.27. BASIN___-BE4 (659199) 230.0 kV to remove bus # b.28. LELAND_1-BEG (659110) 22.0 kV to remove bus # b.30. NEWSALEM-MG7 (655748) 115.0 kV to remove bus # b.31. MANSWTCH-MG7 (655749) 115.0 kV to remove bus # b.32. ROUGHRDR-MG7 (655750) 115.0 kV to remove bus # b.33. NRWSTMDN-MG7 (655751) 115.0 kV to remove bus # b.34. NWMDNTAP-MG7 (655752) 115.0 kV to remove bus # b.35. DEVAUL -MG8 (655746) 69.0 kV to remove bus # b.36. DEVALTP -MG8 (655744) 69.0 kV to remove bus # b.37. DEVAUL 8 (652257) 69.0 kV to remove bus # b.38. LARK -MG8 (655731) 69.0 kV to remove bus # b.39. CANNON -MG8 (655740) 69.0 kV to remove bus # b.40. CEDAR -MG8 (655741) 69.0 kV to remove bus # b.41. GRANT -MG8 (655742) 69.0 kV to remove bus # b.42. FLASHER -MG8 (655732) 69.0 kV to remove bus # b.44. DEVAUL -MG7 (655747) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_005 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_006 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_007 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CCR.KV4A-BE9 (659319) 13.8 kV to remove bus # b.3. CCR.KV3A-BE9 (659318) 13.8 kV to remove bus # b.4. CHARL_CK-BE4 (659302) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_008 | Single Phase Fault with Stuck Breaker on JDS 345 (659333) 345 kV Bus a. Apply Fault at the JDS 345 (659333) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to remove bus # b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips OAKTREE WIND (660013). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_019 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on PLNTYWD7 115.00 (661077) 115 kV Bus a. Apply fault at the PLNTYWD7 115.00 (661077) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLNTYWD7 (661077) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on LTL SIOUX 5 161.00 (635360) 161 kV Bus a. Apply fault at the LTL SIOUX 5 161.00 (635360) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.2. CLIPPER5 (635350) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.3. LTL SIOUX 5 (635360) 161.0 kV to LTL SIOUX 8 (635361) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON1AG (608891), BISON 4G (608894), BISON5BG (608895), BISON1BG (608897) and BISON5AG (608898). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G287 NOB4G W (600114) and G287 NOB2G W (600112). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on LKFLDXL3 345.00 (601029) 345 kV Bus a. Apply fault at the LKFLDXL3 345.00 (601029) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LKFLDXL3 (601029) 345.0 kV to CRANDAL 3 (601074) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on TERRY TAP 115.00 (652394) 115 kV Bus a. Apply fault at the TERRY TAP 115.00 (652394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.3. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on ABERDN JCT 7115.00 (660000) 115 kV Bus a. Apply fault at the ABERDN JCT 7115.00 (660000) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_129 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_130 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | No | Yes | No | No | Simulation crashes due to oscillations from PS_RCP.B-BEG (659432 and 659431). Disabling the dynamic controller model allows the simulation to reach the end following which oscilations are observed at GEN-2018-067 (763024 and 763027) generating site. The following CQ unit was determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_132 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_133 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | No | Yes | No | Yes | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. The following CQ unit were determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_135 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_136 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_137 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_138 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_139 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_140 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_141 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_142 | 3 Phase fault on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_143 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN-LNX3 (652829) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_144 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_145 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_146 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_147 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_148 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_149 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_150 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_151 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_152 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_153 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_154 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_155 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_156 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_157 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_158 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_161 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_162 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_166 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_167 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_168 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_169 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_170 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_171 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_172 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_173 | 3 Phase fault on LOGANPK8 69.000 (635245) 69 kV Bus a. Apply fault at the LOGANPK8 69.000 (635245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGANPK8 (635245) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_174 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_175 | 3 Phase fault on LEMARS S 8 69.000 (635262) 69 kV Bus a. Apply fault at the LEMARS S 8 69.000 (635262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARS S 8 (635262) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_176 | 3 Phase fault on MERRIL 8 69.000 (635393) 69 kV Bus a. Apply fault at the MERRIL 8 69.000 (635393) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIL 8 (635393) 69.0 kV to MERRILN8 (635394) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_178 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_179 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_180 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_181 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_182 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_183 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_184 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_185 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_186 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_187 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_188 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to FERNEY-ER8 (655256) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_189 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON-ER8 (655267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_190 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_191 | 3 Phase fault on GROTON2 869.000 (652253) 69 kV Bus a. Apply fault at the GROTON2 869.000 (652253) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON (660430) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_192 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_193 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_194 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_195 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_196 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_197 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_198 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_199 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_200 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_201 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_202 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_203 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_204 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_205 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_206 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_207 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_208 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_209 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_210 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_211 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_212 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_213 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_214 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_215 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_216 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_217 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_218 | 3 Phase fault on SUMMIT-7 115.00 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 115.00 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_219 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_220 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_221 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_222 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_223 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_224 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_225 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_226 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_227 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_228 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_229 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_230 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_231 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_233 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_234 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_235 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_236 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_237 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_238 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_239 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_240 | 3 Phase fault on MOS-RDFL-ER869.000 (655054) 69 kV Bus a. Apply fault at the MOS-RDFL-ER869.000 (655054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RDFL-ER8 (655054) 69.0 kV to REDFELD-ER8 (655482) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_241 | 3 Phase fault on MOS-ASHT-ER869.000 (655059) 69 kV Bus a. Apply fault at the MOS-ASHT-ER869.000 (655059) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ASHT-ER8 (655059) 69.0 kV to REDFELD-ER8 (655482) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_242 | 3 Phase fault on MOS-CLRM-ER869.000 (655082) 69 kV Bus a. Apply fault at the MOS-CLRM-ER869.000 (655082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CLRM-ER8 (655082) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_243 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_244 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_245 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_246 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_247 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_248 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_249 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_250 | 3 Phase fault on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_251 | 3 Phase fault on BATH-ER8 69.000 (655269) 69 kV Bus a. Apply fault at the BATH-ER8 69.000 (655269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATH-ER8 (655269) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_252 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_253 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_254 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_255 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_256 | 3 Phase fault on MARLEY -LY7115.00 (655793) 115 kV Bus a. Apply fault at the MARLEY -LY7115.00 (655793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLEY -LY7 (655793) 115.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_257 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_258 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_259 | 3 Phase fault on OAKDALE -MK7115.00 (655836) 115 kV Bus a. Apply fault at the OAKDALE -MK7115.00 (655836) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKDALE -MK7 (655836) 115.0 kV to BEARCREK-MK7 (655853) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_260 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_261 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_262 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_263 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_264 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_265 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_266 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_267 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_268 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_269 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_270 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_271 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_272 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_273 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_274 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_275 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_276 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_277 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_278 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_279 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_280 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_281 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_282 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_283 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_284 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to 32STREET-RR7 (659442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_285 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to PRNGHORN-RR7 (659544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_286 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_287 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_288 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_289 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_290 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_291 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_292 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_293 | 3 Phase fault on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_294 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_295 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_296 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_297 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_298 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_299 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_300 | 3 Phase fault on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_301 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_302 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_303 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_304 | 3 Phase fault on J12_____-NI869.000 (659918) 69 kV Bus a. Apply fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J12_____-NI8 (659918) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_305 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_306 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_307 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_308 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_309 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_310 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_311 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_312 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_313 | 3 Phase fault on FALLON 7 115.00 (652407) 115 kV Bus a. Apply fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_314 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_315 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_316 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_317 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_318 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_319 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_320 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_321 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_322 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_323 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_324 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_325 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_326 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_327 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_328 | 3 Phase fault on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_329 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_330 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_331 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_332 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_333 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_334 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_335 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_336 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_337 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_338 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_339 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_340 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_341 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_342 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_343 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_344 | 3 Phase fault on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_345 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_346 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_347 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_348 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_349 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_350 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_351 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_352 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_353 | 3 Phase fault on BEAVRHIL-GW4230.00 (659535) 230 kV Bus a. Apply fault at the BEAVRHIL-GW4230.00 (659535) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVRHIL-GW4 (659535) 230.0 kV to BEAVRHIL-GW7 (659536) 115.0 kV to BEAVRHIL-GW9 (659537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_354 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_355 | 3 Phase fault on BAKER 4 230.00 (661004) 230 kV Bus a. Apply fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_356 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_357 | 3 Phase fault on MI CTYW4 230.00 (652402) 230 kV Bus a. Apply fault at the MI CTYW4 230.00 (652402) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYW4 (652402) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_358 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_359 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_360 | 3 Phase fault on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE7 (652412) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_361 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_362 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_363 | 3 Phase fault on REDFELD-ER8 69.000 (655482) 69 kV Bus a. Apply fault at the REDFELD-ER8 69.000 (655482) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER8 (655482) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_364 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_365 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_366 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.3. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply Fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.5. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.6. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LEWIS 7 115.00 (661056) 115 kV Bus a. Apply Fault at the LEWIS 7 115.00 (661056) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.2. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.3. LEWIS 7 (661056) 115.0 kV to LEWIS71G (661055) 13.8 kV Two Winding #1 b.4. LEWIS 7 (661056) 115.0 kV to LEWIS72G (661104) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z b.5. BEULAH 7 (661008) 115.0 kV to COYOTE 7 (661018) 115.0 kV Transmission Circuit #1 b.6. BEULAH 7 (661008) 115.0 kV to COYOTETAP 7 (661057) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply Fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 b.3. GLENDCT7 (661032) 115.0 kV to Load #Y0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 b.3. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.4. GLENDCT7 (661032) 115.0 kV to GLNDCT1G (661100) 13.8 kV Two Winding #1 b.5. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply Fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.4. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.5. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.6. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.7. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.8. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.9. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.10. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.4. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply Fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on GU CTR 5 161.00 (631072) 161 kV Bus a. Apply Fault at the GU CTR 5 161.00 (631072) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.3. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #1 b.4. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #2 b.5. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.6. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.7. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.8. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.9. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.10. SCRANTN5 (631071) 161.0 kV to SCRANTN9 (629111) 34.5 kV Two Winding #1 b.11. SCRANTN5 (631071) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.12. SCRANTN5 (631071) 161.0 kV to GR JCT 5 (631074) 161.0 kV Transmission Circuit #1 b.13. GU CTR 5 (631072) 161.0 kV to GU CTR 9 (629113) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply Fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.3. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to None Three Winding #1 b.4. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 b.5. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 b.3. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.4. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.5. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply Fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.4. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.5. EDGELEY 19 (652328) 13.2 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.2. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.3. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.4. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.5. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.6. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.6. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7 115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7 115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to Load #BB b.6. GARRISN7 (652442) 115.0 kV to Load #BW b.7. GARRISN7 (652442) 115.0 kV to Load #R0 b.8. GARRISN7 (652442) 115.0 kV to Load #W0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. EXIRA 5 (652603) 161.0 kV to EXIRA 2G (658001) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.11. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 b.7. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply Fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | No | Yes | No | Yes | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. The following CQ unit were determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | No | Yes | No | Yes | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. The following CQ unit were determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on FORTUNA -SH7115.00 (655777) 115 kV Bus a. Apply Fault at the FORTUNA -SH7115.00 (655777) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 b.2. FORTUNA -SH7 (655777) 115.0 kV to AMBROSE -BD7 (655784) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.5. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.7. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.8. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.9. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply Fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 b.4. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. BROOKS 5 (635037) 161.0 kV to ADAMS 5 (635056) 161.0 kV Transmission Circuit #1 b.5. ADAMS 5 (635056) 161.0 kV to ADAMS B1 9 (635057) 34.5 kV Two Winding #1 b.6. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.7. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. NBCS_10_-PPR (659278) 12.5 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.3. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 b.3. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.9. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 b.10. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.10. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on HOSPERS8 69.000 (635371) 69 kV Bus a. Apply Fault at the HOSPERS8 69.000 (635371) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSPERS8 (635371) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 b.2. HOSPERS8 (635371) 69.0 kV to SHELDON8 (635370) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply Fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCKVALY8 (635380) 69.0 kV to DOONTAP8 (635377) 69.0 kV Transmission Circuit #1 b.2. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on RKVALTT8 69.000 (635381) 69 kV Bus a. Apply Fault at the RKVALTT8 69.000 (635381) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RKVALTT8 (635381) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 b.2. RKVALTT8 (635381) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on INWOODT8 69.000 (635383) 69 kV Bus a. Apply Fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 b.2. INWOODT8 (635383) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply Fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. HUDSON 8 (635385) 69.0 kV to INWOODT8 (635383) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on IRETONT8 69.000 (635391) 69 kV Bus a. Apply Fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. IRETONT8 (635391) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z2 b.2. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. DENISON8 (652583) 69.0 kV to DENISON4 (652567) 230.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply Fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply Fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply Fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 b.2. TEMPLTON8 (656247) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on DENISONWEST869.000 (658030) 69 kV Bus a. Apply Fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on L6OC E MUNI869.000 (658904) 69 kV Bus a. Apply Fault at the L6OC E MUNI869.000 (658904) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L6OC E MUNI8 (658904) 69.0 kV to L7OC W MUNI8 (658906) 69.0 kV Transmission Circuit #1 b.2. L6OC E MUNI8 (658904) 69.0 kV to L14OCINDMUN8 (658903) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on L7OC W MUNI869.000 (658906) 69 kV Bus a. Apply Fault at the L7OC W MUNI869.000 (658906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L7OC W MUNI8 (658906) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 b.2. L7OC W MUNI8 (658906) 69.0 kV to L6OC E MUNI8 (658904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply Fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 b.2. K125DUNL-NI8 (659853) 69.0 kV to K126MEC -NI8 (659852) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply Fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply Fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 b.2. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply Fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply Fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K307DENI-NI8 (659862) 69.0 kV Transmission Circuit #1 b.2. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply Fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on K228WSTB-NI869.000 (659896) 69 kV Bus a. Apply Fault at the K228WSTB-NI869.000 (659896) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K228WSTB-NI8 (659896) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 b.2. K228WSTB-NI8 (659896) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to EAGLE___-NI4 (659900) 230.0 kV Two Winding #2 b.2. EAGLE___-NI8 (659901) 69.0 kV to EAGLE___-NI4 (659900) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on L1______-NI869.000 (659902) 69 kV Bus a. Apply Fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on L3______-NI869.000 (659904) 69 kV Bus a. Apply Fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L3______-NI8 (659904) 69.0 kV to K228WSTB-NI8 (659896) 69.0 kV Transmission Circuit #1 b.2. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on L8______-NI869.000 (659905) 69 kV Bus a. Apply Fault at the L8______-NI869.000 (659905) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L8______-NI8 (659905) 69.0 kV to L7OC W MUNI8 (658906) 69.0 kV Transmission Circuit #1 b.2. L8______-NI8 (659905) 69.0 kV to K228WSTB-NI8 (659896) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. J6BOYER_-NI8 (659912) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on J12_____-NI869.000 (659918) 69 kV Bus a. Apply Fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J12_____-NI8 (659918) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. J12_____-NI8 (659918) 69.0 kV to K125DUNL-NI8 (659853) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J15_____-NI8 (659921) 69.0 kV to L4SXCTNMUNI8 (658900) 69.0 kV Transmission Circuit #1 b.2. J15_____-NI8 (659921) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on K202PRES-NI869.000 (659944) 69 kV Bus a. Apply Fault at the K202PRES-NI869.000 (659944) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K202PRES-NI8 (659944) 69.0 kV to K226MERR-NI8 (659945) 69.0 kV Transmission Circuit #1 b.2. K202PRES-NI8 (659944) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on K214____-NI869.000 (659948) 69 kV Bus a. Apply Fault at the K214____-NI869.000 (659948) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K214____-NI8 (659948) 69.0 kV to K211SENY-NI8 (659949) 69.0 kV Transmission Circuit #1 b.2. K214____-NI8 (659948) 69.0 kV to K221ALTO-NI8 (659947) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply Fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 b.2. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.2. FTTHOM2-LNX3 (652807) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply Fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.2. AV.LS-BD-BE3 (659420) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply Fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #1 b.2. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND-BE3 (659120) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply Fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 b.2. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on K213HOSP-NI869.000 (659955) 69 kV Bus a. Apply Fault at the K213HOSP-NI869.000 (659955) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K213HOSP-NI8 (659955) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 b.2. K213HOSP-NI8 (659955) 69.0 kV to HOSPERS8 (635371) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on K218ROCK-NI869.000 (659977) 69 kV Bus a. Apply Fault at the K218ROCK-NI869.000 (659977) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K218ROCK-NI8 (659977) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. K218ROCK-NI8 (659977) 69.0 kV to RKVALTT8 (635381) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTON__-BE3 (659160) 345.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on MANNINGTAP 869.000 (656267) 69 kV Bus a. Apply Fault at the MANNINGTAP 869.000 (656267) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANNINGTAP 8 (656267) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. MANNINGTAP 8 (656267) 69.0 kV to TEMPLTON8 (656247) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on DENSOUMAIN8 69.000 (658031) 69 kV Bus a. Apply Fault at the DENSOUMAIN8 69.000 (658031) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENSOUMAIN8 (658031) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENSOUMAIN8 (658031) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply Fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSBORN -MW7 (655919) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.2. OSBORN -MW7 (655919) 115.0 kV to E.NEWTWN-MW7 (655907) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on K338WTCT-NI869.000 (659897) 69 kV Bus a. Apply Fault at the K338WTCT-NI869.000 (659897) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K338WTCT-NI8 (659897) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 b.2. K338WTCT-NI8 (659897) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on K308EARL-NI869.000 (659856) 69 kV Bus a. Apply Fault at the K308EARL-NI869.000 (659856) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K308EARL-NI8 (659856) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 b.2. K308EARL-NI8 (659856) 69.0 kV to K321MEC -NI8 (659857) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on K317MANN-NI869.000 (659906) 69 kV Bus a. Apply Fault at the K317MANN-NI869.000 (659906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K317MANN-NI8 (659906) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 b.2. K317MANN-NI8 (659906) 69.0 kV to K330MANM-NI8 (659864) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on K326OTTE-NI869.000 (659886) 69 kV Bus a. Apply Fault at the K326OTTE-NI869.000 (659886) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K326OTTE-NI8 (659886) 69.0 kV to K306SCHL-NI8 (659885) 69.0 kV Transmission Circuit #1 b.2. K326OTTE-NI8 (659886) 69.0 kV to K333SCHL-NI8 (659887) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on K217HWDN-NI869.000 (659942) 69 kV Bus a. Apply Fault at the K217HWDN-NI869.000 (659942) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K217HWDN-NI8 (659942) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. K217HWDN-NI8 (659942) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply Fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K222HULL-NI8 (659941) 69.0 kV to L4SXCTNMUNI8 (658900) 69.0 kV Transmission Circuit #1 b.2. K222HULL-NI8 (659941) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on K207OC N-NI869.000 (659943) 69 kV Bus a. Apply Fault at the K207OC N-NI869.000 (659943) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K207OC N-NI8 (659943) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 b.2. K207OC N-NI8 (659943) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply Fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K223SIOU-NI8 (659940) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. K223SIOU-NI8 (659940) 69.0 kV to L5SXCTWMUNI8 (658902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on K106CHAR-NI869.000 (659999) 69 kV Bus a. Apply Fault at the K106CHAR-NI869.000 (659999) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K106CHAR-NI8 (659999) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 b.2. K106CHAR-NI8 (659999) 69.0 kV to K105UTE_-NI8 (659998) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on K226MERR-NI869.000 (659945) 69 kV Bus a. Apply Fault at the K226MERR-NI869.000 (659945) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K226MERR-NI8 (659945) 69.0 kV to K225ADAV-NI8 (659899) 69.0 kV Transmission Circuit #1 b.2. K226MERR-NI8 (659945) 69.0 kV to K202PRES-NI8 (659944) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MONT -MW7 115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7 115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to remove bus # | P4 | No | Yes | Yes | No | Yes | No | Yes | Oscilations are observed at GEN-2018-067 (763024 and 763027) generating site post fault clearance. The following CQ unit were determined to be the cause of the oscillations: - GEN-2018-067 : PTDF of 0.82688 | Build Strandahl to Black Tail 115 kV line
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7 115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7 115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply Fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on DENISON8 69.00 (652583) 69 kV Bus a. Apply Fault at the DENISON8 69.00 (652583) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI8 69.00 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI8 69.00 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on EAGLE___-NI8 69.00 (659901) 69 kV Bus a. Apply Fault at the EAGLE___-NI8 69.00 (659901) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on J1CENTER-NI8 69.00 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI8 69.00 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on L1______-NI8 69.00 (659902) 69 kV Bus a. Apply Fault at the L1______-NI8 69.00 (659902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L1______-NI8 (659902) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3 345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3 345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BROWNSV4 230.00 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 230.00 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on ASTORIA 3 345.00 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 345.00 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #1 b.2. ASTORIA 3 (620483) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_001 | Single Phase Fault with Stuck Breaker on AVS 345 (659420) 345 kV Bus a. Apply Fault at the AVS 345 (659420) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to remove bus #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to Load #BB b.3. COTEAU_1-RR8 (659222) 69.0 kV to Load #BW b.4. DGC UREA-BE8 (659236) 69.0 kV to Load #BG b.5. COTEAU 1-RR9 (659219) 13.8 kV to remove bus # b.6. COTEAU 2-RR9 (659231) 13.8 kV to remove bus # b.7. COTEAU_1-RR8 (659222) 69.0 kV to remove bus # b.8. COTEAU__-RR3 (659218) 345.0 kV to remove bus # b.9. DGC UREA-BE8 (659236) 69.0 kV to remove bus # b.10. AV.LS-BD-BE3 (659420) 345.0 kV to remove bus # b.11. AV.LS-BD-BE3 (659420) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_002 | Single Phase Fault with Stuck Breaker on LOS 345 (659424) 345 kV Bus a. Apply Fault at the LOS 345 (659424) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #Z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to Switched Shunt Device # b.3. CC.LS-LO-BE3 (659428) 345.0 kV to Switched Shunt Device # b.4. LELAND_2-BEG (659111) 20.0 kV to Load #S0 b.5. LELAND_2-BEG (659111) 20.0 kV to Generator #2 b.6. LELAND_2-BEG (659111) 20.0 kV to remove bus # b.7. CC.LS-LO-BE3 (659428) 345.0 kV to remove bus # b.8. LO.LS-FT-BE3 (659424) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_003 | Single Phase Fault with Stuck Breaker on LOS 345 (659422) 345 kV Bus a. Apply Fault at the LOS 345 (659422) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #Z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to Switched Shunt Device # b.3. LO.LS-GR-BE3 (659422) 345.0 kV to Switched Shunt Device # b.4. LO.KU1A_-BE9 (659201) 13.8 kV to Switched Shunt Device # b.5. LO.LS-GR-BE3 (659422) 345.0 kV to remove bus # b.6. GR.LS-LO-BE3 (659423) 345.0 kV to remove bus # b.7. LO.KU1A_-BE9 (659201) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_004 | Single Phase Fault with Stuck Breaker on LOS 230 (659106) 230 kV Bus a. Apply Fault at the LOS 230 (659106) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to Load #BB b.3. BASIN___-BE7 (659109) 115.0 kV to Load #BW b.4. BASIN___-BE7 (659109) 115.0 kV to Load #W0 b.5. LELAND_1-BEG (659110) 22.0 kV to Load #S0 b.6. LELAND_1-BEG (659110) 22.0 kV to Generator #1 b.7. NEWSALEM-MG7 (655748) 115.0 kV to Load #BB b.8. NEWSALEM-MG7 (655748) 115.0 kV to Load #BW b.9. ROUGHRDR-MG7 (655750) 115.0 kV to Load #BB b.10. ROUGHRDR-MG7 (655750) 115.0 kV to Load #BW b.11. NRWSTMDN-MG7 (655751) 115.0 kV to Load #BB b.12. NRWSTMDN-MG7 (655751) 115.0 kV to Load #BW b.13. DEVAUL -MG8 (655746) 69.0 kV to Load #W0 b.14. CANNON -MG8 (655740) 69.0 kV to Load #BB b.15. CANNON -MG8 (655740) 69.0 kV to Load #BW b.16. CEDAR -MG8 (655741) 69.0 kV to Load #BB b.17. CEDAR -MG8 (655741) 69.0 kV to Load #BW b.18. GRANT -MG8 (655742) 69.0 kV to Load #BB b.19. GRANT -MG8 (655742) 69.0 kV to Load #BW b.20. FLASHER -MG8 (655732) 69.0 kV to Load #BB b.21. FLASHER -MG8 (655732) 69.0 kV to Load #BW b.22. LO.KU1A_-BE9 (659201) 13.8 kV to remove bus # b.23. LO.KVA2_-BE9 (659202) 13.8 kV to remove bus # b.24. BAL.KY1A-BE9 (659200) 13.8 kV to remove bus # b.25. LELAND_O-BE4 (659106) 230.0 kV to remove bus # b.26. BASIN___-BE7 (659109) 115.0 kV to remove bus # b.27. BASIN___-BE4 (659199) 230.0 kV to remove bus # b.28. LELAND_1-BEG (659110) 22.0 kV to remove bus # b.30. NEWSALEM-MG7 (655748) 115.0 kV to remove bus # b.31. MANSWTCH-MG7 (655749) 115.0 kV to remove bus # b.32. ROUGHRDR-MG7 (655750) 115.0 kV to remove bus # b.33. NRWSTMDN-MG7 (655751) 115.0 kV to remove bus # b.34. NWMDNTAP-MG7 (655752) 115.0 kV to remove bus # b.35. DEVAUL -MG8 (655746) 69.0 kV to remove bus # b.36. DEVALTP -MG8 (655744) 69.0 kV to remove bus # b.37. DEVAUL 8 (652257) 69.0 kV to remove bus # b.38. LARK -MG8 (655731) 69.0 kV to remove bus # b.39. CANNON -MG8 (655740) 69.0 kV to remove bus # b.40. CEDAR -MG8 (655741) 69.0 kV to remove bus # b.41. GRANT -MG8 (655742) 69.0 kV to remove bus # b.42. FLASHER -MG8 (655732) 69.0 kV to remove bus # b.44. DEVAUL -MG7 (655747) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_005 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_006 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_007 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CCR.KV4A-BE9 (659319) 13.8 kV to remove bus # b.3. CCR.KV3A-BE9 (659318) 13.8 kV to remove bus # b.4. CHARL_CK-BE4 (659302) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_008 | Single Phase Fault with Stuck Breaker on JDS 345 (659333) 345 kV Bus a. Apply Fault at the JDS 345 (659333) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to remove bus # b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from PS_RCP.B-BEG (659432 and 659431). Disabling the dynamic controller model allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP1_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MONT -MW7 115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7 115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from PS_RCP.B-BEG (659432 and 659431). Disabling the dynamic controller model allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP1_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MONT -MW7 115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7 115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_001 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on W LINCOLN 7 115.00 (650208) 115 kV Bus a. Apply fault at the W LINCOLN 7 115.00 (650208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_003 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_004 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_005 | 3 Phase fault on 8&N 7 115.00 (650217) 115 kV Bus a. Apply fault at the 8&N 7 115.00 (650217) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_006 | 3 Phase fault on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_007 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_008 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_009 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_010 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_011 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_012 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_013 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_014 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_015 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_016 | 3 Phase fault on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_017 | 3 Phase fault on 93&O 7 115.00 (650273) 115 kV Bus a. Apply fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_018 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_019 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_020 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_021 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_022 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_023 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_024 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on COOPER1G 22.000 (640009) 22 kV Bus a. Apply fault at the COOPER1G 22.000 (640009) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER1G (640009) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on NW56&MORTN7 115.00 (650207) 115 kV Bus a. Apply fault at the NW56&MORTN7 115.00 (650207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.6. 40&ROKEBY 7 (650250) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 70&CALVERT7 (650270) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_065 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power Oscillations are oberserved at the Grand Prairie Wind Farm (645065, 645066, 645067 and 645068) following the fault and the units are tripped due to internal protection before reaching the 10 second post-fault time mark. The issue is resolved when the critical clearing time is reduced to 3 cycles. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_068 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_069 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_070 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_071 | 3 Phase fault on SUB-H G 115.00 (642066) 115 kV Bus a. Apply fault at the SUB-H G 115.00 (642066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-H G (642066) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_072 | 3 Phase fault on SUB-C 7 115.00 (642070) 115 kV Bus a. Apply fault at the SUB-C 7 115.00 (642070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-C 7 (642070) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_073 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_074 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_075 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_076 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to STOCKVL8 (640366) 69.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 b.4. STOCKVLLET19 (643146) 13.8 kV to STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_077 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_078 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_079 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_080 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_081 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_082 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to FAIRBRYG (640170) 34.5 kV to FAIRBURY T19 (643056) 13.8 kV Three Winding #1 b.4. FAIRBURY T19 (643056) 13.8 kV to FAIRBRYG (640170) 34.5 kV to FAIRBRY7 (640169) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_083 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_084 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_085 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_086 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_087 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_088 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_089 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_090 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_091 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_092 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_093 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_094 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_095 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_096 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_097 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_098 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_099 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_100 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_101 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_102 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_103 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_104 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_105 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_106 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_107 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_108 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_109 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_110 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_111 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_112 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_113 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_114 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_115 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_116 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_117 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_118 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_119 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_120 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_121 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_122 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_123 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_124 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_125 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_126 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_127 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 b.2. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_128 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_129 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_130 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_131 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_132 | 3 Phase fault on CREITON8 69.000 (640150) 69 kV Bus a. Apply fault at the CREITON8 69.000 (640150) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_133 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_134 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_135 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_136 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_137 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_138 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_139 | 3 Phase fault on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHUYLR7 (640336) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_140 | 3 Phase fault on SILVRCK8 69.000 (640346) 69 kV Bus a. Apply fault at the SILVRCK8 69.000 (640346) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_141 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_142 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_143 | 3 Phase fault on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETERSBRG.N7 (640444) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_144 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_145 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_146 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_147 | 3 Phase fault on HOSKINS4 230.00 (640227) 345 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_148 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_149 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_150 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_151 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_152 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_153 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_154 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_155 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_156 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_157 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_158 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_159 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_160 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_161 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_162 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_163 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_164 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_165 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_166 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_167 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_168 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_169 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_170 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_171 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_172 | 3 Phase fault on NCU903 8 69.000 (647401) 69 kV Bus a. Apply fault at the NCU903 8 69.000 (647401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S962 8 (647962) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_173 | 3 Phase fault on S977 8 69.000 (647977) 69 kV Bus a. Apply fault at the S977 8 69.000 (647977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_174 | 3 Phase fault on S965 8 69.000 (647965) 69 kV Bus a. Apply fault at the S965 8 69.000 (647965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_175 | 3 Phase fault on S967 8 69.000 (647967) 69 kV Bus a. Apply fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_176 | 3 Phase fault on S969 8 69.000 (647969) 69 kV Bus a. Apply fault at the S969 8 69.000 (647969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.2. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.3. S968 8 (647968) 69.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_177 | 3 Phase fault on S973 8 69.000 (647973) 69 kV Bus a. Apply fault at the S973 8 69.000 (647973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_178 | 3 Phase fault on FREM D 8 69.000 (647424) 69 kV Bus a. Apply fault at the FREM D 8 69.000 (647424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM D 8 (647424) 69.0 kV to FREM E 8 (647425) 69.0 kV Transmission Circuit #1 b.2. FREM D 8 (647424) 69.0 kV to S976 8 (647976) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_179 | 3 Phase fault on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_180 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_181 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_182 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_183 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_184 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_185 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_186 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_187 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_188 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_189 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_190 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_192 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_193 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_194 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV Switched Shunt Device #//1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_195 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_196 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_197 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_198 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_199 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_200 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_201 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_202 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_203 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_204 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_205 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_206 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_207 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_210 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_211 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_212 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_213 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_214 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_215 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_216 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_217 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_218 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_219 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_220 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_221 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_222 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_224 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_226 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_227 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_228 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_229 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_232 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_233 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_234 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_235 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_236 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_237 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_238 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_239 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_240 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_241 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_242 | 3 Phase fault on BEAT. S7 115.00 (640074) 115 kV Bus a. Apply fault at the BEAT. S7 115.00 (640074) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_243 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_244 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_245 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_246 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_247 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_248 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_249 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_250 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_251 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_252 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_253 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_254 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_255 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_256 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_257 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_258 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_259 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_260 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_261 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_262 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_263 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_264 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_265 | 3 Phase fault on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_266 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_267 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_268 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_269 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_270 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_271 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_272 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_273 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_274 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_275 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_276 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_277 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_278 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_279 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_280 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_281 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_282 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_283 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_284 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_285 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_286 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_287 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_288 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_289 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_290 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_291 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_292 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_293 | 3 Phase fault on HARBINE7 115.00 (640208) 115 kV Bus a. Apply fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_295 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_296 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_297 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_298 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_299 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_300 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_301 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_302 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_303 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_304 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_305 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_306 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_307 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_308 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_309 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_310 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_311 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_312 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_313 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_314 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_315 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_316 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_317 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_318 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_320 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_321 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_322 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_323 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_324 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_325 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_326 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_327 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_328 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_329 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_330 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_331 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_332 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_333 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_334 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_335 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_336 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_337 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_338 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_339 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_340 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_341 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 3 (640529) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_342 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_343 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_344 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_345 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | The Laramie generating site (659118) loses synchronism after the fault. The issue is resolved when the critical clearing time is reduced to 5 cycles. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_347 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_348 | 3 Phase fault on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_349 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_350 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_351 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_352 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_353 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_354 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_355 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_356 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 8 (640085) 69.0 kV to BLMFLD 7 (640084) 115.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_357 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_358 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_359 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_360 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_361 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_362 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_363 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_364 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_365 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_366 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_367 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY8 (640417) 69.0 kV to RISNGCY7 (640328) 115.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_370 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_371 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_372 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 8 (640468) 69.0 kV to TAMORA 7 (640375) 115.0 kV to TAMORA T2 9 (643181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_373 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_374 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_375 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_376 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S966 8 (647966) 69.0 kV to STEINER7 (640361) 115.0 kV to STEINER T1 9 (643143) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_377 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_378 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_379 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_380 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_381 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_001 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_002 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_005 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_006 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_007 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_008 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_009 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_012 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_015 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_017 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_018 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_020 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_027 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_028 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_032 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_041 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_042 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_043 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_044 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_045 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_046 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_047 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_048 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MADISON3 345.00 (635635) 345 kV Bus a. Apply Fault at the MADISON3 345.00 (635635) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORIENT 3 (635570) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.2. BOONVIL3 (635630) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.3. MADISON3 (635635) 345.0 kV to NORWLK3 (635640) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.7. S1366 5 (646366) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.4. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.5. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T1 9 (643004) 13.8 kV Three Winding #1 b.6. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T2 9 (643005) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.4. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.3. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT19 (643032) 13.8 kV Three Winding #1 b.4. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT29 (643033) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 b.2. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.2. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.3. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T1 9 (643046) 4.2 kV Three Winding #1 b.4. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T2 9 (643047) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FREMONT7 115.00 (640173) 115 kV Bus a. Apply Fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.3. FREMONT7 (640173) 115.0 kV to S976 8 (647976) 69.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 b.4. FREMONT7 (640173) 115.0 kV to S976 8 (647976) 69.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.3. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.4. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.5. GENEVA 7 (640178) 115.0 kV to GENEVA 8 (640179) 69.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T1 9 (643064) 13.8 kV Three Winding #1 b.4. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T2 9 (643065) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HARBINE7 115.00 (640208) 115 kV Bus a. Apply Fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.3. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to KINGSLY7 (640255) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.3. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to MCCOOK G (640017) 13.8 kV Two Winding #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.4. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.5. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.6. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.4. MCCOOL 7 (640272) 115.0 kV to MCCOOL 8 (640273) 69.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on MINDEN 7 115.00 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 115.00 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.4. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply Fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.3. RISNGCY7 (640328) 115.0 kV to RISNGCY9 (640329) 34.5 kV to RISINGCTYT19 (643126) 13.8 kV Three Winding #1 b.4. RISNGCY7 (640328) 115.0 kV to RISNGCY8 (640417) 69.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply Fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.3. SCHUYLR7 (640336) 115.0 kV to SCHUYLR9 (640337) 34.5 kV to SCHUYLER T19 (643131) 13.8 kV Three Winding #1 b.4. SCHUYLR7 (640336) 115.0 kV to SCHUYLR9 (640337) 34.5 kV to SCHUYLER T29 (643132) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.3. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.4. SEWARD 7 (640340) 115.0 kV to SEWARD 9 (640341) 34.5 kV to SEWARD T1 9 (643134) 13.8 kV Three Winding #1 b.5. SEWARD 7 (640340) 115.0 kV to SEWARD 9 (640341) 34.5 kV to SEWARD T2 9 (643135) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.3. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T19 (643139) 13.8 kV Three Winding #1 b.4. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T29 (643169) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.3. THEDFRD7 (640381) 115.0 kV to THEDFRD9 (640382) 34.5 kV to THEDFORD T19 (643153) 13.8 kV Three Winding #1 b.4. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WAHOO 7 115.00 (640402) 115 kV Bus a. Apply Fault at the WAHOO 7 115.00 (640402) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.3. WAHOO 29 (648402) 13.8 kV to WAHOO 7 (640402) 115.0 kV Two Winding #1 b.4. WAHOO 7 (640402) 115.0 kV to WAHOO G (640403) 34.5 kV to WAHOO T1 9 (643163) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.4. YORK 7 (640411) 115.0 kV to YORK 9 (640412) 34.5 kV to YORK T1 9 (643166) 13.8 kV Three Winding #1 b.5. YORK 7 (640411) 115.0 kV to YORK 8 (640443) 69.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. YORK SW7 (640413) 115.0 kV to YORK SW9 (640414) 34.5 kV to YORK.SW T1 9 (643168) 13.8 kV Three Winding #1 b.4. YORK SW7 (640413) 115.0 kV to YORK.SW T2 8 (640447) 69.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to Load #NW b.2. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to Load #NW b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.3. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.4. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS9 (640137) 34.5 kV to Load #N0 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.5. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. E.COL. 4 (640126) 230.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.4. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT19 (643037) 13.8 kV Three Winding #1 b.5. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT29 (643038) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to Load #N2 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to Load #N2 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.4. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY9 (640251) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.8. KEARNEY7 (640250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 b.5. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to NORTHPLT T79 (643107) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply Fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z b.3. OGALALA9 (640303) 34.5 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T29 (643116) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 b.2. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on STEELEC7 115.00 (640426) 115 kV Bus a. Apply Fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.2. STEELEC9 (640427) 4.2 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 b.3. STEELEC7 (640426) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.7. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply Fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. ELKRDG.PLT D (640419) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.4. CROFTN.PLT D (640423) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.5. BLMFLD 7 (640084) 115.0 kV to BLMFLD 8 (640085) 69.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS9 (640137) 34.5 kV to Load #N0 b.2. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COLMBUS7 (640136) 115.0 kV to COLMBS1G (640006) 13.8 kV Two Winding #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS2G (640007) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.6. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.8. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.9. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.12. COLMBUS7 (640136) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.6. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on COL.COG7 115.00 (640119) 115 kV Bus a. Apply Fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 b.2. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.4. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.5. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.6. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT19 (643037) 13.8 kV Three Winding #1 b.7. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT29 (643038) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.5. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.6. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.7. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.8. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG9 (640225) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.5. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.10. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.3. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.4. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on STEELEC7 115.00 (640426) 115 kV Bus a. Apply Fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.2. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.3. STEELEC7 (640426) 115.0 kV to S.FLATS.PLT7 (640558) 115.0 kV Transmission Circuit #1 b.4. STEELEC9 (640427) 4.2 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 b.5. STEELEC_KXL9 (640440) 6.9 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.3. N.PLATTG (640018) 13.8 kV to N.PLATT9 (640289) 34.5 kV to N.PLATT7 (640287) 115.0 kV Three Winding #1 b.4. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.6. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus a. Apply Fault at the FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on KELLY 5 161.00 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.4. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.4. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.5. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply Fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.4. GRANTNB_-TS7 (659800) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.5. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.6. OGALALA_-TS7 (659801) 115.0 kV to MCONGHY_-TS7 (659824) 115.0 kV Transmission Circuit #1 b.7. ELSIETP_-TS7 (659807) 115.0 kV to PAXTON__-TS7 (659808) 115.0 kV Transmission Circuit #1 b.8. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.9. ELSIETP_-TS7 (659807) 115.0 kV to ELSIE___-TS7 (659822) 115.0 kV Transmission Circuit #1 b.10. MCONGHY_-TS7 (659824) 115.0 kV to ARTHUR__-TS7 (659825) 115.0 kV Transmission Circuit #1 b.11. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 b.12. OGALALA9 (640303) 34.5 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T29 (643116) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply Fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply Fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on 8&N 7 115.00 (650217) 115 kV Bus a. Apply Fault at the 8&N 7 115.00 (650217) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8&J 9 (650100) 34.5 kV to 171TERTIARY (650517) 34.5 kV Transmission Circuit #1 b.2. 8&N 7 (650217) 115.0 kV to 17&HOLDRGE7 (650219) 115.0 kV Transmission Circuit #1 b.3. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. 8&N 7 (650217) 115.0 kV to 8&N A9 (650317) 13.2 kV to 171TERTIARY (650517) 34.5 kV Three Winding #1 b.5. 8&N 7 (650217) 115.0 kV to 8&N B9 (650417) 13.2 kV to 172TERTIARY (650617) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&Q 7 (650260) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 30&A 7 (650252) 115.0 kV to 56&EVERETT7 (650256) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on 40&GERTIE 7 115.00 (650258) 115 kV Bus a. Apply Fault at the 40&GERTIE 7 115.00 (650258) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.5. 40&GERTIE 7 (650258) 115.0 kV to 40&GE A9 (650358) 13.2 kV to 581TERTIARY (650558) 7.2 kV Three Winding #1 b.6. 40&GERTIE 7 (650258) 115.0 kV to 40&GE B9 (650458) 13.2 kV to 582TERTIARY (650658) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.4. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.5. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.6. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.9. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.5. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 b.11. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 3G (650093) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 1G (650091) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply Fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.3. 27&PLR 7 (650229) 115.0 kV to 27&PLR A9 (650329) 12.5 kV to 291TERTIARY (650529) 7.2 kV Three Winding #1 b.4. 27&PLR 7 (650229) 115.0 kV to 27&PLR B9 (650429) 12.5 kV to 292TERTIARY (650629) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.5. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.6. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply Fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on 56&PLR 7 115.00 (650255) 115 kV Bus a. Apply Fault at the 56&PLR 7 115.00 (650255) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on NW12&ARBOR7 115.00 (650226) 115 kV Bus a. Apply Fault at the NW12&ARBOR7 115.00 (650226) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 b.2. NW56&MORTN7 (650207) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.3. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.4. 19&ALVO 7 (650215) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.5. NW70FAIRFD7 (650210) 115.0 kV to NW70FAIRFD9 (650310) 12.5 kV to 101TERTIARY (650510) 7.2 kV Three Winding #1 b.6. NW12&ARBOR7 (650226) 115.0 kV to NW12&AR 9 (650326) 12.5 kV to 261TERTIARY (650526) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on NW5&BENTON7 115.00 (650212) 115 kV Bus a. Apply Fault at the NW5&BENTON7 115.00 (650212) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4&MORTON 7 (650205) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.2. W LINCOLN 7 (650208) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.3. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. W LINCOLN 7 (650208) 115.0 kV to WLINCOLN 9 (650308) 13.2 kV to 084TERTIARY (650508) 7.2 kV Three Winding #1 b.5. NW5&BENTON7 (650212) 115.0 kV to NW5BENTN 9 (650312) 12.5 kV to 121TERTIARY (650512) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.7. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 b.2. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S967 8 69.000 (647967) 69 kV Bus a. Apply Fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.2. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on S968 8 69.000 (647968) 69 kV Bus a. Apply Fault at the S968 8 69.000 (647968) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.2. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.4. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply Fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. NC SYRA8 (647402) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.5. NC SYRA8 (647402) 69.0 kV to S971 8 (647971) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on S974 8 69.000 (647974) 69 kV Bus a. Apply Fault at the S974 8 69.000 (647974) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.2. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.3. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.5. S968 8 (647968) 69.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on STERLNG7 115.00 (640362) 115 kV Bus a. Apply Fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.5. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.2. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.3. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 b.5. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on S993 8 69.000 (647993) 69 kV Bus a. Apply Fault at the S993 8 69.000 (647993) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.5. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.6. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.7. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply Fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.5. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.4. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 b.5. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 b.4. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 b.5. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on EAST 5 161.00 (541254) 161 kV Bus a. Apply Fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on IND PRK5 161.00 (541256) 161 kV Bus a. Apply Fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 b.2. IND PRK5 (541256) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on G13-002-TAP 115.00 (560746) 115 kV Bus a. Apply Fault at the G13-002-TAP 115.00 (560746) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G13-002-TAP (560746) 115.0 kV to GEN-2013-019 (583700) 115.0 kV Transmission Circuit #1 b.2. G13-002-TAP (560746) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-023 (584650) 345.0 kV to G15-023XFMR2 (584654) 34.5 kV to G15-023-TER2 (584659) 13.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on GEN-2015-088345.00 (585241) 345 kV Bus a. Apply Fault at the GEN-2015-088345.00 (585241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-088 (585241) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-088 (585241) 345.0 kV to G15-088-XF-2 (585249) 34.5 kV to G15-088-TR-1 (906007) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RLHILLS3 (635100) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on S HILLS 3 345.00 (635568) 345 kV Bus a. Apply Fault at the S HILLS 3 345.00 (635568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HILLS 3 (635568) 345.0 kV to BOONVIL3 (635630) 345.0 kV Transmission Circuit #1 b.2. S HILLS 3 (635568) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply Fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #2 b.2. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on CLATONA7 115.00 (640111) 115 kV Bus a. Apply Fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CO.LINE7 (640115) 115.0 kV to BATTLCR7 (640072) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to HAYSTACK.WD3 (640598) 345.0 kV Transmission Circuit #1 b.2. TURTLE.CRK 3 (640588) 345.0 kV to PLUMBCR.W 3 (643271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on GEN-2017-181345.00 (761292) 345 kV Bus a. Apply Fault at the GEN-2017-181345.00 (761292) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-181 (761292) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-181 (761292) 345.0 kV to GEN-2017-182 (761313) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on GEN-2017-183345.00 (761376) 345 kV Bus a. Apply Fault at the GEN-2017-183345.00 (761376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-183 (761376) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-183 (761376) 345.0 kV to G17-184XFMR2 (761401) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply Fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-065-TAP (763031) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 b.2. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply Fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 b.2. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. GENOA 7 (640181) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply Fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCHUYLR7 (640336) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. SCHUYLR7 (640336) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z b.2. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SD.LS-KS-MB3 (659425) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to None Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to J748POI (87487) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on COOK 5 161.00 (541257) 161 kV Bus a. Apply Fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOK 5 (541257) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on WOODBIN5 161.00 (541258) 161 kV Bus a. Apply Fault at the WOODBIN5 161.00 (541258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODBIN5 (541258) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. WOODBIN5 (541258) 161.0 kV to EAST 5 (541254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on AVENUECTY 5 161.00 (541394) 161 kV Bus a. Apply Fault at the AVENUECTY 5 161.00 (541394) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVENUECTY 5 (541394) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 b.2. AVENUECTY 5 (541394) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on GEN-2013-019115.00 (583700) 115 kV Bus a. Apply Fault at the GEN-2013-019115.00 (583700) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2013-019 (583700) 115.0 kV to G13-002-TAP (560746) 115.0 kV Transmission Circuit #1 b.2. GEN-2013-019 (583700) 115.0 kV to G13-019XFMR1 (583701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on ORIENT 3 345.00 (635570) 345 kV Bus a. Apply Fault at the ORIENT 3 345.00 (635570) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORIENT 3 (635570) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.2. ORIENT 3 (635570) 345.0 kV to S HILLS 3 (635568) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on G18-131-TAP 345.00 (763443) 345 kV Bus a. Apply Fault at the G18-131-TAP 345.00 (763443) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-131-TAP (763443) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 b.2. G18-131-TAP (763443) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on G19-069-TAP 345.00 (763982) 345 kV Bus a. Apply Fault at the G19-069-TAP 345.00 (763982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-069-TAP (763982) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. G19-069-TAP (763982) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on STEINER7 115.00 (640361) 115 kV Bus a. Apply Fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEINER7 (640361) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. STEINER7 (640361) 115.0 kV to HUMBOLT7 (640235) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on GEN-2017-210345.00 (761208) 345 kV Bus a. Apply Fault at the GEN-2017-210345.00 (761208) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-210 (761208) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-210 (761208) 345.0 kV to G17-210-XFMR (761209) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on GEN-2017-144345.00 (760767) 345 kV Bus a. Apply Fault at the GEN-2017-144345.00 (760767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-144 (760767) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-144 (760767) 345.0 kV to G17-144XFMR2 (760771) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on HAYSTACK.WD3345.00 (640598) 345 kV Bus a. Apply Fault at the HAYSTACK.WD3345.00 (640598) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSTACK.WD3 (640598) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. HAYSTACK.WD3 (640598) 345.0 kV to HAYSTCK.C2 9 (643293) 34.5 kV to HAYSTCK.T2 9 (643298) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on GEN-2017-201345.00 (760788) 345 kV Bus a. Apply Fault at the GEN-2017-201345.00 (760788) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-201 (760788) 345.0 kV to G17-201XFMR1 (760789) 34.5 kV Two Winding #1 b.2. GEN-2017-201 (760788) 345.0 kV to SHOLES.W 3 (640589) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on GEN-2017-182345.00 (761313) 345 kV Bus a. Apply Fault at the GEN-2017-182345.00 (761313) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-182 (761313) 345.0 kV to GEN-2017-181 (761292) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-182 (761313) 345.0 kV to G17-182XFMR1 (761314) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on GEN-2017-105161.00 (762070) 161 kV Bus a. Apply Fault at the GEN-2017-105161.00 (762070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-105 (762070) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-105 (762070) 161.0 kV to G17-105XFM1 (762071) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-043 (762780) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-043 (762780) 345.0 kV to G18-043-XFM1 (762781) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on G19-039-TAP 115.00 (763718) 115 kV Bus a. Apply Fault at the G19-039-TAP 115.00 (763718) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-039-TAP (763718) 115.0 kV to RISNGCY7 (640328) 115.0 kV Transmission Circuit #1 b.2. G19-039-TAP (763718) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply Fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILVRCK7 (640345) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. SILVRCK7 (640345) 115.0 kV to CENCITY7 (640107) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply Fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply Fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 115.00 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 115.00 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1280 5 (646280) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESTON7 (640151) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_001 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_002 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_003 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.3. COOPER1G (640009) 22.0 kV to Generator #1 b.4. COOPER1G (640009) 22.0 kV to Load #S1 b.5. COOPER1G (640009) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_004 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 14.5 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 b.3. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_005 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_006 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_007 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_008 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_NPPD_FAULT_009 | Single Phase Fault with Stuck Breaker on COLMBUS4 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 (640133) 230 kV Bus b. Clear Fault after 8.5 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to COLMB.W4 (640131) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_TSGT_FAULT_001 | Single Phase Fault with Stuck Breaker on SIDNEY (MBPP) (659210) 230 kV Bus a. Apply Fault at the SIDNEY (MBPP) (659210) 230 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.2. SIDNEY___TS4 (659134) 230.0 kV to remove bus # b.3. SIDNEY__-MB4 (659210) 230.0 kV to remove bus # b.4. SIDNEY__-TS8 (659803) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LES_FAULT_001 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LES_FAULT_002 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LES_FAULT_003 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ROKEBY 7 (650290) 115.0 kV to 27&PLR 7 (650229) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LES_FAULT_004 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ROKEBY 7 (650290) 115.0 kV to ROKEBY 1G (650091) 13.8 kV Two Winding #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 3G (650093) 13.8 kV Two Winding #1 b.3. ROKEBY 1G (650091) 13.8 kV to Generator #1 b.4. ROKEBY 1G (650091) 13.8 kV to Load #S1 b.5. ROKEBY 1G (650091) 13.8 kV to remove bus # b.7. ROKEBY 3G (650093) 13.8 kV to Generator #3 b.8. ROKEBY 3G (650093) 13.8 kV to Load #S1 b.9. ROKEBY 3G (650093) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LES_FAULT_005 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LES_FAULT_006 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_LES_FAULT_007 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. ROKEBY 1G (650091) 13.8 kV to Generator #1 b.2. ROKEBY 3G (650093) 13.8 kV to Generator #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_OPPD_FAULT_001 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP2_P4_OPPD_FAULT_002 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 25.5 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1244 5 (646244) 161.0 kV to Load #O0 b.4. S1244 5 (646244) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_001 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on W LINCOLN 7 115.00 (650208) 115 kV Bus a. Apply fault at the W LINCOLN 7 115.00 (650208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_003 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_004 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_005 | 3 Phase fault on 8&N 7 115.00 (650217) 115 kV Bus a. Apply fault at the 8&N 7 115.00 (650217) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_006 | 3 Phase fault on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_007 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_008 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_009 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_010 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_011 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_012 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_013 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_014 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_015 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_016 | 3 Phase fault on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_017 | 3 Phase fault on 93&O 7 115.00 (650273) 115 kV Bus a. Apply fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_018 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_019 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_020 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_021 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_022 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_023 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_024 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on COOPER1G 22.000 (640009) 22 kV Bus a. Apply fault at the COOPER1G 22.000 (640009) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER1G (640009) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on NW56&MORTN7 115.00 (650207) 115 kV Bus a. Apply fault at the NW56&MORTN7 115.00 (650207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.6. 40&ROKEBY 7 (650250) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 70&CALVERT7 (650270) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_065 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power Oscillations are oberserved at the Grand Prairie Wind Farm (645065, 645066, 645067 and 645068) following the fault and the units are tripped due to internal protection before reaching the 10 second post-fault time mark. The issue is resolved when the critical clearing time is reduced to 3 cycles. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_068 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_069 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_070 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_071 | 3 Phase fault on SUB-H G 115.00 (642066) 115 kV Bus a. Apply fault at the SUB-H G 115.00 (642066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-H G (642066) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_072 | 3 Phase fault on SUB-C 7 115.00 (642070) 115 kV Bus a. Apply fault at the SUB-C 7 115.00 (642070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-C 7 (642070) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_073 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_074 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_075 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_076 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to STOCKVL8 (640366) 69.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 b.4. STOCKVLLET19 (643146) 13.8 kV to STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_077 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_078 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_079 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_080 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_081 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_082 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to FAIRBRYG (640170) 34.5 kV to FAIRBURY T19 (643056) 13.8 kV Three Winding #1 b.4. FAIRBURY T19 (643056) 13.8 kV to FAIRBRYG (640170) 34.5 kV to FAIRBRY7 (640169) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_083 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_084 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_085 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_086 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_087 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_088 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_089 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_090 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_091 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_092 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_093 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_094 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_095 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_096 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_097 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_098 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_099 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_100 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_101 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_102 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_103 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_104 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_105 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_106 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_107 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_108 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_109 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_110 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_111 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_112 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_113 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_114 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_115 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_116 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_117 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_118 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_119 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_120 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_121 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_122 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_123 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_124 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_125 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_126 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_127 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 b.2. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_128 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_129 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_130 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_131 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_132 | 3 Phase fault on CREITON8 69.000 (640150) 69 kV Bus a. Apply fault at the CREITON8 69.000 (640150) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_133 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_134 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_135 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_136 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_137 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_138 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_139 | 3 Phase fault on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHUYLR7 (640336) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_140 | 3 Phase fault on SILVRCK8 69.000 (640346) 69 kV Bus a. Apply fault at the SILVRCK8 69.000 (640346) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_141 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_142 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_143 | 3 Phase fault on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETERSBRG.N7 (640444) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_144 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_145 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_146 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_147 | 3 Phase fault on HOSKINS4 230.00 (640227) 345 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_148 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_149 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_150 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_151 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_152 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_153 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_154 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_155 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_156 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_157 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_158 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_159 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_160 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_161 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_162 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_163 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_164 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_165 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_166 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_167 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_168 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_169 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_170 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_171 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_172 | 3 Phase fault on NCU903 8 69.000 (647401) 69 kV Bus a. Apply fault at the NCU903 8 69.000 (647401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S962 8 (647962) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_173 | 3 Phase fault on S977 8 69.000 (647977) 69 kV Bus a. Apply fault at the S977 8 69.000 (647977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_174 | 3 Phase fault on S965 8 69.000 (647965) 69 kV Bus a. Apply fault at the S965 8 69.000 (647965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_175 | 3 Phase fault on S967 8 69.000 (647967) 69 kV Bus a. Apply fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_176 | 3 Phase fault on S969 8 69.000 (647969) 69 kV Bus a. Apply fault at the S969 8 69.000 (647969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.2. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.3. S968 8 (647968) 69.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_177 | 3 Phase fault on S973 8 69.000 (647973) 69 kV Bus a. Apply fault at the S973 8 69.000 (647973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_178 | 3 Phase fault on FREM D 8 69.000 (647424) 69 kV Bus a. Apply fault at the FREM D 8 69.000 (647424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM D 8 (647424) 69.0 kV to FREM E 8 (647425) 69.0 kV Transmission Circuit #1 b.2. FREM D 8 (647424) 69.0 kV to S976 8 (647976) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_179 | 3 Phase fault on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_180 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_181 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_182 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_183 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_184 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_185 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_186 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_187 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_188 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_189 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_190 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_192 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_193 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_194 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV Switched Shunt Device #//1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_195 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_196 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_197 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_198 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_199 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_200 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_201 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_202 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_203 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_204 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_205 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_206 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_207 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_210 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_211 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_212 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_213 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_214 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_215 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_216 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_217 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_218 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_219 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_220 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_221 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_222 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_224 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_226 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_227 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_228 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_229 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_232 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_233 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_234 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_235 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_236 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_237 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_238 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_239 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_240 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_241 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_242 | 3 Phase fault on BEAT. S7 115.00 (640074) 115 kV Bus a. Apply fault at the BEAT. S7 115.00 (640074) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_243 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_244 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_245 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_246 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_247 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_248 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_249 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_250 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_251 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_252 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_253 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_254 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_255 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_256 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_257 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_258 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_259 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_260 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_261 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_262 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_263 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_264 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_265 | 3 Phase fault on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_266 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_267 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_268 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_269 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_270 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_271 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_272 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_273 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_274 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_275 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_276 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_277 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_278 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_279 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_280 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_281 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_282 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_283 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_284 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_285 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_286 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_287 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_288 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_289 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_290 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_291 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_292 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_293 | 3 Phase fault on HARBINE7 115.00 (640208) 115 kV Bus a. Apply fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_295 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_296 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_297 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_298 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_299 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_300 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_301 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_302 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_303 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_304 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_305 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_306 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_307 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_308 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_309 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_310 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_311 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_312 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_313 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_314 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_315 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_316 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_317 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_318 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_320 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_321 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_322 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_323 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_324 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_325 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_326 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_327 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_328 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_329 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_330 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_331 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_332 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_333 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_334 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_335 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_336 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_337 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_338 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_339 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_340 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_341 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 3 (640529) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_342 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_343 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_344 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_345 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | The Laramie generating site (659118) loses synchronism after the fault. The issue is resolved when the critical clearing time is reduced to 5 cycles. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_347 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_348 | 3 Phase fault on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_349 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_350 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_351 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_352 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_353 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_354 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_355 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_356 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 8 (640085) 69.0 kV to BLMFLD 7 (640084) 115.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_357 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_358 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_359 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_360 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_361 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_362 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_363 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_364 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_365 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_366 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_367 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY8 (640417) 69.0 kV to RISNGCY7 (640328) 115.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_370 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_371 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_372 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 8 (640468) 69.0 kV to TAMORA 7 (640375) 115.0 kV to TAMORA T2 9 (643181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_373 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_374 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_375 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_376 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S966 8 (647966) 69.0 kV to STEINER7 (640361) 115.0 kV to STEINER T1 9 (643143) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_377 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_378 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_379 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_380 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_381 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_001 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_002 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_005 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_006 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_007 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_008 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_009 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_012 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_015 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_017 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_018 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_020 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_027 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_028 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_032 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_041 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_042 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_043 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_044 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_045 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_046 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_047 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_048 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MADISON3 345.00 (635635) 345 kV Bus a. Apply Fault at the MADISON3 345.00 (635635) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORIENT 3 (635570) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.2. BOONVIL3 (635630) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.3. MADISON3 (635635) 345.0 kV to NORWLK3 (635640) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.7. S1366 5 (646366) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.4. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.5. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T1 9 (643004) 13.8 kV Three Winding #1 b.6. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T2 9 (643005) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.4. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.3. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT19 (643032) 13.8 kV Three Winding #1 b.4. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT29 (643033) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 b.2. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.2. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.3. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T1 9 (643046) 4.2 kV Three Winding #1 b.4. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T2 9 (643047) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FREMONT7 115.00 (640173) 115 kV Bus a. Apply Fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.3. FREMONT7 (640173) 115.0 kV to S976 8 (647976) 69.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 b.4. FREMONT7 (640173) 115.0 kV to S976 8 (647976) 69.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.3. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.4. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.5. GENEVA 7 (640178) 115.0 kV to GENEVA 8 (640179) 69.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T1 9 (643064) 13.8 kV Three Winding #1 b.4. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T2 9 (643065) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HARBINE7 115.00 (640208) 115 kV Bus a. Apply Fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.3. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to KINGSLY7 (640255) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.3. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to MCCOOK G (640017) 13.8 kV Two Winding #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.4. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.5. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.6. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.4. MCCOOL 7 (640272) 115.0 kV to MCCOOL 8 (640273) 69.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on MINDEN 7 115.00 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 115.00 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.4. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply Fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.3. RISNGCY7 (640328) 115.0 kV to RISNGCY9 (640329) 34.5 kV to RISINGCTYT19 (643126) 13.8 kV Three Winding #1 b.4. RISNGCY7 (640328) 115.0 kV to RISNGCY8 (640417) 69.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply Fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.3. SCHUYLR7 (640336) 115.0 kV to SCHUYLR9 (640337) 34.5 kV to SCHUYLER T19 (643131) 13.8 kV Three Winding #1 b.4. SCHUYLR7 (640336) 115.0 kV to SCHUYLR9 (640337) 34.5 kV to SCHUYLER T29 (643132) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.3. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.4. SEWARD 7 (640340) 115.0 kV to SEWARD 9 (640341) 34.5 kV to SEWARD T1 9 (643134) 13.8 kV Three Winding #1 b.5. SEWARD 7 (640340) 115.0 kV to SEWARD 9 (640341) 34.5 kV to SEWARD T2 9 (643135) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.3. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T19 (643139) 13.8 kV Three Winding #1 b.4. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T29 (643169) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.3. THEDFRD7 (640381) 115.0 kV to THEDFRD9 (640382) 34.5 kV to THEDFORD T19 (643153) 13.8 kV Three Winding #1 b.4. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WAHOO 7 115.00 (640402) 115 kV Bus a. Apply Fault at the WAHOO 7 115.00 (640402) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.3. WAHOO 29 (648402) 13.8 kV to WAHOO 7 (640402) 115.0 kV Two Winding #1 b.4. WAHOO 7 (640402) 115.0 kV to WAHOO G (640403) 34.5 kV to WAHOO T1 9 (643163) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.4. YORK 7 (640411) 115.0 kV to YORK 9 (640412) 34.5 kV to YORK T1 9 (643166) 13.8 kV Three Winding #1 b.5. YORK 7 (640411) 115.0 kV to YORK 8 (640443) 69.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. YORK SW7 (640413) 115.0 kV to YORK SW9 (640414) 34.5 kV to YORK.SW T1 9 (643168) 13.8 kV Three Winding #1 b.4. YORK SW7 (640413) 115.0 kV to YORK.SW T2 8 (640447) 69.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to Load #NW b.2. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to Load #NW b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.3. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.4. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS9 (640137) 34.5 kV to Load #N0 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.5. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. E.COL. 4 (640126) 230.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.4. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT19 (643037) 13.8 kV Three Winding #1 b.5. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT29 (643038) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to Load #N2 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to Load #N2 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.4. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY9 (640251) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.8. KEARNEY7 (640250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 b.5. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to NORTHPLT T79 (643107) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply Fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z b.3. OGALALA9 (640303) 34.5 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T29 (643116) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 b.2. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on STEELEC7 115.00 (640426) 115 kV Bus a. Apply Fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.2. STEELEC9 (640427) 4.2 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 b.3. STEELEC7 (640426) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.7. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply Fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. ELKRDG.PLT D (640419) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.4. CROFTN.PLT D (640423) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.5. BLMFLD 7 (640084) 115.0 kV to BLMFLD 8 (640085) 69.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS9 (640137) 34.5 kV to Load #N0 b.2. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COLMBUS7 (640136) 115.0 kV to COLMBS1G (640006) 13.8 kV Two Winding #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS2G (640007) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.6. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.8. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.9. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.12. COLMBUS7 (640136) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.6. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on COL.COG7 115.00 (640119) 115 kV Bus a. Apply Fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 b.2. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.4. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.5. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.6. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT19 (643037) 13.8 kV Three Winding #1 b.7. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT29 (643038) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.5. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.6. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.7. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.8. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG9 (640225) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.5. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.10. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.3. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.4. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on STEELEC7 115.00 (640426) 115 kV Bus a. Apply Fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.2. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.3. STEELEC7 (640426) 115.0 kV to S.FLATS.PLT7 (640558) 115.0 kV Transmission Circuit #1 b.4. STEELEC9 (640427) 4.2 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 b.5. STEELEC_KXL9 (640440) 6.9 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.3. N.PLATTG (640018) 13.8 kV to N.PLATT9 (640289) 34.5 kV to N.PLATT7 (640287) 115.0 kV Three Winding #1 b.4. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.6. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus a. Apply Fault at the FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on KELLY 5 161.00 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.4. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.4. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.5. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply Fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.4. GRANTNB_-TS7 (659800) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.5. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.6. OGALALA_-TS7 (659801) 115.0 kV to MCONGHY_-TS7 (659824) 115.0 kV Transmission Circuit #1 b.7. ELSIETP_-TS7 (659807) 115.0 kV to PAXTON__-TS7 (659808) 115.0 kV Transmission Circuit #1 b.8. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.9. ELSIETP_-TS7 (659807) 115.0 kV to ELSIE___-TS7 (659822) 115.0 kV Transmission Circuit #1 b.10. MCONGHY_-TS7 (659824) 115.0 kV to ARTHUR__-TS7 (659825) 115.0 kV Transmission Circuit #1 b.11. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 b.12. OGALALA9 (640303) 34.5 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T29 (643116) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply Fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply Fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on 8&N 7 115.00 (650217) 115 kV Bus a. Apply Fault at the 8&N 7 115.00 (650217) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8&J 9 (650100) 34.5 kV to 171TERTIARY (650517) 34.5 kV Transmission Circuit #1 b.2. 8&N 7 (650217) 115.0 kV to 17&HOLDRGE7 (650219) 115.0 kV Transmission Circuit #1 b.3. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. 8&N 7 (650217) 115.0 kV to 8&N A9 (650317) 13.2 kV to 171TERTIARY (650517) 34.5 kV Three Winding #1 b.5. 8&N 7 (650217) 115.0 kV to 8&N B9 (650417) 13.2 kV to 172TERTIARY (650617) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&Q 7 (650260) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 30&A 7 (650252) 115.0 kV to 56&EVERETT7 (650256) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on 40&GERTIE 7 115.00 (650258) 115 kV Bus a. Apply Fault at the 40&GERTIE 7 115.00 (650258) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.5. 40&GERTIE 7 (650258) 115.0 kV to 40&GE A9 (650358) 13.2 kV to 581TERTIARY (650558) 7.2 kV Three Winding #1 b.6. 40&GERTIE 7 (650258) 115.0 kV to 40&GE B9 (650458) 13.2 kV to 582TERTIARY (650658) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.4. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.5. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.6. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.9. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.5. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 b.11. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 3G (650093) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 1G (650091) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply Fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.3. 27&PLR 7 (650229) 115.0 kV to 27&PLR A9 (650329) 12.5 kV to 291TERTIARY (650529) 7.2 kV Three Winding #1 b.4. 27&PLR 7 (650229) 115.0 kV to 27&PLR B9 (650429) 12.5 kV to 292TERTIARY (650629) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.5. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.6. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply Fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on 56&PLR 7 115.00 (650255) 115 kV Bus a. Apply Fault at the 56&PLR 7 115.00 (650255) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on NW12&ARBOR7 115.00 (650226) 115 kV Bus a. Apply Fault at the NW12&ARBOR7 115.00 (650226) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 b.2. NW56&MORTN7 (650207) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.3. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.4. 19&ALVO 7 (650215) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.5. NW70FAIRFD7 (650210) 115.0 kV to NW70FAIRFD9 (650310) 12.5 kV to 101TERTIARY (650510) 7.2 kV Three Winding #1 b.6. NW12&ARBOR7 (650226) 115.0 kV to NW12&AR 9 (650326) 12.5 kV to 261TERTIARY (650526) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on NW5&BENTON7 115.00 (650212) 115 kV Bus a. Apply Fault at the NW5&BENTON7 115.00 (650212) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4&MORTON 7 (650205) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.2. W LINCOLN 7 (650208) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.3. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. W LINCOLN 7 (650208) 115.0 kV to WLINCOLN 9 (650308) 13.2 kV to 084TERTIARY (650508) 7.2 kV Three Winding #1 b.5. NW5&BENTON7 (650212) 115.0 kV to NW5BENTN 9 (650312) 12.5 kV to 121TERTIARY (650512) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.7. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 b.2. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S967 8 69.000 (647967) 69 kV Bus a. Apply Fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.2. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on S968 8 69.000 (647968) 69 kV Bus a. Apply Fault at the S968 8 69.000 (647968) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.2. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.4. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply Fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. NC SYRA8 (647402) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.5. NC SYRA8 (647402) 69.0 kV to S971 8 (647971) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on S974 8 69.000 (647974) 69 kV Bus a. Apply Fault at the S974 8 69.000 (647974) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.2. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.3. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.5. S968 8 (647968) 69.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on STERLNG7 115.00 (640362) 115 kV Bus a. Apply Fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.5. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.2. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.3. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 b.5. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on S993 8 69.000 (647993) 69 kV Bus a. Apply Fault at the S993 8 69.000 (647993) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.5. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.6. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.7. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply Fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.5. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.4. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 b.5. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 b.4. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 b.5. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on EAST 5 161.00 (541254) 161 kV Bus a. Apply Fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on IND PRK5 161.00 (541256) 161 kV Bus a. Apply Fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 b.2. IND PRK5 (541256) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on G13-002-TAP 115.00 (560746) 115 kV Bus a. Apply Fault at the G13-002-TAP 115.00 (560746) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G13-002-TAP (560746) 115.0 kV to GEN-2013-019 (583700) 115.0 kV Transmission Circuit #1 b.2. G13-002-TAP (560746) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-023 (584650) 345.0 kV to G15-023XFMR2 (584654) 34.5 kV to G15-023-TER2 (584659) 13.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on GEN-2015-088345.00 (585241) 345 kV Bus a. Apply Fault at the GEN-2015-088345.00 (585241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-088 (585241) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-088 (585241) 345.0 kV to G15-088-XF-2 (585249) 34.5 kV to G15-088-TR-1 (906007) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RLHILLS3 (635100) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on S HILLS 3 345.00 (635568) 345 kV Bus a. Apply Fault at the S HILLS 3 345.00 (635568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HILLS 3 (635568) 345.0 kV to BOONVIL3 (635630) 345.0 kV Transmission Circuit #1 b.2. S HILLS 3 (635568) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply Fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #2 b.2. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on CLATONA7 115.00 (640111) 115 kV Bus a. Apply Fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CO.LINE7 (640115) 115.0 kV to BATTLCR7 (640072) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to HAYSTACK.WD3 (640598) 345.0 kV Transmission Circuit #1 b.2. TURTLE.CRK 3 (640588) 345.0 kV to PLUMBCR.W 3 (643271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on GEN-2017-181345.00 (761292) 345 kV Bus a. Apply Fault at the GEN-2017-181345.00 (761292) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-181 (761292) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-181 (761292) 345.0 kV to GEN-2017-182 (761313) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on GEN-2017-183345.00 (761376) 345 kV Bus a. Apply Fault at the GEN-2017-183345.00 (761376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-183 (761376) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-183 (761376) 345.0 kV to G17-184XFMR2 (761401) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply Fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-065-TAP (763031) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 b.2. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply Fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 b.2. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. GENOA 7 (640181) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply Fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCHUYLR7 (640336) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. SCHUYLR7 (640336) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z b.2. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SD.LS-KS-MB3 (659425) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to None Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to J748POI (87487) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on COOK 5 161.00 (541257) 161 kV Bus a. Apply Fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOK 5 (541257) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on WOODBIN5 161.00 (541258) 161 kV Bus a. Apply Fault at the WOODBIN5 161.00 (541258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODBIN5 (541258) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. WOODBIN5 (541258) 161.0 kV to EAST 5 (541254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on AVENUECTY 5 161.00 (541394) 161 kV Bus a. Apply Fault at the AVENUECTY 5 161.00 (541394) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVENUECTY 5 (541394) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 b.2. AVENUECTY 5 (541394) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on GEN-2013-019115.00 (583700) 115 kV Bus a. Apply Fault at the GEN-2013-019115.00 (583700) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2013-019 (583700) 115.0 kV to G13-002-TAP (560746) 115.0 kV Transmission Circuit #1 b.2. GEN-2013-019 (583700) 115.0 kV to G13-019XFMR1 (583701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on ORIENT 3 345.00 (635570) 345 kV Bus a. Apply Fault at the ORIENT 3 345.00 (635570) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORIENT 3 (635570) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.2. ORIENT 3 (635570) 345.0 kV to S HILLS 3 (635568) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on G18-131-TAP 345.00 (763443) 345 kV Bus a. Apply Fault at the G18-131-TAP 345.00 (763443) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-131-TAP (763443) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 b.2. G18-131-TAP (763443) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on G19-069-TAP 345.00 (763982) 345 kV Bus a. Apply Fault at the G19-069-TAP 345.00 (763982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-069-TAP (763982) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. G19-069-TAP (763982) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on STEINER7 115.00 (640361) 115 kV Bus a. Apply Fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEINER7 (640361) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. STEINER7 (640361) 115.0 kV to HUMBOLT7 (640235) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on GEN-2017-210345.00 (761208) 345 kV Bus a. Apply Fault at the GEN-2017-210345.00 (761208) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-210 (761208) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-210 (761208) 345.0 kV to G17-210-XFMR (761209) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on GEN-2017-144345.00 (760767) 345 kV Bus a. Apply Fault at the GEN-2017-144345.00 (760767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-144 (760767) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-144 (760767) 345.0 kV to G17-144XFMR2 (760771) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on HAYSTACK.WD3345.00 (640598) 345 kV Bus a. Apply Fault at the HAYSTACK.WD3345.00 (640598) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSTACK.WD3 (640598) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. HAYSTACK.WD3 (640598) 345.0 kV to HAYSTCK.C2 9 (643293) 34.5 kV to HAYSTCK.T2 9 (643298) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on GEN-2017-201345.00 (760788) 345 kV Bus a. Apply Fault at the GEN-2017-201345.00 (760788) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-201 (760788) 345.0 kV to G17-201XFMR1 (760789) 34.5 kV Two Winding #1 b.2. GEN-2017-201 (760788) 345.0 kV to SHOLES.W 3 (640589) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on GEN-2017-182345.00 (761313) 345 kV Bus a. Apply Fault at the GEN-2017-182345.00 (761313) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-182 (761313) 345.0 kV to GEN-2017-181 (761292) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-182 (761313) 345.0 kV to G17-182XFMR1 (761314) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on GEN-2017-105161.00 (762070) 161 kV Bus a. Apply Fault at the GEN-2017-105161.00 (762070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-105 (762070) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-105 (762070) 161.0 kV to G17-105XFM1 (762071) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-043 (762780) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-043 (762780) 345.0 kV to G18-043-XFM1 (762781) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on G19-039-TAP 115.00 (763718) 115 kV Bus a. Apply Fault at the G19-039-TAP 115.00 (763718) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-039-TAP (763718) 115.0 kV to RISNGCY7 (640328) 115.0 kV Transmission Circuit #1 b.2. G19-039-TAP (763718) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply Fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILVRCK7 (640345) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. SILVRCK7 (640345) 115.0 kV to CENCITY7 (640107) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply Fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply Fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 115.00 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 115.00 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1280 5 (646280) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESTON7 (640151) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_001 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_002 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_003 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.3. COOPER1G (640009) 22.0 kV to Generator #1 b.4. COOPER1G (640009) 22.0 kV to Load #S1 b.5. COOPER1G (640009) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_004 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 14.5 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 b.3. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_005 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_006 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_007 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_008 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_NPPD_FAULT_009 | Single Phase Fault with Stuck Breaker on COLMBUS4 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 (640133) 230 kV Bus b. Clear Fault after 8.5 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to COLMB.W4 (640131) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_TSGT_FAULT_001 | Single Phase Fault with Stuck Breaker on SIDNEY (MBPP) (659210) 230 kV Bus a. Apply Fault at the SIDNEY (MBPP) (659210) 230 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.2. SIDNEY___TS4 (659134) 230.0 kV to remove bus # b.3. SIDNEY__-MB4 (659210) 230.0 kV to remove bus # b.4. SIDNEY__-TS8 (659803) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LES_FAULT_001 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LES_FAULT_002 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LES_FAULT_003 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ROKEBY 7 (650290) 115.0 kV to 27&PLR 7 (650229) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LES_FAULT_004 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ROKEBY 7 (650290) 115.0 kV to ROKEBY 1G (650091) 13.8 kV Two Winding #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 3G (650093) 13.8 kV Two Winding #1 b.3. ROKEBY 1G (650091) 13.8 kV to Generator #1 b.4. ROKEBY 1G (650091) 13.8 kV to Load #S1 b.5. ROKEBY 1G (650091) 13.8 kV to remove bus # b.7. ROKEBY 3G (650093) 13.8 kV to Generator #3 b.8. ROKEBY 3G (650093) 13.8 kV to Load #S1 b.9. ROKEBY 3G (650093) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LES_FAULT_005 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LES_FAULT_006 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_LES_FAULT_007 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. ROKEBY 1G (650091) 13.8 kV to Generator #1 b.2. ROKEBY 3G (650093) 13.8 kV to Generator #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_OPPD_FAULT_001 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP2_P4_OPPD_FAULT_002 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 25.5 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1244 5 (646244) 161.0 kV to Load #O0 b.4. S1244 5 (646244) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power Oscillations are oberserved at the Grand Prairie Wind Farm (645065, 645066, 645067 and 645068) following the fault and the units are tripped due to internal protection before reaching the 10 second post-fault time mark. The issue is resolved when the critical clearing time is reduced to 3 cycles. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | The Laramie generating site (659118) loses synchronism after the fault. The issue is resolved when the critical clearing time is reduced to 4 cycles. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power Oscillations are oberserved at the Grand Prairie Wind Farm (645065, 645066, 645067 and 645068) following the fault and the units are tripped due to internal protection before reaching the 10 second post-fault time mark. The issue is resolved when the critical clearing time is reduced to 3 cycles. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | The Laramie generating site (659118) loses synchronism after the fault. The issue is resolved when the critical clearing time is reduced to 4 cycles. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on HOL387 5 161.00 (547482) 161 kV Bus a. Apply fault at the HOL387 5 161.00 (547482) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.2. HOL387 5 (547482) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on RDS295 5 161.00 (547473) 161 kV Bus a. Apply fault at the RDS295 5 161.00 (547473) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on BRN331 5 161.00 (547475) 161 kV Bus a. Apply fault at the BRN331 5 161.00 (547475) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.2. BRN331 5 (547475) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on GRT433 5 161.00 (547495) 161 kV Bus a. Apply fault at the GRT433 5 161.00 (547495) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRN412 5 (547488) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 b.2. BRN413 5 (547489) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on RVS438 5 161.00 (547497) 161 kV Bus a. Apply fault at the RVS438 5 161.00 (547497) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVS438 5 (547497) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.5. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.6. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on MANVILE3 115.00 (533426) 115 kV Bus a. Apply fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on REFINRY3 115.00 (533427) 115 kV Bus a. Apply fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on HEC 2 69.000 (533513) 69 kV Bus a. Apply fault at the HEC 2 69.000 (533513) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 2 (533513) 69.0 kV to 17HALST2 (533521) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7BLAND (344154) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7LOOSECRK (344327) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to 5OSAGE CRK#! (338682) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.3. BUFORD 5 (504440) 161.0 kV to NORFORK5 (505448) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.2. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on OZD312 5 161.00 (547474) 161 kV Bus a. Apply fault at the OZD312 5 161.00 (547474) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZD312 5 (547474) 161.0 kV to OZD312 2 (547562) 69.0 kV to OZD312T1 (547710) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on BRN413 5 161.00 (547489) 161 kV Bus a. Apply fault at the BRN413 5 161.00 (547489) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRN413 5 (547489) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on 5OMAHA+ 161.00 (338105) 161 kV Bus a. Apply fault at the 5OMAHA+ 161.00 (338105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HARRISON.E! (338104) 161.0 kV to 5OMAHA+ (338105) 161.0 kV Transmission Circuit #1 b.2. 5OMAHA+ (338105) 161.0 kV to 5OMAHA (338106) 161.0 kV Transmission Circuit #1 b.3. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_082 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_083 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_086 | 3 Phase fault on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_087 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_088 | 3 Phase fault on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_089 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_090 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_091 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_092 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_093 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_094 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_095 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_096 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_097 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_098 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_099 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_100 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_101 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_102 | 3 Phase fault on CORONAD3 115.00 (533394) 115 kV Bus a. Apply fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_103 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_104 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_105 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_106 | 3 Phase fault on 43LORAN 115.00 (533440) 115 kV Bus a. Apply fault at the 43LORAN 115.00 (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_107 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_108 | 3 Phase fault on BYRONTP4 138.00 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 138.00 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.2. CHRKCTY4 (520431) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.3. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. BYRONTP4 (520432) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.5. BYRONTP4 (520432) 138.0 kV to BYRON 4 (520477) 138.0 kV Transmission Circuit #1 b.6. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.7. SANDYCR4 (520433) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.8. SANDYCR4 (520433) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.9. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_109 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_110 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_111 | 3 Phase fault on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.3. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_112 | 3 Phase fault on BYPASJT2 69.000 (543084) 69 kV Bus a. Apply fault at the BYPASJT2 69.000 (543084) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYJT2 (543079) 69.0 kV to BYPASJT2 (543084) 69.0 kV Transmission Circuit #1 b.2. BYPASJT2 (543084) 69.0 kV to IND WTR2 (543086) 69.0 kV Transmission Circuit #1 b.3. BYPASJT2 (543084) 69.0 kV to LIBRTYS2 (543095) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_113 | 3 Phase fault on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_114 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_115 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_116 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_117 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_118 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_119 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_120 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_121 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_122 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_123 | 3 Phase fault on SALTCRK3 115.00 (533434) 115 kV Bus a. Apply fault at the SALTCRK3 115.00 (533434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_124 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_126 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_128 | 3 Phase fault on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_130 | 3 Phase fault on FROSTRD_CAP5161.00 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5161.00 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_132 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_133 | 3 Phase fault on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_135 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. NICHOL XF1 1 (549940) 13.2 kV to NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_136 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.3. MILL XF1 1 (549946) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 b.3. MILL XF2 1 (549948) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_138 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_139 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_140 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_141 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_142 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_143 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_144 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_145 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_146 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_147 | 3 Phase fault on SUB B 69.000 (548810) 69 kV Bus a. Apply fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_148 | 3 Phase fault on SUB J 69.000 (548811) 69 kV Bus a. Apply fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_149 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_150 | 3 Phase fault on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_151 | 3 Phase fault on KCPL JCT 69.000 (548832) 69 kV Bus a. Apply fault at the KCPL JCT 69.000 (548832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB F (548803) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 b.2. SUB E (548804) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_152 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_153 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_154 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_155 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_156 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_157 | 3 Phase fault on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_158 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_159 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (543064) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_160 | 3 Phase fault on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCRK_S2 (543163) 69.0 kV Transmission Circuit #z1 b.2. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.3. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.4. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.5. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_161 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_162 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_163 | 3 Phase fault on 3 VANBU3 115.00 (533435) 115 kV Bus a. Apply fault at the 3 VANBU3 115.00 (533435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3 VANBU3 (533435) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_164 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_165 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_166 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_167 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_168 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_169 | 3 Phase fault on CRAWFRD3 115.00 (533364) 115 kV Bus a. Apply fault at the CRAWFRD3 115.00 (533364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD3 (533364) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 b.3. MENTOR 3 (533374) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_170 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_171 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_172 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_173 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_174 | 3 Phase fault on WPRTTS 2 69.000 (530596) 69 kV Bus a. Apply fault at the WPRTTS 2 69.000 (530596) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.2. GB STH 2 (530569) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.4. WPRTTS 2 (530596) 69.0 kV to WPRT2 2 (530597) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_175 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_176 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_177 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_178 | 3 Phase fault on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_179 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_180 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_181 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_182 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_183 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_184 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_185 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_186 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_187 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_188 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_189 | 3 Phase fault on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_190 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_191 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_192 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_193 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_194 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_195 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_196 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_197 | 3 Phase fault on BUSHTON3 115.00 (530681) 115 kV Bus a. Apply fault at the BUSHTON3 115.00 (530681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHTON3 (530681) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_198 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_199 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_200 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_201 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_202 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_203 | 3 Phase fault on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_204 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_205 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_206 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_207 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_208 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_209 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_210 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_211 | 3 Phase fault on OTISSUB3 115.00 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 115.00 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding #1 b.3. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS2-T (539926) 2.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_212 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_213 | 3 Phase fault on EUREKA 5 161.00 (506932) 161 kV Bus a. Apply fault at the EUREKA 5 161.00 (506932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.2. 5OSAGE CRK#! (338682) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.3. BEAVER 5 (505480) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_214 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_215 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_216 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_217 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_218 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_219 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_220 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_221 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_222 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_223 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_224 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_225 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_226 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_227 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_228 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_229 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_230 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_231 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_232 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_233 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_234 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_235 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_236 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_237 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_238 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_239 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_240 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_241 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_242 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_243 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_244 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_245 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_246 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_247 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_248 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_249 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_250 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_251 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_252 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_253 | 3 Phase fault on SUNCITY3 115.00 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 115.00 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_254 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_255 | 3 Phase fault on ST JOHN3 115.00 (530624) 115 kV Bus a. Apply fault at the ST JOHN3 115.00 (530624) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_256 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_257 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_258 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_259 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_260 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_261 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_262 | 3 Phase fault on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_263 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_264 | 3 Phase fault on N-DODGE3 115.00 (539680) 115 kV Bus a. Apply fault at the N-DODGE3 115.00 (539680) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DODG3 (539641) 115.0 kV to N-DODGE3 (539680) 115.0 kV Transmission Circuit #1 b.2. N-DODGE3 (539680) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. N-DODGE3 (539680) 115.0 kV to N-DODGE1 (539720) 34.5 kV to N-DODG-T (539922) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_265 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_266 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_267 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_268 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_269 | 3 Phase fault on BARBER 4 138.00 (539674) 138 kV Bus a. Apply fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_270 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_271 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_272 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_273 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_274 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_275 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_276 | 3 Phase fault on ELLSWTH3 115.00 (539662) 115 kV Bus a. Apply fault at the ELLSWTH3 115.00 (539662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTH3 (539662) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_277 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_278 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_279 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_280 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_281 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7SALEMTP (300472) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_282 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_283 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_284 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_285 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_286 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_287 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_288 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_289 | 3 Phase fault on 7FRANKSRCTP 345.00 (300051) 345 kV Bus a. Apply fault at the 7FRANKSRCTP 345.00 (300051) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKSRCTP (300051) 345.0 kV to 7FRANKSRCT (301554) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_290 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_291 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_292 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_293 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_294 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_295 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_296 | 3 Phase fault on 5COFFMN 161.00 (300072) 161 kV Bus a. Apply fault at the 5COFFMN 161.00 (300072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COFFMN (300072) 161.0 kV to 5HUBEN (300088) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_297 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_298 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_299 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5MRSHFL (300102) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_300 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5PHLIPS (300109) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_301 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5WHISPR (301077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_302 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_303 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_304 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_305 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_306 | 3 Phase fault on 5MANSFDMN 161.00 (300095) 161 kV Bus a. Apply fault at the 5MANSFDMN 161.00 (300095) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_307 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_308 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_309 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_310 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_311 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_312 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_313 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_314 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_315 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_316 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_317 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_318 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_319 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_320 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_321 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_322 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_323 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_324 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_325 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_326 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_327 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_328 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_329 | 3 Phase fault on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_330 | 3 Phase fault on 2BEAMAN 69.000 (300527) 69 kV Bus a. Apply fault at the 2BEAMAN 69.000 (300527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEAMAN (300527) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_331 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_332 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_333 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_334 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_335 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_336 | 3 Phase fault on 2HUGHSV 69.000 (300533) 69 kV Bus a. Apply fault at the 2HUGHSV 69.000 (300533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HUGHSV (300533) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_337 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_338 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_339 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_340 | 3 Phase fault on 2MALTAB 69.000 (300535) 69 kV Bus a. Apply fault at the 2MALTAB 69.000 (300535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAB (300535) 69.0 kV to 2MALTAJ (300536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_341 | 3 Phase fault on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2MARSHL (300537) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_342 | 3 Phase fault on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_343 | 3 Phase fault on 2MARSHL 69.000 (300537) 69 kV Bus a. Apply fault at the 2MARSHL 69.000 (300537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MARSHL (300537) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_344 | 3 Phase fault on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_345 | 3 Phase fault on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2PILOTG (300560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_346 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_347 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_348 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2FLORNC (300553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_349 | 3 Phase fault on 2SWSPJC 69.000 (300543) 69 kV Bus a. Apply fault at the 2SWSPJC 69.000 (300543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SWSPJC (300543) 69.0 kV to 2SWSPNG (300544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_350 | 3 Phase fault on 2FLORNC 69.000 (300553) 69 kV Bus a. Apply fault at the 2FLORNC 69.000 (300553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FLORNC (300553) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_351 | 3 Phase fault on 2IVYBND 69.000 (300557) 69 kV Bus a. Apply fault at the 2IVYBND 69.000 (300557) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IVYBND (300557) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_352 | 3 Phase fault on 2MTHULD 69.000 (300558) 69 kV Bus a. Apply fault at the 2MTHULD 69.000 (300558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MTHULD (300558) 69.0 kV to 2STOVER (300562) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_353 | 3 Phase fault on 2KENOMA 69.000 (300650) 69 kV Bus a. Apply fault at the 2KENOMA 69.000 (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV to 2LOCKWD (300676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_354 | 3 Phase fault on 2MILO 69.000 (300654) 69 kV Bus a. Apply fault at the 2MILO 69.000 (300654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MILO (300654) 69.0 kV to 2CLARK (300802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_355 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_356 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_357 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_358 | 3 Phase fault on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BILLNG (300658) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_359 | 3 Phase fault on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BILLNG (300658) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_360 | 3 Phase fault on 2BOWRML 69.000 (300659) 69 kV Bus a. Apply fault at the 2BOWRML 69.000 (300659) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOWRML (300659) 69.0 kV to 2ROUNDGRVETP (301395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_361 | 3 Phase fault on 2BOWRML 69.000 (300659) 69 kV Bus a. Apply fault at the 2BOWRML 69.000 (300659) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOWRML (300659) 69.0 kV to ALB262 2 (547553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_362 | 3 Phase fault on 2CAPEFR 69.000 (300662) 69 kV Bus a. Apply fault at the 2CAPEFR 69.000 (300662) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CAPEFR (300662) 69.0 kV to 2FLTCRK (300671) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_363 | 3 Phase fault on 2CAPEFR 69.000 (300662) 69 kV Bus a. Apply fault at the 2CAPEFR 69.000 (300662) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CAPEFR (300662) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_364 | 3 Phase fault on 2CLEVER 69.000 (300665) 69 kV Bus a. Apply fault at the 2CLEVER 69.000 (300665) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVER (300665) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_365 | 3 Phase fault on 2CRANE 69.000 (300667) 69 kV Bus a. Apply fault at the 2CRANE 69.000 (300667) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CRANE (300667) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_366 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2GRNFLD (300672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_367 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_368 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2BONA (300800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_369 | 3 Phase fault on 2ELWOOD 69.000 (300669) 69 kV Bus a. Apply fault at the 2ELWOOD 69.000 (300669) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_370 | 3 Phase fault on 2GRNFLD 69.000 (300672) 69 kV Bus a. Apply fault at the 2GRNFLD 69.000 (300672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRNFLD (300672) 69.0 kV to 2LOCKWD (300676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_371 | 3 Phase fault on 2GRNFLD 69.000 (300672) 69 kV Bus a. Apply fault at the 2GRNFLD 69.000 (300672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRNFLD (300672) 69.0 kV to 2ARCOLA (300797) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_372 | 3 Phase fault on 2GRNFLD 69.000 (300672) 69 kV Bus a. Apply fault at the 2GRNFLD 69.000 (300672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRNFLD (300672) 69.0 kV to 2ROUNDGRVETP (301395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_373 | 3 Phase fault on 2MTVRN 69.000 (300677) 69 kV Bus a. Apply fault at the 2MTVRN 69.000 (300677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MTVRN (300677) 69.0 kV to 2MIDWYTP (300684) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_374 | 3 Phase fault on 2MTVRN 69.000 (300677) 69 kV Bus a. Apply fault at the 2MTVRN 69.000 (300677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MTVRN (300677) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_375 | 3 Phase fault on 5NIXA-1 161.00 (300678) 161 kV Bus a. Apply fault at the 5NIXA-1 161.00 (300678) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_376 | 3 Phase fault on 2PRDYTP 69.000 (300679) 69 kV Bus a. Apply fault at the 2PRDYTP 69.000 (300679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PRDYTP (300679) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_377 | 3 Phase fault on 2VERONA 69.000 (300680) 69 kV Bus a. Apply fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_378 | 3 Phase fault on 2MIDWY 69.000 (300683) 69 kV Bus a. Apply fault at the 2MIDWY 69.000 (300683) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIDWY (300683) 69.0 kV to 2MIDWYTP (300684) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_379 | 3 Phase fault on 2MIDWYTP 69.000 (300684) 69 kV Bus a. Apply fault at the 2MIDWYTP 69.000 (300684) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIDWYTP (300684) 69.0 kV to ALB262 2 (547553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_380 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_381 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_382 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_383 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_384 | 3 Phase fault on 2BEARCK 69.000 (300713) 69 kV Bus a. Apply fault at the 2BEARCK 69.000 (300713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEARCK (300713) 69.0 kV to 2GRTNA (300720) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_385 | 3 Phase fault on 2BEARCK 69.000 (300713) 69 kV Bus a. Apply fault at the 2BEARCK 69.000 (300713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEARCK (300713) 69.0 kV to 2ROCKWY (300728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_386 | 3 Phase fault on 2BLUWTP 69.000 (300714) 69 kV Bus a. Apply fault at the 2BLUWTP 69.000 (300714) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLUWTP (300714) 69.0 kV to 2BLUWTR (300715) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_387 | 3 Phase fault on 2BLUWTP 69.000 (300714) 69 kV Bus a. Apply fault at the 2BLUWTP 69.000 (300714) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLUWTP (300714) 69.0 kV to 2KMBRLNTP (300721) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_388 | 3 Phase fault on 2BLUWTP 69.000 (300714) 69 kV Bus a. Apply fault at the 2BLUWTP 69.000 (300714) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLUWTP (300714) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_389 | 3 Phase fault on 2BRANSN 69.000 (300716) 69 kV Bus a. Apply fault at the 2BRANSN 69.000 (300716) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRANSN (300716) 69.0 kV to 2ROCKWY (300728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_390 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_391 | 3 Phase fault on 2GRTNA 69.000 (300720) 69 kV Bus a. Apply fault at the 2GRTNA 69.000 (300720) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRTNA (300720) 69.0 kV to 2REEDSP (300725) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_392 | 3 Phase fault on 2KMBRLNTP 69.000 (300721) 69 kV Bus a. Apply fault at the 2KMBRLNTP 69.000 (300721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KMBRLNTP (300721) 69.0 kV to 2STONBR (300733) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_393 | 3 Phase fault on 2KMBRLNTP 69.000 (300721) 69 kV Bus a. Apply fault at the 2KMBRLNTP 69.000 (300721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KMBRLNTP (300721) 69.0 kV to 2KMBRLN (301625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_394 | 3 Phase fault on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAKE-K (300722) 69.0 kV to 2REEDSP (300725) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_395 | 3 Phase fault on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAKE-K (300722) 69.0 kV to 2SILDOL (300730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_396 | 3 Phase fault on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAKE-K (300722) 69.0 kV to 2STONBR (300733) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_397 | 3 Phase fault on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAKE-K (300722) 69.0 kV to 2STULTS (300734) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_398 | 3 Phase fault on 2PARDIS 69.000 (300723) 69 kV Bus a. Apply fault at the 2PARDIS 69.000 (300723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PARDIS (300723) 69.0 kV to TABLE R2 (505474) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_399 | 3 Phase fault on 2ROCKWY 69.000 (300728) 69 kV Bus a. Apply fault at the 2ROCKWY 69.000 (300728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROCKWY (300728) 69.0 kV to 2TANYVL (300736) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_400 | 3 Phase fault on 2SILDOL 69.000 (300730) 69 kV Bus a. Apply fault at the 2SILDOL 69.000 (300730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILDOL (300730) 69.0 kV to 2T.ROCKSW (301360) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_401 | 3 Phase fault on 2SPOKAN 69.000 (300732) 69 kV Bus a. Apply fault at the 2SPOKAN 69.000 (300732) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SPOKAN (300732) 69.0 kV to 2RENOHLW (300738) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_402 | 3 Phase fault on 2STULTS 69.000 (300734) 69 kV Bus a. Apply fault at the 2STULTS 69.000 (300734) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STULTS (300734) 69.0 kV to 2RENOHLW (300738) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_403 | 3 Phase fault on 2T.ROCK 69.000 (300735) 69 kV Bus a. Apply fault at the 2T.ROCK 69.000 (300735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2T.ROCK (300735) 69.0 kV to TABLE R2 (505474) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_404 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_405 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_406 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_407 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2MARCH (300781) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_408 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2POLK (300786) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_409 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_410 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2WOODHL (300791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_411 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2LONGLN (301068) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_412 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_413 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_414 | 3 Phase fault on 2FAIRGR 69.000 (300775) 69 kV Bus a. Apply fault at the 2FAIRGR 69.000 (300775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRGR (300775) 69.0 kV to 2PLEAST (300785) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_415 | 3 Phase fault on 2PLEAST 69.000 (300785) 69 kV Bus a. Apply fault at the 2PLEAST 69.000 (300785) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PLEAST (300785) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_416 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_417 | 3 Phase fault on 2ARCOLA 69.000 (300797) 69 kV Bus a. Apply fault at the 2ARCOLA 69.000 (300797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ARCOLA (300797) 69.0 kV to 2HYDERHL (300798) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_418 | 3 Phase fault on 2HYDERHL 69.000 (300798) 69 kV Bus a. Apply fault at the 2HYDERHL 69.000 (300798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HYDERHL (300798) 69.0 kV to 2ARNICA (300799) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_419 | 3 Phase fault on 2HYDERHL 69.000 (300798) 69 kV Bus a. Apply fault at the 2HYDERHL 69.000 (300798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HYDERHL (300798) 69.0 kV to 2CEDRSP (300801) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_420 | 3 Phase fault on 2CLARK 69.000 (300802) 69 kV Bus a. Apply fault at the 2CLARK 69.000 (300802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 2WALKER (300814) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_421 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_422 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_423 | 3 Phase fault on 2T.ROCKSW 69.000 (301360) 69 kV Bus a. Apply fault at the 2T.ROCKSW 69.000 (301360) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2T.ROCKSW (301360) 69.0 kV to TABLE R2 (505474) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_424 | 3 Phase fault on 2ROUNDGROVE 69.000 (301393) 69 kV Bus a. Apply fault at the 2ROUNDGROVE 69.000 (301393) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROUNDGROVE (301393) 69.0 kV to 2ROUNDGRVETP (301395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_425 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_426 | 3 Phase fault on 5MCBAINB2 161.00 (301489) 161 kV Bus a. Apply fault at the 5MCBAINB2 161.00 (301489) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_427 | 3 Phase fault on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_428 | 3 Phase fault on 5LOYMART 2 161.00 (344041) 161 kV Bus a. Apply fault at the 5LOYMART 2 161.00 (344041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_429 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_430 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_431 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_432 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_433 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2MACON_AM (346096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_434 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2DUPONT (346169) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_435 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2ROTH TAP (346170) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_436 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2SPRK TAP (346171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_437 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_438 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_439 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_440 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_441 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_442 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_443 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_444 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_445 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_446 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_447 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_448 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_449 | 3 Phase fault on NIXA 2 69.000 (505501) 69 kV Bus a. Apply fault at the NIXA 2 69.000 (505501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_450 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_451 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_452 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_453 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_454 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_455 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_456 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_457 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_458 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_459 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_460 | 3 Phase fault on HAYS 3 115.00 (530562) 115 kV Bus a. Apply fault at the HAYS 3 115.00 (530562) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYS 3 (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_461 | 3 Phase fault on HAYS 3 115.00 (530562) 115 kV Bus a. Apply fault at the HAYS 3 115.00 (530562) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYS 3 (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_462 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_463 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_464 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_465 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_466 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_467 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_468 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_469 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTONW 3 (530718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_470 | 3 Phase fault on VINETAP3 115.00 (530693) 115 kV Bus a. Apply fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_471 | 3 Phase fault on VINE2 3 115.00 (530694) 115 kV Bus a. Apply fault at the VINE2 3 115.00 (530694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_472 | 3 Phase fault on VINE2 3 115.00 (530694) 115 kV Bus a. Apply fault at the VINE2 3 115.00 (530694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_473 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_474 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_475 | 3 Phase fault on CLARKCOUNTY7 345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G19-030-TAP (763677) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_476 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_477 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_478 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_479 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_480 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_481 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_482 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_483 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_484 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_485 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_486 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_487 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_488 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_489 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_490 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_491 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_492 | 3 Phase fault on BERG 3 115.00 (533367) 115 kV Bus a. Apply fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_493 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_494 | 3 Phase fault on ARKVAL 3 115.00 (533411) 115 kV Bus a. Apply fault at the ARKVAL 3 115.00 (533411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_495 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_496 | 3 Phase fault on CESSNAJ2 69.000 (533503) 69 kV Bus a. Apply fault at the CESSNAJ2 69.000 (533503) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CESSNAJ2 (533503) 69.0 kV to 11HALST2 (533509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_497 | 3 Phase fault on 11HALST2 69.000 (533509) 69 kV Bus a. Apply fault at the 11HALST2 69.000 (533509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 11HALST2 (533509) 69.0 kV to 17HALST2 (533521) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_498 | 3 Phase fault on 14LORAN2 69.000 (533511) 69 kV Bus a. Apply fault at the 14LORAN2 69.000 (533511) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 14LORAN2 (533511) 69.0 kV to 17HUXMN2 (533522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_499 | 3 Phase fault on 17HALST2 69.000 (533521) 69 kV Bus a. Apply fault at the 17HALST2 69.000 (533521) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17HALST2 (533521) 69.0 kV to 17HUXMN2 (533522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_500 | 3 Phase fault on 17HUXMN2 69.000 (533522) 69 kV Bus a. Apply fault at the 17HUXMN2 69.000 (533522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17HUXMN2 (533522) 69.0 kV to 17 PLUM2 (533523) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_501 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_502 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to LOCHS (539944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_503 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_504 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_505 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_506 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_507 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_508 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_509 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_510 | 3 Phase fault on FROSTRD_CAP5161.00 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5161.00 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_511 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_512 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_513 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_514 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_515 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_516 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_517 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_518 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_519 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_520 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_521 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_522 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_523 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_524 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_525 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_526 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_527 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_528 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_529 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_530 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_531 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_532 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_533 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_534 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_535 | 3 Phase fault on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_536 | 3 Phase fault on FROSTRD5 161.00 (541220) 161 kV Bus a. Apply fault at the FROSTRD5 161.00 (541220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_537 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_538 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_539 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_540 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_541 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 5 (541229) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_542 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_543 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_544 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_545 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_546 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_547 | 3 Phase fault on 13&40 2 69.000 (541266) 69 kV Bus a. Apply fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_548 | 3 Phase fault on ODESSA 2 69.000 (541267) 69 kV Bus a. Apply fault at the ODESSA 2 69.000 (541267) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSACTY2 (541526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_549 | 3 Phase fault on WBURGP 2 69.000 (541268) 69 kV Bus a. Apply fault at the WBURGP 2 69.000 (541268) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to WBURGE 2 (541269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_550 | 3 Phase fault on WBURGE 2 69.000 (541269) 69 kV Bus a. Apply fault at the WBURGE 2 69.000 (541269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to MONSERTP (541524) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_551 | 3 Phase fault on KNOSTER2 69.000 (541270) 69 kV Bus a. Apply fault at the KNOSTER2 69.000 (541270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTER2 (541270) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_552 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_553 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_554 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_555 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_556 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_557 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_558 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_559 | 3 Phase fault on COLECMP2 69.000 (541276) 69 kV Bus a. Apply fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_560 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_561 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_562 | 3 Phase fault on NRAYMORE 161.00 (541317) 161 kV Bus a. Apply fault at the NRAYMORE 161.00 (541317) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_563 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_564 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_565 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_566 | 3 Phase fault on MONSERTP 69.000 (541524) 69 kV Bus a. Apply fault at the MONSERTP 69.000 (541524) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONSERTP (541524) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_567 | 3 Phase fault on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_568 | 3 Phase fault on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMONTETP (541535) 69.0 kV to LAMONTE (541536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_569 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_570 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_571 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_572 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_573 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_574 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_575 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_576 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_577 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_578 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_579 | 3 Phase fault on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_580 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_581 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_582 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_583 | 3 Phase fault on MALTABN5 161.00 (543059) 161 kV Bus a. Apply fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_584 | 3 Phase fault on MALTABN5 161.00 (543059) 161 kV Bus a. Apply fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_585 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_586 | 3 Phase fault on S EAST 5 161.00 (543071) 161 kV Bus a. Apply fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_587 | 3 Phase fault on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_588 | 3 Phase fault on DUNCNRD2 69.000 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 69.000 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_589 | 3 Phase fault on SUGRCRK_S2 69.000 (543163) 69 kV Bus a. Apply fault at the SUGRCRK_S2 69.000 (543163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_S2 (543163) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_590 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON416J2 (547402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_591 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_592 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON352 2 (547406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_593 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_594 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_595 | 3 Phase fault on RES364 2 69.000 (547424) 69 kV Bus a. Apply fault at the RES364 2 69.000 (547424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RES364 2 (547424) 69.0 kV to ALB262 2 (547553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_596 | 3 Phase fault on HER209 2 69.000 (547425) 69 kV Bus a. Apply fault at the HER209 2 69.000 (547425) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HER209 2 (547425) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_597 | 3 Phase fault on BUF243J2 69.000 (547432) 69 kV Bus a. Apply fault at the BUF243J2 69.000 (547432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF243J2 (547432) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_598 | 3 Phase fault on BUF409 2 69.000 (547434) 69 kV Bus a. Apply fault at the BUF409 2 69.000 (547434) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF409 2 (547434) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_599 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to CUPSUB 2 (547437) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_600 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_601 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to GRN614 2 (547613) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_602 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to EXP4502 (547441) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_603 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_604 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to BRT323 2 (547567) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_605 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_606 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_607 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_608 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_609 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_610 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_611 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_612 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_613 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_614 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_615 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_616 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_617 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_618 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_619 | 3 Phase fault on RVS438 5 161.00 (547497) 161 kV Bus a. Apply fault at the RVS438 5 161.00 (547497) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVS438 5 (547497) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_620 | 3 Phase fault on BOL 73 2 69.000 (547528) 69 kV Bus a. Apply fault at the BOL 73 2 69.000 (547528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 2 (547528) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_621 | 3 Phase fault on BOL 73 2 69.000 (547528) 69 kV Bus a. Apply fault at the BOL 73 2 69.000 (547528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 2 (547528) 69.0 kV to BOL367 2 (547584) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_622 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_623 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to LAW260 2 (547552) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_624 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_625 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_626 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MON152 2 (547540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_627 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_628 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_629 | 3 Phase fault on MON152 2 69.000 (547540) 69 kV Bus a. Apply fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_630 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_631 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to BOL602 2 (547612) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_632 | 3 Phase fault on BIL221 2 69.000 (547546) 69 kV Bus a. Apply fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIL221 2 (547546) 69.0 kV to REP359 2 (547580) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_633 | 3 Phase fault on BIL221 2 69.000 (547546) 69 kV Bus a. Apply fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIL221 2 (547546) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_634 | 3 Phase fault on ARC250 2 69.000 (547549) 69 kV Bus a. Apply fault at the ARC250 2 69.000 (547549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARC250 2 (547549) 69.0 kV to GRN614 2 (547613) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_635 | 3 Phase fault on LAW260 2 69.000 (547552) 69 kV Bus a. Apply fault at the LAW260 2 69.000 (547552) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAW260 2 (547552) 69.0 kV to HTC338 2 (547573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_636 | 3 Phase fault on ALB262 2 69.000 (547553) 69 kV Bus a. Apply fault at the ALB262 2 69.000 (547553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALB262 2 (547553) 69.0 kV to HTC338 2 (547573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_637 | 3 Phase fault on ALB262 2 69.000 (547553) 69 kV Bus a. Apply fault at the ALB262 2 69.000 (547553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALB262 2 (547553) 69.0 kV to MTV463 2 (547619) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_638 | 3 Phase fault on TIP292 2 69.000 (547559) 69 kV Bus a. Apply fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_639 | 3 Phase fault on OZD312 2 69.000 (547562) 69 kV Bus a. Apply fault at the OZD312 2 69.000 (547562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZD312 2 (547562) 69.0 kV to FOR410 2 (547603) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_640 | 3 Phase fault on MTV351 2 69.000 (547577) 69 kV Bus a. Apply fault at the MTV351 2 69.000 (547577) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTV351 2 (547577) 69.0 kV to MTV420 2 (547606) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_641 | 3 Phase fault on MTV351 2 69.000 (547577) 69 kV Bus a. Apply fault at the MTV351 2 69.000 (547577) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTV351 2 (547577) 69.0 kV to MTV463 2 (547619) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_642 | 3 Phase fault on MTV351 2 69.000 (547577) 69 kV Bus a. Apply fault at the MTV351 2 69.000 (547577) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTV351 2 (547577) 69.0 kV to MTV348 2 (547620) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_643 | 3 Phase fault on AUR355 2 69.000 (547578) 69 kV Bus a. Apply fault at the AUR355 2 69.000 (547578) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR355 2 (547578) 69.0 kV to MTV420 2 (547606) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_644 | 3 Phase fault on BOL367 2 69.000 (547584) 69 kV Bus a. Apply fault at the BOL367 2 69.000 (547584) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL367 2 (547584) 69.0 kV to BOL602 2 (547612) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_645 | 3 Phase fault on RNM393 2 69.000 (547595) 69 kV Bus a. Apply fault at the RNM393 2 69.000 (547595) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 2 (547595) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_646 | 3 Phase fault on LKW400 2 69.000 (547598) 69 kV Bus a. Apply fault at the LKW400 2 69.000 (547598) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKW400 2 (547598) 69.0 kV to GRN614 2 (547613) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_647 | 3 Phase fault on STK418 2 69.000 (547605) 69 kV Bus a. Apply fault at the STK418 2 69.000 (547605) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STK418 2 (547605) 69.0 kV to STK324J2 (547616) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_648 | 3 Phase fault on WIL369 2 69.000 (547691) 69 kV Bus a. Apply fault at the WIL369 2 69.000 (547691) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIL369 2 (547691) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_649 | 3 Phase fault on WIL482 69.000 (547726) 69 kV Bus a. Apply fault at the WIL482 69.000 (547726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIL482 (547726) 69.0 kV to WIL479 (547727) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_650 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_651 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_652 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_653 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_654 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_655 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_656 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_657 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_658 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_659 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_660 | 3 Phase fault on MENTOR 5161.00 (549963) 161 kV Bus a. Apply fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_661 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_662 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_663 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_664 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5FRANKS (300078) 161.0 kV to 7FRANKS (300041) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_665 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5FRANKS (300078) 161.0 kV to 7FRANKS (300041) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_666 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_667 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_668 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_669 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_670 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_671 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_672 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_673 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_674 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_675 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_676 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_677 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_678 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_679 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_680 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_681 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_682 | 3 Phase fault on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDSP (300725) 69.0 kV to 5REEDSP (301521) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_683 | 3 Phase fault on 5RENOHLW 161.00 (301129) 161 kV Bus a. Apply fault at the 5RENOHLW 161.00 (301129) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RENOHLW (300738) 69.0 kV to 5RENOHLW (301129) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_684 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_685 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_686 | 3 Phase fault on 5HYDERHL 161.00 (300793) 161 kV Bus a. Apply fault at the 5HYDERHL 161.00 (300793) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HYDERHL (300798) 69.0 kV to 5HYDERHL (300793) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_687 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_688 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_689 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_690 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_691 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_692 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_693 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_694 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_695 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_696 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_697 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_698 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_699 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_700 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_701 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_702 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_703 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_704 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_705 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_706 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_707 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_708 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_709 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_710 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_711 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_712 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_713 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_714 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_715 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_716 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_717 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_718 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_719 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_720 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_721 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_722 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_723 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_724 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_725 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_726 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_727 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_728 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_729 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_730 | 3 Phase fault on HEC 3 115.00 (533419) 115 kV Bus a. Apply fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_731 | 3 Phase fault on 3 VANBU3 115.00 (533435) 115 kV Bus a. Apply fault at the 3 VANBU3 115.00 (533435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3 VANBU3 (533435) 115.0 kV to 3 VANBU2 (533527) 69.0 kV to 3VANBUR1 (533446) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_732 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_733 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_734 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_735 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_736 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_737 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to None Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_738 | 3 Phase fault on NEVADA 5 161.00 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 161.00 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVADA 5 (541208) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_739 | 3 Phase fault on NEVADA 5 161.00 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 161.00 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVADA 5 (541208) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_740 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_741 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_742 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_743 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_744 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSA 5 (541229) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_745 | 3 Phase fault on LEX161 5 161.00 (541232) 161 kV Bus a. Apply fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEX161 5 (541232) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_746 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_747 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_748 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_749 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_750 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_751 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_752 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_753 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_754 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH 12 (400) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_755 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to None Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_756 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_757 | 3 Phase fault on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_758 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_759 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_760 | 3 Phase fault on MON383 5 161.00 (547480) 161 kV Bus a. Apply fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_761 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_762 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_763 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_764 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STK418 2 (547605) 69.0 kV to 5STKAEC (300118) 161.0 kV to STK418 1 (547719) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_765 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_766 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_767 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_768 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_769 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_770 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_771 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_772 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_773 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_774 | 3 Phase fault on 2BEARCK 69.000 (300713) 69 kV Bus a. Apply fault at the 2BEARCK 69.000 (300713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEARCK (300713) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_775 | 3 Phase fault on 2REEDSP 69.000 (300725) 69 kV Bus a. Apply fault at the 2REEDSP 69.000 (300725) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDSP (300725) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_776 | 3 Phase fault on 7FRANKSRCT 345.00 (301554) 345 kV Bus a. Apply fault at the 7FRANKSRCT 345.00 (301554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKSRCT (301554) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_777 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL3 (539701) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_778 | 3 Phase fault on MON383 2 69.000 (547591) 69 kV Bus a. Apply fault at the MON383 2 69.000 (547591) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 2 (547591) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_779 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_780 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_781 | 3 Phase fault on SUB M 69.000 (548815) 69 kV Bus a. Apply fault at the SUB M 69.000 (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_782 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_783 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_784 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_785 | 3 Phase fault on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_786 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_787 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. NICHOL XF1 1 (549940) 13.2 kV to NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_788 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.3. MILL XF1 1 (549946) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_789 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 b.3. MILL XF2 1 (549948) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_790 | 3 Phase fault on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BILLNG (300658) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_791 | 3 Phase fault on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BILLNG (300658) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_792 | 3 Phase fault on 2BRNSPG 69.000 (300660) 69 kV Bus a. Apply fault at the 2BRNSPG 69.000 (300660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRNSPG (300660) 69.0 kV to 2CLEVER (300665) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_793 | 3 Phase fault on 2CASSIDY 69.000 (300663) 69 kV Bus a. Apply fault at the 2CASSIDY 69.000 (300663) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CASSIDY (300663) 69.0 kV to 2JAMESV (300673) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_794 | 3 Phase fault on 2CLEVER 69.000 (300665) 69 kV Bus a. Apply fault at the 2CLEVER 69.000 (300665) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVER (300665) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_795 | 3 Phase fault on 2JAMESV 69.000 (300673) 69 kV Bus a. Apply fault at the 2JAMESV 69.000 (300673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_796 | 3 Phase fault on 2MTVRN 69.000 (300677) 69 kV Bus a. Apply fault at the 2MTVRN 69.000 (300677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MTVRN (300677) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_797 | 3 Phase fault on 5STRAFFORD 161.00 (301368) 161 kV Bus a. Apply fault at the 5STRAFFORD 161.00 (301368) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STRAFFORD (301368) 161.0 kV to 5MCCARTNEY (301568) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_798 | 3 Phase fault on 5MCCARTNEY 161.00 (301568) 161 kV Bus a. Apply fault at the 5MCCARTNEY 161.00 (301568) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCCARTNEY (301568) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_799 | 3 Phase fault on HER209 2 69.000 (547425) 69 kV Bus a. Apply fault at the HER209 2 69.000 (547425) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HER209 2 (547425) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_800 | 3 Phase fault on BUF243J2 69.000 (547432) 69 kV Bus a. Apply fault at the BUF243J2 69.000 (547432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF243J2 (547432) 69.0 kV to BUF243 2 (547547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_801 | 3 Phase fault on BUF243J2 69.000 (547432) 69 kV Bus a. Apply fault at the BUF243J2 69.000 (547432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF243J2 (547432) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_802 | 3 Phase fault on BUF243J2 69.000 (547432) 69 kV Bus a. Apply fault at the BUF243J2 69.000 (547432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF243J2 (547432) 69.0 kV to FRG397 2 (547596) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_803 | 3 Phase fault on STRKAMO2 69.000 (547433) 69 kV Bus a. Apply fault at the STRKAMO2 69.000 (547433) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRKAMO2 (547433) 69.0 kV to STR370 2 (547587) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_804 | 3 Phase fault on STRKAMO2 69.000 (547433) 69 kV Bus a. Apply fault at the STRKAMO2 69.000 (547433) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRKAMO2 (547433) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_805 | 3 Phase fault on BUF409 2 69.000 (547434) 69 kV Bus a. Apply fault at the BUF409 2 69.000 (547434) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF409 2 (547434) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_806 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_807 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to EXP4502 (547441) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_808 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_809 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to BRT323 2 (547567) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_810 | 3 Phase fault on OZK457 2 69.000 (547442) 69 kV Bus a. Apply fault at the OZK457 2 69.000 (547442) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZK457 2 (547442) 69.0 kV to OZK434 2 (547609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_811 | 3 Phase fault on REP451 2 69.000 (547443) 69 kV Bus a. Apply fault at the REP451 2 69.000 (547443) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REP451 2 (547443) 69.0 kV to REP345 2 (547576) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_812 | 3 Phase fault on REP451 2 69.000 (547443) 69 kV Bus a. Apply fault at the REP451 2 69.000 (547443) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REP451 2 (547443) 69.0 kV to REP359 2 (547580) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_813 | 3 Phase fault on BOL 73 2 69.000 (547528) 69 kV Bus a. Apply fault at the BOL 73 2 69.000 (547528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 2 (547528) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_814 | 3 Phase fault on BOL 73 2 69.000 (547528) 69 kV Bus a. Apply fault at the BOL 73 2 69.000 (547528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 2 (547528) 69.0 kV to BOL367 2 (547584) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_815 | 3 Phase fault on SED 80 2 69.000 (547529) 69 kV Bus a. Apply fault at the SED 80 2 69.000 (547529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SED 80 2 (547529) 69.0 kV to BRT323 2 (547567) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_816 | 3 Phase fault on SED 80 2 69.000 (547529) 69 kV Bus a. Apply fault at the SED 80 2 69.000 (547529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SED 80 2 (547529) 69.0 kV to FRG397 2 (547596) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_817 | 3 Phase fault on SED 80 2 69.000 (547529) 69 kV Bus a. Apply fault at the SED 80 2 69.000 (547529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SED 80 2 (547529) 69.0 kV to WIL479 (547727) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_818 | 3 Phase fault on SED 80 2 69.000 (547529) 69 kV Bus a. Apply fault at the SED 80 2 69.000 (547529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SED 80 2 (547529) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_819 | 3 Phase fault on NIX114 2 69.000 (547535) 69 kV Bus a. Apply fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_820 | 3 Phase fault on NIX114 2 69.000 (547535) 69 kV Bus a. Apply fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIX114 2 (547535) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_821 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to LAW260 2 (547552) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_822 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_823 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_824 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_825 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to REP345 2 (547576) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_826 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_827 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_828 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_829 | 3 Phase fault on BIL221 2 69.000 (547546) 69 kV Bus a. Apply fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIL221 2 (547546) 69.0 kV to REP359 2 (547580) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_830 | 3 Phase fault on BIL221 2 69.000 (547546) 69 kV Bus a. Apply fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIL221 2 (547546) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_831 | 3 Phase fault on LAW260 2 69.000 (547552) 69 kV Bus a. Apply fault at the LAW260 2 69.000 (547552) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAW260 2 (547552) 69.0 kV to HTC338 2 (547573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_832 | 3 Phase fault on OZK330 2 69.000 (547570) 69 kV Bus a. Apply fault at the OZK330 2 69.000 (547570) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZK330 2 (547570) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_833 | 3 Phase fault on OZK330 2 69.000 (547570) 69 kV Bus a. Apply fault at the OZK330 2 69.000 (547570) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZK330 2 (547570) 69.0 kV to OZK434 2 (547609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_834 | 3 Phase fault on BOL367 2 69.000 (547584) 69 kV Bus a. Apply fault at the BOL367 2 69.000 (547584) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL367 2 (547584) 69.0 kV to BOL602 2 (547612) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_835 | 3 Phase fault on STR370 2 69.000 (547587) 69 kV Bus a. Apply fault at the STR370 2 69.000 (547587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STR370 2 (547587) 69.0 kV to FRG397 2 (547596) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_836 | 3 Phase fault on WIL369 2 69.000 (547691) 69 kV Bus a. Apply fault at the WIL369 2 69.000 (547691) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIL369 2 (547691) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_837 | 3 Phase fault on WIL482 69.000 (547726) 69 kV Bus a. Apply fault at the WIL482 69.000 (547726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIL482 (547726) 69.0 kV to WIL479 (547727) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_838 | 3 Phase fault on HIGHWAY M 269.000 (549909) 69 kV Bus a. Apply fault at the HIGHWAY M 269.000 (549909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHWAY M 2 (549909) 69.0 kV to BLACKMAN 2 (549916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_839 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_840 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_841 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_842 | 3 Phase fault on GALLOWAY 269.000 (549915) 69 kV Bus a. Apply fault at the GALLOWAY 269.000 (549915) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALLOWAY 2 (549915) 69.0 kV to BLACKMAN 2 (549916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_843 | 3 Phase fault on BLACKMAN 269.000 (549916) 69 kV Bus a. Apply fault at the BLACKMAN 269.000 (549916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKMAN 2 (549916) 69.0 kV to INGRAM 2 (549917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_844 | 3 Phase fault on BLACKMAN 269.000 (549916) 69 kV Bus a. Apply fault at the BLACKMAN 269.000 (549916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKMAN 2 (549916) 69.0 kV to MILL 2 (549918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_845 | 3 Phase fault on INGRAM 269.000 (549917) 69 kV Bus a. Apply fault at the INGRAM 269.000 (549917) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INGRAM 2 (549917) 69.0 kV to MILL 2 (549918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_846 | 3 Phase fault on MILL 269.000 (549918) 69 kV Bus a. Apply fault at the MILL 269.000 (549918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 2 (549918) 69.0 kV to CHAD 2 (549919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_847 | 3 Phase fault on MILL 269.000 (549918) 69 kV Bus a. Apply fault at the MILL 269.000 (549918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 2 (549918) 69.0 kV to PACKER 2 (549932) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_848 | 3 Phase fault on CHAD 269.000 (549919) 69 kV Bus a. Apply fault at the CHAD 269.000 (549919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAD 2 (549919) 69.0 kV to HARGISS 2 (549920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_849 | 3 Phase fault on HARGISS 269.000 (549920) 69 kV Bus a. Apply fault at the HARGISS 269.000 (549920) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARGISS 2 (549920) 69.0 kV to MAIN STREET2 (549921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_850 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to GRAND 2 (549922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_851 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_852 | 3 Phase fault on GRAND 269.000 (549922) 69 kV Bus a. Apply fault at the GRAND 269.000 (549922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 2 (549922) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_853 | 3 Phase fault on LAUREL 269.000 (549924) 69 kV Bus a. Apply fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_854 | 3 Phase fault on NICHOLS 269.000 (549925) 69 kV Bus a. Apply fault at the NICHOLS 269.000 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 2 (549925) 69.0 kV to FRISCO 2 (549926) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_855 | 3 Phase fault on FRISCO 269.000 (549926) 69 kV Bus a. Apply fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_856 | 3 Phase fault on N HWY13 269.000 (549927) 69 kV Bus a. Apply fault at the N HWY13 269.000 (549927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HWY13 2 (549927) 69.0 kV to NORTON 2 (549928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_857 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_858 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to NEERGARD 2 (549930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_859 | 3 Phase fault on NEERGARD 269.000 (549930) 69 kV Bus a. Apply fault at the NEERGARD 269.000 (549930) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEERGARD 2 (549930) 69.0 kV to LECOMPTE 2 (549931) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_860 | 3 Phase fault on LECOMPTE 269.000 (549931) 69 kV Bus a. Apply fault at the LECOMPTE 269.000 (549931) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LECOMPTE 2 (549931) 69.0 kV to PACKER 2 (549932) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_861 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_862 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_863 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_864 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_865 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_866 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_867 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_868 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_869 | 3 Phase fault on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_870 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_871 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_872 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_873 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_874 | 3 Phase fault on NORTON 5161.00 (549967) 161 kV Bus a. Apply fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_875 | 3 Phase fault on OZK434 2 69.000 (547609) 69 kV Bus a. Apply fault at the OZK434 2 69.000 (547609) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZK434 2 (547609) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_876 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_001 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_002 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_004 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_005 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_006 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_007 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_010 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_015 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_016 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_017 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_018 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_022 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_024 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_025 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_026 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_029 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_032 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_033 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_036 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_037 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_038 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_039 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_040 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_041 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_043 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_048 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_049 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.5. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.6. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.7. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.8. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.9. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.10. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.11. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.12. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding #1 b.13. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.14. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.15. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.16. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.17. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.3. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on SLATECRK4 138.00 (533070) 138 kV Bus a. Apply Fault at the SLATECRK4 138.00 (533070) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to SLATECRK4 (533070) 138.0 kV Transmission Circuit #1 b.3. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.4. SLATEXFMR1 (533139) 34.5 kV to SLATEGSU1 (533140) 34.5 kV Transmission Circuit #1 b.5. SLATEGEN1 (533141) 0.7 kV to SLATEGSU1 (533140) 34.5 kV Two Winding #1 b.6. SLATECRK4 (533070) 138.0 kV to SLATEXFMR1 (533139) 34.5 kV to SLATETV1 (533142) 13.2 kV Three Winding #1 b.7. CRESW1 1 (533080) 13.2 kV to CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.4. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.7. MIDLTNT4 (514804) 138.0 kV to GEN-2016-071 (587480) 138.0 kV Transmission Circuit #1 b.8. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.9. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.6. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.5. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 b.6. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.6. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.4. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.5. SUMNER 4 (532984) 138.0 kV to GEN-2017-121 (761838) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 3 VANBU3 115.00 (533435) 115 kV Bus a. Apply Fault at the 3 VANBU3 115.00 (533435) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. 3 VANBU3 (533435) 115.0 kV to 3 VANBU2 (533527) 69.0 kV to 3VANBUR1 (533446) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.4. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.5. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.6. CIRCLE 3 (533413) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.2. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.5. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on HEC GT 3 115.00 (533421) 115 kV Bus a. Apply Fault at the HEC GT 3 115.00 (533421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.5. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on MANVILE3 115.00 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to MCPHGT4 (532705) 13.8 kV Two Winding #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to MCPHGT3 (532704) 13.8 kV Two Winding #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.4. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.3. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.4. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.5. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. RENO 1X1 (532807) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. RENO 2X1 (532810) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on RENO 3 115.00 (533416) 115 kV Bus a. Apply Fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.7. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.8. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.2. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.5. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on 7CALAWY 1 345.00 (344224) 345 kV Bus a. Apply Fault at the 7CALAWY 1 345.00 (344224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7CALAWY 1 (344224) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on 5HARRISON.E!161.00 (338104) 161 kV Bus a. Apply Fault at the 5HARRISON.E!161.00 (338104) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HARRISON.E! (338104) 161.0 kV to 5OMAHA+ (338105) 161.0 kV Transmission Circuit #1 b.2. 5HARRISON.E! (338104) 161.0 kV to 5EVERTON RD (338107) 161.0 kV Transmission Circuit #1 b.3. 5HARRISON.E! (338104) 161.0 kV to 5SUMMIT (338121) 161.0 kV Transmission Circuit #1 b.4. 5HARRISON.E! (338104) 161.0 kV to 5HARRISON.S# (338681) 161.0 kV Transmission Circuit #1 b.5. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply Fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 b.2. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 b.3. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on OZD312 5 161.00 (547474) 161 kV Bus a. Apply Fault at the OZD312 5 161.00 (547474) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.3. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.4. OZD312 5 (547474) 161.0 kV to OZD312 1 (547648) 4.6 kV Two Winding #1 b.5. OZD312 5 (547474) 161.0 kV to OZD312 2 (547562) 69.0 kV to OZD312T1 (547710) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on CPK446 5 161.00 (547499) 161 kV Bus a. Apply Fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.5. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.6. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on OZD312 5 161.00 (547474) 161 kV Bus a. Apply Fault at the OZD312 5 161.00 (547474) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.3. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.4. OZD312 5 (547474) 161.0 kV to OZD312 1 (547648) 4.6 kV Two Winding #1 b.5. BRN331 5 (547475) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.6. OZD312 5 (547474) 161.0 kV to OZD312 2 (547562) 69.0 kV to OZD312T1 (547710) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.6. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on BRN412 5 161.00 (547488) 161 kV Bus a. Apply Fault at the BRN412 5 161.00 (547488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.3. BRN331 5 (547475) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.4. BRN412 5 (547488) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BRN412 5 161.00 (547488) 161 kV Bus a. Apply Fault at the BRN412 5 161.00 (547488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.2. BRN331 5 (547475) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.3. BRN412 5 (547488) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 b.4. BRN413 5 (547489) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on GRT433 5 161.00 (547495) 161 kV Bus a. Apply Fault at the GRT433 5 161.00 (547495) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRN412 5 (547488) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 b.2. BRN413 5 (547489) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 b.3. BRN413 5 (547489) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on RDS295 5 161.00 (547473) 161 kV Bus a. Apply Fault at the RDS295 5 161.00 (547473) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on RVS438 5 161.00 (547497) 161 kV Bus a. Apply Fault at the RVS438 5 161.00 (547497) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.3. HOL387 5 (547482) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 b.4. BRN413 5 (547489) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.5. RVS438 5 (547497) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on OZD312 5 161.00 (547474) 161 kV Bus a. Apply Fault at the OZD312 5 161.00 (547474) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.3. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.4. OZD312 5 (547474) 161.0 kV to OZD312 1 (547648) 4.6 kV Two Winding #1 b.5. HOL387 5 (547482) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 b.6. OZD312 5 (547474) 161.0 kV to OZD312 2 (547562) 69.0 kV to OZD312T1 (547710) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply Fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.3. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.4. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.3. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 b.4. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.5. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CORONAD3 115.00 (533394) 115 kV Bus a. Apply Fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEC 2 (533513) 69.0 kV to HEC GT 2 (533514) 69.0 kV Transmission Circuit #1 b.2. HEC 2 (533513) 69.0 kV to 17HALST2 (533521) 69.0 kV Transmission Circuit #1 b.3. HEC 2 (533513) 69.0 kV to HEC 3 (533419) 115.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 b.4. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply Fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.2. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.4. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BLUVLY 161.00 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 161.00 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.3. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.4. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.5. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 b.6. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.7. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 b.8. BLU VAL 1 (548833) 14.4 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.9. BLU VAL 2 (548834) 14.4 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.10. BLU VAL 3 (548835) 13.8 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.11. BLUVLY (548806) 69.0 kV to Load #T1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on JTEC 5161.00 (549954) 161 kV Bus a. Apply Fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. JTEC GEN#1 1 (549890) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.3. JTEC CTS 1 (549891) 12.5 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.4. JTEC GEN#2 1 (549893) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.5. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.6. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.7. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.4. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.4. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply Fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JRPS GT1 1 (549900) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.2. JRPS GT2 1 (549901) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.3. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.4. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.5. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 b.6. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on MILL 5161.00 (549962) 161 kV Bus a. Apply Fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.4. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on MENTOR 5161.00 (549963) 161 kV Bus a. Apply Fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.2. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.5. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.6. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on CLAY 5161.00 (549970) 161 kV Bus a. Apply Fault at the CLAY 5161.00 (549970) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.4. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on PIC WEST 5161.00 (549971) 161 kV Bus a. Apply Fault at the PIC WEST 5161.00 (549971) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on BLUVLY 69.00 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 69.00 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY (548806) 69.0 kV to Load #T2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TWR 33 3 115.00 (533455) 115 kV Bus a. Apply Fault at the TWR 33 3 115.00 (533455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.2. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.4. SPF X3 1 (505495) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 b.4. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RENOHLWTP (300130) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.2. 5RENOHLWTP (300130) 161.0 kV to 5RIVERSIDE (300805) 161.0 kV Transmission Circuit #1 b.3. 5RENOHLWTP (300130) 161.0 kV to 5RENOHLW (301129) 161.0 kV Transmission Circuit #1 b.4. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5COMPTN (300719) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.6. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.7. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.8. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.9. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.10. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.11. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.12. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.13. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.4. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.6. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.7. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.8. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.9. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.10. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.11. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 b.2. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.5. SPF X1 1 (505491) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 b.2. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 b.3. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 b.4. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 b.5. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.6. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #2 b.7. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.5. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.6. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.7. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply Fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.4. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply Fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.3. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply Fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 b.3. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply Fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 b.3. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on DRIFTWD4 138.00 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 138.00 (521200) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.2. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.3. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on DRIFTWD4 138.00 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 138.00 (521200) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.3. DRFTWDTERT (521185) 13.8 kV to DRIFTWD4 (521200) 138.0 kV to DRIFTWD2 (521201) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.3. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.8. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.2. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.9. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to Load #S1 b.6. HOLCOMB3 (531448) 115.0 kV to Load #S2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply Fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. FTDODGP1 (539670) 15.0 kV to FTDODGE3 (539671) 115.0 kV Two Winding #1 b.4. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.5. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 b.6. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. FTDODGE3 (539671) 115.0 kV to FTDDGDV1 (539715) 34.5 kV to FTDODG-T (539915) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.3. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to CIM-PLT (539780) 13.8 kV Two Winding #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply Fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.6. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.5. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on BUSHTON3 115.00 (530681) 115 kV Bus a. Apply Fault at the BUSHTON3 115.00 (530681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 b.2. BUSHTON3 (530681) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on RICE 6 230.00 (530686) 230 kV Bus a. Apply Fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to Load #1 b.3. RICE 3 (530623) 115.0 kV to Load #K1 b.4. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to Load #1 b.3. RICE 3 (530623) 115.0 kV to Load #K1 b.4. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on PAWN-ED3 115.00 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 115.00 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.4. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.6. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.7. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.8. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.9. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.10. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on BUFLOCRK6 230.00 (530688) 230 kV Bus a. Apply Fault at the BUFLOCRK6 230.00 (530688) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.3. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.4. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 b.5. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.8. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.4. RICE 3 (530623) 115.0 kV to Load #1 b.5. RICE 3 (530623) 115.0 kV to Load #K1 b.6. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to Load #1 b.2. LYONS 3 (530620) 115.0 kV to Load #E1 b.3. LYONS 3 (530620) 115.0 kV to Load #K1 b.4. LYONS 3 (530620) 115.0 kV to Load #K2 b.5. LYONS 3 (530620) 115.0 kV to Load #K3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.4. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to RCKFALL4 (515427) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to RCKFALL4 (515427) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on 5CLARK 161.00 (300070) 161 kV Bus a. Apply Fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 b.2. 5CLARK (300070) 161.0 kV to 2CLARK (300802) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply Fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 b.2. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 5MPLTAP (300036) 161.0 kV Transmission Circuit #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply Fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 b.2. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply Fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 b.2. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on 5NORTON 161.00 (300105) 161 kV Bus a. Apply Fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply Fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to 2SEDALI (300541) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply Fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. 5STKAEC (300118) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply Fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply Fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 b.2. 2SMTHTN (300542) 69.0 kV to 2FLORNC (300553) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply Fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BILLNG (300658) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 b.2. 2BILLNG (300658) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on 2CAPEFR 69.000 (300662) 69 kV Bus a. Apply Fault at the 2CAPEFR 69.000 (300662) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CAPEFR (300662) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 b.2. 2CAPEFR (300662) 69.0 kV to 2FLTCRK (300671) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply Fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 b.2. 2DADEVL (300668) 69.0 kV to 2GRNFLD (300672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on 2MTVRN 69.000 (300677) 69 kV Bus a. Apply Fault at the 2MTVRN 69.000 (300677) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTVRN (300677) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 b.2. 2MTVRN (300677) 69.0 kV to 2MIDWYTP (300684) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on 2VERONA 69.000 (300680) 69 kV Bus a. Apply Fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 b.2. 2VERONA (300680) 69.0 kV to 2PRDYTP (300679) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on 2BEARCK 69.000 (300713) 69 kV Bus a. Apply Fault at the 2BEARCK 69.000 (300713) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BEARCK (300713) 69.0 kV to 2GRTNA (300720) 69.0 kV Transmission Circuit #1 b.2. 2BEARCK (300713) 69.0 kV to 2ROCKWY (300728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on 2BLUWTP 69.000 (300714) 69 kV Bus a. Apply Fault at the 2BLUWTP 69.000 (300714) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BLUWTP (300714) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 b.2. 2BLUWTP (300714) 69.0 kV to 2KMBRLNTP (300721) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on 2GRTNA 69.000 (300720) 69 kV Bus a. Apply Fault at the 2GRTNA 69.000 (300720) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GRTNA (300720) 69.0 kV to 2REEDSP (300725) 69.0 kV Transmission Circuit #1 b.2. 2GRTNA (300720) 69.0 kV to 2BEARCK (300713) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on 2KMBRLNTP 69.000 (300721) 69 kV Bus a. Apply Fault at the 2KMBRLNTP 69.000 (300721) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KMBRLNTP (300721) 69.0 kV to 2BLUWTP (300714) 69.0 kV Transmission Circuit #1 b.2. 2KMBRLNTP (300721) 69.0 kV to 2STONBR (300733) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply Fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LAKE-K (300722) 69.0 kV to 2REEDSP (300725) 69.0 kV Transmission Circuit #1 b.2. 2LAKE-K (300722) 69.0 kV to 2SILDOL (300730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on 2SILDOL 69.000 (300730) 69 kV Bus a. Apply Fault at the 2SILDOL 69.000 (300730) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SILDOL (300730) 69.0 kV to 2T.ROCKSW (301360) 69.0 kV Transmission Circuit #1 b.2. 2SILDOL (300730) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on 2STULTS 69.000 (300734) 69 kV Bus a. Apply Fault at the 2STULTS 69.000 (300734) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STULTS (300734) 69.0 kV to 2RENOHLW (300738) 69.0 kV Transmission Circuit #1 b.2. 2STULTS (300734) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply Fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 b.2. 2EUDORA (300774) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply Fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5COLLINS (300816) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 b.2. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on 5MCBAINB2 161.00 (301489) 161 kV Bus a. Apply Fault at the 5MCBAINB2 161.00 (301489) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5MCBAINB2 (301489) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on 5LOYMART 2 161.00 (344041) 161 kV Bus a. Apply Fault at the 5LOYMART 2 161.00 (344041) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOYMART 2 (344041) 161.0 kV to 5LOYMART 1 (344040) 161.0 kV Transmission Circuit #z b.2. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply Fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply Fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MDFRDTP4 (515569) 138.0 kV to RENFROW4 (515544) 138.0 kV Transmission Circuit #1 b.2. MDFRDTP4 (515569) 138.0 kV to RDRUNNR4 (515426) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to KNOBHIL4 (514795) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on RICE 6 230.00 (530686) 230 kV Bus a. Apply Fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 3 (530623) 115.0 kV to LYONS 3 (530620) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER3 (533417) 115.0 kV to EMCPHER6 (532872) 230.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 b.2. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on REFINRY3 115.00 (533427) 115 kV Bus a. Apply Fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REFINRY3 (533427) 115.0 kV to EMCPHER3 (533417) 115.0 kV Transmission Circuit #1 b.2. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply Fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GRNBURG3 115.00 (539664) 115 kV Bus a. Apply Fault at the GRNBURG3 115.00 (539664) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.2. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on FORD 3 115.00 (539758) 115 kV Bus a. Apply Fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #2 b.2. NFTDODG3 (539771) 115.0 kV to SPRVL 3 (539759) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on CRKCK 3 115.00 (539783) 115 kV Bus a. Apply Fault at the CRKCK 3 115.00 (539783) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRKCK 3 (539783) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CRKCK 3 (539783) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on GEN-2011-008345.00 (539840) 345 kV Bus a. Apply Fault at the GEN-2011-008345.00 (539840) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-008 (539840) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. GEN-2011-008 (539840) 345.0 kV to G-2011-008-3 (539857) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply Fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on PRALEE 5 161.00 (541206) 161 kV Bus a. Apply Fault at the PRALEE 5 161.00 (541206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply Fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply Fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to WSTELEC_CAP5 (541149) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on GRAINVL5 161.00 (541226) 161 kV Bus a. Apply Fault at the GRAINVL5 161.00 (541226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAINVL5 (541226) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply Fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKGRV 5 (541227) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply Fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WBURGE_CAP5 (541148) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply Fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ODESSA 5 (541229) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #1 b.2. ODESSA 5 (541229) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on RICHMND5 161.00 (541236) 161 kV Bus a. Apply Fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on BLSPW 5 161.00 (541237) 161 kV Bus a. Apply Fault at the BLSPW 5 161.00 (541237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPW 5 (541237) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDEAST5 (541241) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. SEDEAST5 (541241) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply Fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 b.2. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 b.2. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.2. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply Fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELHYS 2 (541273) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 b.2. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply Fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDS 2 (541272) 69.0 kV Transmission Circuit #1 b.2. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on COLECMP2 69.000 (541276) 69 kV Bus a. Apply Fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLECMP2 (541276) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 b.2. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply Fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 b.2. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply Fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WAFBW_SW5 (541335) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAFBE_SW5 (541337) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. WAFBE_SW5 (541337) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_411 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_412 | Single Phase Fault with Stuck Breaker on MONSERTP 69.000 (541524) 69 kV Bus a. Apply Fault at the MONSERTP 69.000 (541524) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONSERTP (541524) 69.0 kV to WBURGE 2 (541269) 69.0 kV Transmission Circuit #1 b.2. MONSERTP (541524) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_413 | Single Phase Fault with Stuck Breaker on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply Fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 b.2. KNOSTERTP (541534) 69.0 kV to MONSERTP (541524) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_414 | Single Phase Fault with Stuck Breaker on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply Fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMONTETP (541535) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. LAMONTETP (541535) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_415 | Single Phase Fault with Stuck Breaker on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply Fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_416 | Single Phase Fault with Stuck Breaker on BLUSPRG2 69.000 (543088) 69 kV Bus a. Apply Fault at the BLUSPRG2 69.000 (543088) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_417 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_418 | Single Phase Fault with Stuck Breaker on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply Fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 b.2. CUPTAP 2 (547436) 69.0 kV to GRN614 2 (547613) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_419 | Single Phase Fault with Stuck Breaker on PRC460 2 69.000 (547449) 69 kV Bus a. Apply Fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 b.2. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_420 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_421 | Single Phase Fault with Stuck Breaker on ASH121 2 69.000 (547536) 69 kV Bus a. Apply Fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 b.2. ASH121 2 (547536) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_422 | Single Phase Fault with Stuck Breaker on AUR124 2 69.000 (547537) 69 kV Bus a. Apply Fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 b.2. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_423 | Single Phase Fault with Stuck Breaker on MON152 2 69.000 (547540) 69 kV Bus a. Apply Fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON152 2 (547540) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_424 | Single Phase Fault with Stuck Breaker on FRP217 2 69.000 (547545) 69 kV Bus a. Apply Fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 b.2. FRP217 2 (547545) 69.0 kV to BOL602 2 (547612) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_425 | Single Phase Fault with Stuck Breaker on BIL221 2 69.000 (547546) 69 kV Bus a. Apply Fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIL221 2 (547546) 69.0 kV to 2BILLNG (300658) 69.0 kV Transmission Circuit #1 b.2. BIL221 2 (547546) 69.0 kV to 2CLEVER (300665) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_426 | Single Phase Fault with Stuck Breaker on MTV351 2 69.000 (547577) 69 kV Bus a. Apply Fault at the MTV351 2 69.000 (547577) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MTV351 2 (547577) 69.0 kV to MTV420 2 (547606) 69.0 kV Transmission Circuit #1 b.2. MTV351 2 (547577) 69.0 kV to MTV463 2 (547619) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_427 | Single Phase Fault with Stuck Breaker on AUR355 2 69.000 (547578) 69 kV Bus a. Apply Fault at the AUR355 2 69.000 (547578) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR355 2 (547578) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. AUR355 2 (547578) 69.0 kV to MTV420 2 (547606) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_428 | Single Phase Fault with Stuck Breaker on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply Fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STK418 2 (547605) 69.0 kV to 5STKAEC (300118) 161.0 kV to STK418 1 (547719) 12.5 kV Three Winding #1 b.2. STK418 2 (547605) 69.0 kV to STK324J2 (547616) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_429 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_430 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_431 | Single Phase Fault with Stuck Breaker on G14-001-TAP 345.00 (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP 345.00 (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. G14-001-TAP (562476) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_432 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR1 (588361) 34.5 kV Two Winding #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_433 | Single Phase Fault with Stuck Breaker on G16-153-TAP 345.00 (588364) 345 kV Bus a. Apply Fault at the G16-153-TAP 345.00 (588364) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-153-TAP (588364) 345.0 kV to GEN-2017-086 (589240) 345.0 kV Transmission Circuit #1 b.2. G16-153-TAP (588364) 345.0 kV to GEN-2016-153 (588360) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_434 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_435 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 b.2. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_436 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 b.2. 2GEORGE (300531) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_437 | Single Phase Fault with Stuck Breaker on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply Fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 b.2. 2MORGAN (300782) 69.0 kV to 2EUDORA (300774) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_438 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 b.2. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_439 | Single Phase Fault with Stuck Breaker on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply Fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2REEDSP (300725) 69.0 kV to 5REEDSP (301521) 161.0 kV Two Winding #1 b.2. 2REEDSP (300725) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_440 | Single Phase Fault with Stuck Breaker on 5HYDERHL 161.00 (300793) 161 kV Bus a. Apply Fault at the 5HYDERHL 161.00 (300793) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HYDERHL (300798) 69.0 kV to 5HYDERHL (300793) 161.0 kV Two Winding #1 b.2. 2HYDERHL (300798) 69.0 kV to 2ARNICA (300799) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_441 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 b.2. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_442 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV to SAWYER 3 (539649) 115.0 kV Transmission Circuit #1 b.2. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_443 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_444 | Single Phase Fault with Stuck Breaker on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply Fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 b.2. WBURGE 2 (541269) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_445 | Single Phase Fault with Stuck Breaker on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply Fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSA 5 (541229) 161.0 kV Two Winding #1 b.2. ODESSA 2 (541267) 69.0 kV to 13&40 2 (541266) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_446 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_447 | Single Phase Fault with Stuck Breaker on GEN-2016-046345.00 (587310) 345 kV Bus a. Apply Fault at the GEN-2016-046345.00 (587310) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-046 (587310) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-046 (587310) 345.0 kV to G16-046XFMR1 (587311) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_448 | Single Phase Fault with Stuck Breaker on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply Fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKTASW4 (520434) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_449 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_450 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_451 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_452 | Single Phase Fault with Stuck Breaker on RVS438 5 161.00 (547497) 161 kV Bus a. Apply Fault at the RVS438 5 161.00 (547497) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RVS438 5 (547497) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. RVS438 5 (547497) 161.0 kV to BRN413 5 (547489) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_453 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 2 (547591) 69.0 kV to MON383 5 (547480) 161.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 b.2. MON383 2 (547591) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_454 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_455 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_456 | Single Phase Fault with Stuck Breaker on 5HYDERHL 161.00 (300793) 161 kV Bus a. Apply Fault at the 5HYDERHL 161.00 (300793) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HYDERHL (300793) 161.0 kV to 2HYDERHL (300798) 69.0 kV Two Winding #1 b.2. 5HYDERHL (300793) 161.0 kV to 5STKAEC (300118) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_457 | Single Phase Fault with Stuck Breaker on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply Fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5HOLDENB2 (300124) 161.0 kV to 2HOLDEN (300336) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_458 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_459 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_460 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTON5 (541242) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #z1 b.2. CLINTON5 (541242) 161.0 kV to CLNTN N2 (541303) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_461 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_462 | Single Phase Fault with Stuck Breaker on 5NORTONTP 161.00 (301567) 161 kV Bus a. Apply Fault at the 5NORTONTP 161.00 (301567) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTONTP (301567) 161.0 kV to 5GEORGE (300082) 161.0 kV Transmission Circuit #1 b.2. 5NORTONTP (301567) 161.0 kV to 5NORTON (300105) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_463 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDLIAW_CAP5 (541146) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_464 | Single Phase Fault with Stuck Breaker on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply Fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. 5BTLFD (300348) 161.0 kV to 5JAMESV (300089) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_465 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. 5MOCITYB1 (301563) 161.0 kV to 5MOCITYB2 (300098) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_466 | Single Phase Fault with Stuck Breaker on 2HUGHSV 69.000 (300533) 69 kV Bus a. Apply Fault at the 2HUGHSV 69.000 (300533) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HUGHSV (300533) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 b.2. 2HUGHSV (300533) 69.0 kV to 2GEOGT1 (300529) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_467 | Single Phase Fault with Stuck Breaker on 2MTHULD 69.000 (300558) 69 kV Bus a. Apply Fault at the 2MTHULD 69.000 (300558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTHULD (300558) 69.0 kV to 2LINCLN (300534) 69.0 kV Transmission Circuit #1 b.2. 2MTHULD (300558) 69.0 kV to 2IVYBND (300557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_468 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_469 | Single Phase Fault with Stuck Breaker on CPK446 5 161.00 (547499) 161 kV Bus a. Apply Fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CPK446 2 (547618) 69.0 kV to CPK446 5 (547499) 161.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 b.2. CPK446 2 (547618) 69.0 kV to 2BILLNG (300658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_470 | Single Phase Fault with Stuck Breaker on 2FLTCRK 69.000 (300671) 69 kV Bus a. Apply Fault at the 2FLTCRK 69.000 (300671) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FLTCRK (300671) 69.0 kV to 2CAPEFR (300662) 69.0 kV Transmission Circuit #1 b.2. 2FLTCRK (300671) 69.0 kV to 2JENKIN (300821) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_471 | Single Phase Fault with Stuck Breaker on 2STONBR 69.000 (300733) 69 kV Bus a. Apply Fault at the 2STONBR 69.000 (300733) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STONBR (300733) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 b.2. 2STONBR (300733) 69.0 kV to 2KMBRLNTP (300721) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_472 | Single Phase Fault with Stuck Breaker on 2T.ROCKSW 69.000 (301360) 69 kV Bus a. Apply Fault at the 2T.ROCKSW 69.000 (301360) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2T.ROCKSW (301360) 69.0 kV to 2SILDOL (300730) 69.0 kV Transmission Circuit #1 b.2. 2T.ROCKSW (301360) 69.0 kV to TABLE R2 (505474) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_473 | Single Phase Fault with Stuck Breaker on 5RENOHLW 161.00 (301129) 161 kV Bus a. Apply Fault at the 5RENOHLW 161.00 (301129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2RENOHLW (300738) 69.0 kV to 5RENOHLW (301129) 161.0 kV Two Winding #1 b.2. 2RENOHLW (300738) 69.0 kV to 2SPOKAN (300732) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_474 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STOCKTN5 (505498) 161.0 kV to 5STKAEC (300118) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_475 | Single Phase Fault with Stuck Breaker on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply Fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 5MCBAIN T (345071) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_476 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CALIF UE 2 (344234) 161.0 kV to 5CALIF UE 1 (344233) 161.0 kV Transmission Circuit #z b.2. 5CALIF UE 2 (344234) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_477 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_478 | Single Phase Fault with Stuck Breaker on G07621119-20345.00 (515599) 345 kV Bus a. Apply Fault at the G07621119-20345.00 (515599) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. None to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_479 | Single Phase Fault with Stuck Breaker on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply Fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_480 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDBORDT (755000) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. WWDBORDT (755000) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_481 | Single Phase Fault with Stuck Breaker on GEN-2019-012345.00 (763527) 345 kV Bus a. Apply Fault at the GEN-2019-012345.00 (763527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-012 (763527) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. GEN-2019-012 (763527) 345.0 kV to G19-012-XFM1 (763528) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_482 | Single Phase Fault with Stuck Breaker on GEN-2017-203345.00 (760809) 345 kV Bus a. Apply Fault at the GEN-2017-203345.00 (760809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-203 (760809) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-203 (760809) 345.0 kV to G17-203XFMR1 (760810) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_483 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_484 | Single Phase Fault with Stuck Breaker on VINEDE_S 115.00 (530722) 115 kV Bus a. Apply Fault at the VINEDE_S 115.00 (530722) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINEDE_S (530722) 115.0 kV to VINE2 3 (530694) 115.0 kV Transmission Circuit #z1 b.2. VINEDE_S (530722) 115.0 kV to HAYS 3 (530562) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_485 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_486 | Single Phase Fault with Stuck Breaker on GEN-2017-220345.00 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220345.00 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-220 (760284) 345.0 kV to G17-220-XFM1 (760285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_487 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_488 | Single Phase Fault with Stuck Breaker on FR3HV 345.00 (578530) 345 kV Bus a. Apply Fault at the FR3HV 345.00 (578530) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FR3HV (578530) 345.0 kV to FR2WEST7 (532795) 345.0 kV Transmission Circuit #1 b.2. FR3HV (578530) 345.0 kV to FR3LV1 (578531) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_489 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_490 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_491 | Single Phase Fault with Stuck Breaker on GEN-2017-226138.00 (760641) 138 kV Bus a. Apply Fault at the GEN-2017-226138.00 (760641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-226 (760641) 138.0 kV to G17-226XFMR1 (760642) 34.5 kV Two Winding #1 b.2. GEN-2017-226 (760641) 138.0 kV to G17-227XFMR1 (760662) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_492 | Single Phase Fault with Stuck Breaker on MANVILE3 115.00 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to EMCPHER3 (533417) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_493 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_494 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 4 (539674) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_495 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_496 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_497 | Single Phase Fault with Stuck Breaker on 2ND-KS 3 115.00 (539689) 115 kV Bus a. Apply Fault at the 2ND-KS 3 115.00 (539689) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ND-KS 3 (539689) 115.0 kV to 24-FREY3 (539661) 115.0 kV Transmission Circuit #1 b.2. 2ND-KS 3 (539689) 115.0 kV to GBENDTP3 (539666) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_498 | Single Phase Fault with Stuck Breaker on SSTARTP3 115.00 (539763) 115 kV Bus a. Apply Fault at the SSTARTP3 115.00 (539763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SSTARTP3 (539763) 115.0 kV to GRNBURG3 (539664) 115.0 kV Transmission Circuit #1 b.2. SSTARTP3 (539763) 115.0 kV to FORD 3 (539758) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_499 | Single Phase Fault with Stuck Breaker on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply Fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_500 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_501 | Single Phase Fault with Stuck Breaker on GEN-2018-049345.00 (762834) 345 kV Bus a. Apply Fault at the GEN-2018-049345.00 (762834) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-049 (762834) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-049 (762834) 345.0 kV to G18-108XFM1 (763285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_502 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_503 | Single Phase Fault with Stuck Breaker on G-2011-008-1345.00 (539841) 345 kV Bus a. Apply Fault at the G-2011-008-1345.00 (539841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G-2011-008-1 (539841) 345.0 kV to GEN-2011-008 (539840) 345.0 kV Transmission Circuit #1 b.2. G-2011-008-1 (539841) 345.0 kV to G11-008XFMR2 (539849) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_504 | Single Phase Fault with Stuck Breaker on G-2011-008-2345.00 (539855) 345 kV Bus a. Apply Fault at the G-2011-008-2345.00 (539855) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G-2011-008-2 (539855) 345.0 kV to G11-008XFMR4 (539856) 34.5 kV Two Winding #1 b.2. G-2011-008-2 (539855) 345.0 kV to GEN-2011-008 (539840) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_505 | Single Phase Fault with Stuck Breaker on G-2011-008-3345.00 (539857) 345 kV Bus a. Apply Fault at the G-2011-008-3345.00 (539857) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G-2011-008-3 (539857) 345.0 kV to GEN-2011-008 (539840) 345.0 kV Transmission Circuit #1 b.2. G-2011-008-3 (539857) 345.0 kV to G11-008XFMR5 (539861) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_506 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to SIBLEY 5 (541202) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to SIBLEY 5 (541202) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_507 | Single Phase Fault with Stuck Breaker on STROTHR5 161.00 (541246) 161 kV Bus a. Apply Fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR5 (541246) 161.0 kV to PRALEE 5 (541206) 161.0 kV Transmission Circuit #1 b.2. STROTHR5 (541246) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_508 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_509 | Single Phase Fault with Stuck Breaker on FROSTRD5 161.00 (541220) 161 kV Bus a. Apply Fault at the FROSTRD5 161.00 (541220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FROSTRD5 (541220) 161.0 kV to FROSTRD_CAP5 (541139) 161.0 kV Transmission Circuit #r b.2. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_510 | Single Phase Fault with Stuck Breaker on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply Fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWOOD 5 (541238) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.2. LKWOOD 5 (541238) 161.0 kV to RAYTOWN5 (541219) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_511 | Single Phase Fault with Stuck Breaker on LEX161 5 161.00 (541232) 161 kV Bus a. Apply Fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to LEX69 2 (541264) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_512 | Single Phase Fault with Stuck Breaker on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply Fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_513 | Single Phase Fault with Stuck Breaker on NUCOR5 161.00 (541395) 161 kV Bus a. Apply Fault at the NUCOR5 161.00 (541395) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUCOR5 (541395) 161.0 kV to NUCOR_D1 (541396) 13.8 kV Two Winding #1 b.2. NUCOR5 (541395) 161.0 kV to NUCOR_S1 (541398) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_514 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_515 | Single Phase Fault with Stuck Breaker on G18-063-TAP 69.000 (762992) 69 kV Bus a. Apply Fault at the G18-063-TAP 69.000 (762992) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-063-TAP (762992) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 b.2. G18-063-TAP (762992) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_516 | Single Phase Fault with Stuck Breaker on WARSAWTP 69.000 (541281) 69 kV Bus a. Apply Fault at the WARSAWTP 69.000 (541281) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARSAWTP (541281) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 b.2. WARSAWTP (541281) 69.0 kV to WARSAW 2 (541277) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_517 | Single Phase Fault with Stuck Breaker on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply Fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTY 2 (543092) 69.0 kV to LAKCTYJ2 (543087) 69.0 kV Transmission Circuit #1 b.2. LAKCTY 2 (543092) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_518 | Single Phase Fault with Stuck Breaker on LAKCTYK2 69.000 (543093) 69 kV Bus a. Apply Fault at the LAKCTYK2 69.000 (543093) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYK2 (543093) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. LAKCTYK2 (543093) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_519 | Single Phase Fault with Stuck Breaker on GEN-2019-04869.000 (763802) 69 kV Bus a. Apply Fault at the GEN-2019-04869.000 (763802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-048 (763802) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. GEN-2019-048 (763802) 69.0 kV to G19-048-XFM1 (763803) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_520 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 2 (547585) 69.0 kV to DAD368 5 (547478) 161.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 b.2. DAD368 2 (547585) 69.0 kV to ASH121 2 (547536) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_521 | Single Phase Fault with Stuck Breaker on GRN614 2 69.000 (547613) 69 kV Bus a. Apply Fault at the GRN614 2 69.000 (547613) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRN614 2 (547613) 69.0 kV to ARC250 2 (547549) 69.0 kV Transmission Circuit #1 b.2. GRN614 2 (547613) 69.0 kV to CUPTAP 2 (547436) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_522 | Single Phase Fault with Stuck Breaker on GEN-2017-060161.00 (588980) 161 kV Bus a. Apply Fault at the GEN-2017-060161.00 (588980) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-060 (588980) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-060 (588980) 161.0 kV to G17-060XFMR1 (588981) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_523 | Single Phase Fault with Stuck Breaker on LAW260 2 69.000 (547552) 69 kV Bus a. Apply Fault at the LAW260 2 69.000 (547552) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAW260 2 (547552) 69.0 kV to ASH121 2 (547536) 69.0 kV Transmission Circuit #1 b.2. LAW260 2 (547552) 69.0 kV to HTC338 2 (547573) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_524 | Single Phase Fault with Stuck Breaker on WIL482 69.000 (547726) 69 kV Bus a. Apply Fault at the WIL482 69.000 (547726) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WIL482 (547726) 69.0 kV to ASH121 2 (547536) 69.0 kV Transmission Circuit #1 b.2. WIL482 (547726) 69.0 kV to WIL479 (547727) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_525 | Single Phase Fault with Stuck Breaker on MAR437 2 69.000 (547611) 69 kV Bus a. Apply Fault at the MAR437 2 69.000 (547611) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAR437 2 (547611) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. MAR437 2 (547611) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_526 | Single Phase Fault with Stuck Breaker on BOL602 2 69.000 (547612) 69 kV Bus a. Apply Fault at the BOL602 2 69.000 (547612) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL602 2 (547612) 69.0 kV to FRP217 2 (547545) 69.0 kV Transmission Circuit #1 b.2. BOL602 2 (547612) 69.0 kV to BOL367 2 (547584) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_527 | Single Phase Fault with Stuck Breaker on MTV420 2 69.000 (547606) 69 kV Bus a. Apply Fault at the MTV420 2 69.000 (547606) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MTV420 2 (547606) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 b.2. MTV420 2 (547606) 69.0 kV to MTV351 2 (547577) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_528 | Single Phase Fault with Stuck Breaker on STK324J2 69.000 (547616) 69 kV Bus a. Apply Fault at the STK324J2 69.000 (547616) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STK324J2 (547616) 69.0 kV to STK418 2 (547605) 69.0 kV Transmission Circuit #1 b.2. STK324J2 (547616) 69.0 kV to ARC250 2 (547549) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_529 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_530 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_531 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to G14-001XFMR1 (583851) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_532 | Single Phase Fault with Stuck Breaker on GEN-2017-086345.00 (589240) 345 kV Bus a. Apply Fault at the GEN-2017-086345.00 (589240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-086 (589240) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-086 (589240) 345.0 kV to G17-086XFMR1 (589241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_533 | Single Phase Fault with Stuck Breaker on G19-035-TAP 161.00 (763696) 161 kV Bus a. Apply Fault at the G19-035-TAP 161.00 (763696) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-035-TAP (763696) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. G19-035-TAP (763696) 161.0 kV to AUR124 5 (547468) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_534 | Single Phase Fault with Stuck Breaker on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply Fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to 2REEDSP (300725) 69.0 kV Two Winding #1 b.2. 5REEDSP (301521) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_535 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIXA 5 (505496) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_536 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_537 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_538 | Single Phase Fault with Stuck Breaker on G16-046XFMR1115.00 (587311) 115 kV Bus a. Apply Fault at the G16-046XFMR1115.00 (587311) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046XFMR1 (587311) 115.0 kV to GEN-2016-046 (587310) 345.0 kV Two Winding #1 b.2. G16-046XFMR1 (587311) 115.0 kV to G16-046XFMR3 (587315) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_539 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_540 | Single Phase Fault with Stuck Breaker on SEDPLT 2 69.00 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 69.00 (541275) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_541 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_542 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_543 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_544 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N-GBEND3 (539681) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_545 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_546 | Single Phase Fault with Stuck Breaker on FR2EAST7 345.00 (532792) 345 kV Bus a. Apply Fault at the FR2EAST7 345.00 (532792) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FR2EAST7 (532792) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_547 | Single Phase Fault with Stuck Breaker on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_548 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_549 | Single Phase Fault with Stuck Breaker on EVANS N4 138.00 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_550 | Single Phase Fault with Stuck Breaker on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply Fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_551 | Single Phase Fault with Stuck Breaker on BROOKLINE 5 161.00 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 161.00 (549969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 5 (549969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_552 | Single Phase Fault with Stuck Breaker on RICE 6 230.00 (530686) 230 kV Bus a. Apply Fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_553 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_554 | Single Phase Fault with Stuck Breaker on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_555 | Single Phase Fault with Stuck Breaker on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply Fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_556 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB 230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB 230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_557 | Single Phase Fault with Stuck Breaker on 2REEDSP 69.00 (300725) 69 kV Bus a. Apply Fault at the 2REEDSP 69.00 (300725) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2REEDSP (300725) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_558 | Single Phase Fault with Stuck Breaker on 2LAKE-K 69.00 (300722) 69 kV Bus a. Apply Fault at the 2LAKE-K 69.00 (300722) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LAKE-K (300722) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_559 | Single Phase Fault with Stuck Breaker on BRN412 5 161.00 (547488) 161 kV Bus a. Apply Fault at the BRN412 5 161.00 (547488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRN412 5 (547488) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_560 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_561 | Single Phase Fault with Stuck Breaker on AUR124 2 69.00 (547537) 69 kV Bus a. Apply Fault at the AUR124 2 69.00 (547537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 2 (547537) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_562 | Single Phase Fault with Stuck Breaker on W-DODGE3 115.00 (539699) 115 kV Bus a. Apply Fault at the W-DODGE3 115.00 (539699) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W-DODGE3 (539699) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_563 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_564 | Single Phase Fault with Stuck Breaker on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_565 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_566 | Single Phase Fault with Stuck Breaker on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply Fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_567 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_568 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_569 | Single Phase Fault with Stuck Breaker on JTEC 5161.00 (549954) 161 kV Bus a. Apply Fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. JTEC GEN#1 1 (549890) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.3. JTEC CTS 1 (549891) 12.5 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.4. JTEC GEN#2 1 (549893) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.5. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.6. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.7. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_570 | Single Phase Fault with Stuck Breaker on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_571 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_572 | Single Phase Fault with Stuck Breaker on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply Fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_573 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.4. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_574 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.4. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_575 | Single Phase Fault with Stuck Breaker on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply Fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_576 | Single Phase Fault with Stuck Breaker on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.3. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_577 | Single Phase Fault with Stuck Breaker on NORTON 5161.00 (549967) 161 kV Bus a. Apply Fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_578 | Single Phase Fault with Stuck Breaker on MC CARTNEY 5161.00 (549968) 161 kV Bus a. Apply Fault at the MC CARTNEY 5161.00 (549968) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCCARTNEY (301568) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #z1 b.2. MAC GT1&2 1 (549892) 13.8 kV to MC CARTNEY 5 (549968) 161.0 kV Two Winding #1 b.3. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.4. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_579 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.5. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.6. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_580 | Single Phase Fault with Stuck Breaker on PIC WEST 5161.00 (549971) 161 kV Bus a. Apply Fault at the PIC WEST 5161.00 (549971) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_581 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.4. SPF X3 1 (505495) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_582 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 b.2. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.5. SPF X1 1 (505491) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_583 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 b.2. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 b.3. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 b.4. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 b.5. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.6. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #2 b.7. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_584 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.5. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.6. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.7. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_585 | Single Phase Fault with Stuck Breaker on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply Fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 b.2. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_586 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 2 (547528) 69.0 kV to BOL 73 5 (547464) 161.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 b.2. BOL 73 2 (547528) 69.0 kV to EXP450T2 (547440) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_587 | Single Phase Fault with Stuck Breaker on ASH121 2 69.000 (547536) 69 kV Bus a. Apply Fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 b.2. ASH121 2 (547536) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_588 | Single Phase Fault with Stuck Breaker on NIC170 2 69.000 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIC170 2 (547542) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 b.2. NIC170 2 (547542) 69.0 kV to SED 80 2 (547529) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_589 | Single Phase Fault with Stuck Breaker on GOLDEN 269.000 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 b.2. GOLDEN 2 (549911) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_590 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAIN STREET2 (549921) 69.0 kV to MAIN STREET5 (549958) 161.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.2. MAIN STREET2 (549921) 69.0 kV to MAIN STREET5 (549958) 161.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_591 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.2. NICHOLS 2 (549925) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_592 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.2. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_593 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_594 | Single Phase Fault with Stuck Breaker on BUF342 2 69.000 (547575) 69 kV Bus a. Apply Fault at the BUF342 2 69.000 (547575) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUF342 2 (547575) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 b.2. BUF342 2 (547575) 69.0 kV to BUF243J2 (547432) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_595 | Single Phase Fault with Stuck Breaker on FRG397 2 69.000 (547596) 69 kV Bus a. Apply Fault at the FRG397 2 69.000 (547596) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRG397 2 (547596) 69.0 kV to SED 80 2 (547529) 69.0 kV Transmission Circuit #1 b.2. FRG397 2 (547596) 69.0 kV to BUF243J2 (547432) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_596 | Single Phase Fault with Stuck Breaker on BRT323 2 69.000 (547567) 69 kV Bus a. Apply Fault at the BRT323 2 69.000 (547567) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRT323 2 (547567) 69.0 kV to EXP450T2 (547440) 69.0 kV Transmission Circuit #1 b.2. BRT323 2 (547567) 69.0 kV to SED 80 2 (547529) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_597 | Single Phase Fault with Stuck Breaker on WIL479 69.000 (547727) 69 kV Bus a. Apply Fault at the WIL479 69.000 (547727) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WIL479 (547727) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 b.2. WIL479 (547727) 69.0 kV to SED 80 2 (547529) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_598 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 2 (547585) 69.0 kV to DAD368 5 (547478) 161.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 b.2. DAD368 2 (547585) 69.0 kV to CUPTAP 2 (547436) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_599 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_600 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 5 (549969) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_601 | Single Phase Fault with Stuck Breaker on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIC170 2 (547542) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_602 | Single Phase Fault with Stuck Breaker on SED 80 2 (547529) 69 kV Bus a. Apply Fault at the SED 80 2 (547529) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SED 80 2 (547529) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_603 | Single Phase Fault with Stuck Breaker on FRG397 2 (547596) 69 kV Bus a. Apply Fault at the FRG397 2 (547596) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRG397 2 (547596) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_604 | Single Phase Fault with Stuck Breaker on ASH121 2 (547536) 69 kV Bus a. Apply Fault at the ASH121 2 (547536) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASH121 2 (547536) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_605 | Single Phase Fault with Stuck Breaker on BOL 73 2 (547528) 69 kV Bus a. Apply Fault at the BOL 73 2 (547528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 2 (547528) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_606 | Single Phase Fault with Stuck Breaker on MILL 2 (549918) 69 kV Bus a. Apply Fault at the MILL 2 (549918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILL 2 (549918) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_607 | Single Phase Fault with Stuck Breaker on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 2 (549925) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_608 | Single Phase Fault with Stuck Breaker on BHJ415 2 (547604) 69 kV Bus a. Apply Fault at the BHJ415 2 (547604) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BHJ415 2 (547604) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GEN-2018-032345.00 (762680) 345 kV Bus a. Apply Fault at the GEN-2018-032345.00 (762680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-032 (762680) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-032 (762680) 345.0 kV to G18-032XFM1 (762681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on G16-153-TAP 345.00 (588364) 345 kV Bus a. Apply Fault at the G16-153-TAP 345.00 (588364) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-153-TAP (588364) 345.0 kV to GEN-2017-086 (589240) 345.0 kV Transmission Circuit #1 b.2. G16-153-TAP (588364) 345.0 kV to GEN-2016-153 (588360) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GEN-2018-049345.00 (762834) 345 kV Bus a. Apply Fault at the GEN-2018-049345.00 (762834) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-049 (762834) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-049 (762834) 345.0 kV to G18-108XFM1 (763285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EMDE_FAULT_001 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.3. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.7. TIP292 5 (547472) 161.0 kV to Load #1 b.8. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EMDE_FAULT_002 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.6. TIP292 5 (547472) 161.0 kV to Load #1 b.7. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EMDE_FAULT_003 | Single Phase Fault with Stuck Breaker on L1G382 1 13.200 (547651) 161 kV Bus a. Apply Fault at the L1G382 1 13.200 (547651) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to L1G382 1 (547651) 13.2 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. L1G382 1 (547651) 13.2 kV to Generator #1 b.5. L1G382 1 (547651) 13.2 kV to Load #S1 b.6. L1G382 1 (547651) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_SWPA_FAULT_001 | Single Phase Fault with Stuck Breaker on Table Rock (505472) 161 kV Bus a. Apply Fault at the Table Rock (505472) 161 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. NIXA 5 (505496) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. TABLE R5 (505472) 161.0 kV to remove bus # b.3. TBR1&2 1 (505476) 13.8 kV to Generator #1 b.4. TBR1&2 1 (505476) 13.8 kV to Generator #2 b.5. TBR3&4 1 (505478) 13.8 kV to Generator #3 b.6. TBR3&4 1 (505478) 13.8 kV to Generator #4 b.7. TBR X1 1 (505473) 13.8 kV to remove bus # b.8. TBR X2 1 (505475) 13.8 kV to remove bus # b.9. TBR1&2 1 (505476) 13.8 kV to remove bus # b.10. TBR3&4 1 (505478) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_SWPA_FAULT_002 | Single Phase Fault with Stuck Breaker on Table Rock (505472) 161 kV Bus a. Apply Fault at the Table Rock (505472) 161 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. RVS438 5 (547497) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. TABLE R5 (505472) 161.0 kV to remove bus # b.3. TBR1&2 1 (505476) 13.8 kV to Generator #1 b.4. TBR1&2 1 (505476) 13.8 kV to Generator #2 b.5. TBR3&4 1 (505478) 13.8 kV to Generator #3 b.6. TBR3&4 1 (505478) 13.8 kV to Generator #4 b.7. TBR X1 1 (505473) 13.8 kV to remove bus # b.8. TBR X2 1 (505475) 13.8 kV to remove bus # b.9. TBR1&2 1 (505476) 13.8 kV to remove bus # b.10. TBR3&4 1 (505478) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.3. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.4. CHRKCTY4 (520431) 138.0 kV to Load #1 b.5. SALTPLN4 (520437) 138.0 kV to Load #1 b.6. SALTPLN4 (520437) 138.0 kV to Load #2 b.7. CHRKCTY4 (520431) 138.0 kV to remove bus # b.8. SALTPLN4 (520437) 138.0 kV to remove bus # b.9. ROSEVLY4 (520436) 138.0 kV to Load #1 b.10. AVARD 4 (520601) 138.0 kV to Load #1 b.11. ROSEVLY4 (520436) 138.0 kV to remove bus # b.12. AVARD 4 (520601) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on WAKTASW4 (520434) 138 kV Bus a. Apply Fault at the WAKTASW4 (520434) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to remove bus # b.3. WFEC_RNFRO4 (520409) 138.0 kV to Load #1 b.4. WFEC_RNFRO4 (520409) 138.0 kV to Load #1A b.5. WFEC_RNFRO4 (520409) 138.0 kV to remove bus # b.6. WAKITA_13.8 (520435) 13.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_WFEC_FAULT_003 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 b.4. SEILING4 (520553) 138.0 kV to Load #1 b.5. SEILING4 (520553) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_WFEC_FAULT_004 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 b.4. SEILING4 (520553) 138.0 kV to Load #1 b.5. SEILING4 (520553) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DUNES23 (523061) 0.7 kV to Generator #1 b.12. BUFF_DUNES13 (523062) 0.7 kV to Generator #1 b.13. BUFF_DUNES23 (523061) 0.7 kV to remove bus # b.14. BUFF_DUNES13 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNES22 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNES12 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_SPRM_FAULT_001 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161 (549959) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 b.2. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_001 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_002 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_003 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_004 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_005 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_006 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_007 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_008 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_009 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_001 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. COLBY 3 (530555) 115.0 kV to remove bus #1 b.6. CLBYT1 1 (530645) 13.8 kV to remove bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_002 | Single Phase Fault with Stuck Breaker on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to remove bus #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #1 b.8. HILLCTY3 (531387) 34.5 kV to Generator #2 b.9. HILLCTY3 (531387) 34.5 kV to Generator #3 b.10. HILLCTY3 (531387) 34.5 kV to Generator #4 b.11. HILLCTY3 (531387) 34.5 kV to Generator #5 b.12. HILLCTY3 (531387) 34.5 kV to Generator #6 b.13. HILLCTY3 (531387) 34.5 kV to remove bus # b.14. REDLIN 3 (530605) 115.0 kV to remove bus # b.15. HOXIE 3 (530556) 115.0 kV to remove bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_003 | Single Phase Fault with Stuck Breaker on ATWOOD 3 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 (530554) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to remove bus #1 b.5. ATWOOD 3 (530554) 115.0 kV to Generator #1 b.6. HILLCTY3 (531387) 34.5 kV to Generator #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #2 b.8. HILLCTY3 (531387) 34.5 kV to Generator #3 b.9. HILLCTY3 (531387) 34.5 kV to Generator #4 b.10. HILLCTY3 (531387) 34.5 kV to Generator #5 b.11. HILLCTY3 (531387) 34.5 kV to Generator #6 b.12. ATWOOD 3 (530554) 115.0 kV to Load #1 b.13. ATWOOD 3 (530554) 115.0 kV to Load #41 b.14. ATWOOD 3 (530554) 115.0 kV to remove bus # b.15. HILLCTY3 (531387) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_004 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_005 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.4. CLBYT1 1 (530645) 13.8 kV to remove bus #1 b.5. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Load #99 b.12. COLBY 3 (530555) 115.0 kV to Generator #C8 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_006 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. CLBYT1 1 (530645) 13.8 kV to remove bus #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Generator #C8 b.12. COLBY 3 (530555) 115.0 kV to Load #99 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_007 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_008 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Transmission Circuit #1 b.4. REDLIN 3 (530605) 115.0 kV to Load #71 b.5. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_009 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. REDLIN 3 (530605) 115.0 kV to Load #71 b.5. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_010 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMECG1 1 (530674) 13.8 kV to remove bus # b.4. GMECG2 1 (530675) 13.8 kV to remove bus # b.5. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_011 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. GMECG1 1 (530674) 13.8 kV to remove bus #1 b.2. GMECG2 1 (530675) 13.8 kV to remove bus #1 b.3. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.6. N HAYS3 (530581) 115.0 kV to remove bus #1 b.7. VINETAP3 (530693) 115.0 kV to remove bus #1 b.8. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes